## Exported from SC
Punchlist ID | Asset (Name/Tag) | Asset Pack | Punchlist Category (Name) | Discipline (Name) | Description | Scheduling - Responsible Company (Name) | Systemization - Subsystem (Summary) | Workflow - Closing Date | Status | Comment | Action Required | Originated Date | Originated By | Priority | Completed Date
PL-000073 | PS5-60-UR-8100A |  | C | M | Gen-Set nameplate and equipment tagging not complete. | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2024-03-21T11:08:57.000 | Thao-my, Alexandre | PS5 - Milestone B
PL-000074 | PS5-60-UR-8100B |  | C | M | Gen-Set nameplate and equipment tagging not complete. | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2024-03-21T11:58:13.000 | Thao-my, Alexandre | PS5 - Milestone B
PL-000075 | PS5-60-UR-8100C |  | C | M | Gen-Set nameplate and equipment tagging not complete. | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  |  | 2024-03-21T12:01:18.000 | Thao-my, Alexandre | PS5 - Milestone D
PL-000076 | PS5-60-UR-8100D |  | C | M | Gen-Set nameplate and equipment tagging not complete. | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2024-03-21T12:02:50.000 | Thao-my, Alexandre | PS5 - Milestone D
PL-000077 | PS5-60-UR-8100E |  | C | M | Gen-Set nameplate and equipment tagging not complete. | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2024-03-21T12:04:20.000 | Thao-my, Alexandre | PS5 - Milestone D
PL-000078 | PS5-60-UR-8100F |  | C | M | Gen-Set nameplate and equipment tagging not complete. | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2024-03-21T12:07:26.000 | Thao-my, Alexandre | PS5 - Milestone D
PL-000079 | PS5-60-UR-8100G |  | C | M | Gen-Set nameplate and equipment tagging not complete. | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2024-03-21T12:08:59.000 | Thao-my, Alexandre | PS5 - Milestone E
PL-000170 | PS5-25-PA-3100A |  | C | M | CE mark not present on pump skid. | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Acquire CE marking on pump skid. New CE marked nameplate to supply and fit. | 2024-04-25T12:07:16.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000171 | PS5-25-PA-3100B |  | C | M | CE mark not present on pump skid. | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Acquire CE marking on pump skid. Carry Over Work confirmed as supplying and fitting new CE marked nameplate. | 2024-04-25T12:11:13.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000172 | PS5-25-PA-3100C |  | C | M | CE mark not present on pump skid. | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Acquire CE marking on pump skid. | 2024-04-25T12:12:40.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000173 | PS5-25-PA-3100A |  | A | M | Thermowells are to be replaced. | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Thermowells to be replaced on site. | 2024-04-25T12:18:16.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000174 | PS5-25-PA-3100B |  | A | M | Thermowells are to be replaced. | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Thermowells to be replaced on site. | 2024-04-25T12:19:34.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000175 | PS5-25-PA-3100C |  | A | M | Thermowells are to be replaced. | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Thermowells to be replaced on site. | 2024-04-25T12:20:30.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000176 | PS5-25-PA-3100A |  | B | M | PS5-25-LIT-3101A: Sunshade is damaged. | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Sunshade to be replaced. Sunshield has been removed for repair and is packed separately. Carry Over Work action is to confirm availability and condition of this sunshade. | 2024-04-25T12:22:28.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000177 | PS5-25-PA-3100C |  | B | M | Sunshade has chips and appears to be damaged - Local to PS5-25-BI-1274C. | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Replace or repair sun shade. Confirmed carry Over Work is to inspect during installation/commissioning and confirm availability and condition. | 2024-04-25T12:24:05.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000178 | PS5-25-PA-3100C |  | 0 | M | PS5-25-BE-0001C: Stopping plugs installed into side of MTB frame do not have legible Ex markings | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C | 2025-05-27T07:12:26.000 | Closed |  | Ensure stopping plugs installed can be verified for suitability at point of visual inspection as per IEC 60079-17. | 2024-04-25T12:24:59.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000327 | PS5-60-UR-8100D |  | A | M | 2: DAMAGED AIR FILTERS. | EPS UNATRAC | PS5-60-10 - Power Generation Package D | 2026-07-04T06:50:38.000 | Closed |  | Replace the air inlet filters . | 2024-08-29T05:37:27.130 | khan, mojammil | PS5 - Milestone D | 2026-07-04T06:50:29.000
PL-000329 | PS5-60-UR-8100D |  | A | M | 4:OIL LEAKAGE FROM GENERATOR BEARING LUBRICATION PUMP TUBING. | EPS UNATRAC | PS5-60-10 - Power Generation Package D | 2026-07-04T06:51:20.000 | Closed |  | CHECK TUBING JOINTS AND TIGHT PROPERLY. | 2024-09-03T05:55:00.923 | khan, mojammil | PS5 - Milestone D | 2026-07-04T06:51:16.000
PL-000330 | PS5-60-UR-8100D |  | B | M | 4.1:CABLE PROTECTION IS DAMAGED | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  | FIX THE CABLE PROTECTION | 2024-09-03T06:04:57.720 | khan, mojammil | PS5 - Milestone D
PL-000331 | PS5-60-UR-8100D |  | A | M | 4.2:OIL LEAKAGE FROM DRAINING POINT | EPS UNATRAC | PS5-60-10 - Power Generation Package D | 2026-07-04T06:52:44.000 | Closed |  | TIGHT PROPERLY THE DRAINING POINT | 2024-09-03T06:05:33.963 | khan, mojammil | PS5 - Milestone D | 2026-07-04T06:52:40.000
PL-000332 | PS5-60-UR-8100D |  | A | M | 4.3: RUST IN SEVERAL AREAS OF GENSET AND PRESENCE OF PIN HOLES IN WELDING. | EPS UNATRAC | PS5-60-10 - Power Generation Package D | 2026-07-04T06:53:09.000 | Closed |  | CLEAN IT WITH SAND PAPER AND APPLY GREASE. | 2024-09-03T06:05:41.210 | khan, mojammil | PS5 - Milestone D | 2026-07-04T06:53:05.000
PL-000333 | PS5-60-UR-8100D |  | C | M | 4.4:PAINT DAMAGED FROM LIFTING POINTS | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  | TOUCH-UP PAINTING OF LIFTING POINTS. | 2024-09-03T06:10:52.070 | khan, mojammil | PS5 - Milestone D
PL-000334 | PS5-60-UR-8100C |  | A | M | 4:LEAKAGE FROM FUEL FILTER. | EPS UNATRAC | PS5-60-07 - Power Generation Package C | 2026-07-04T06:53:39.000 | Closed |  | TIGHT PROPERLY . | 2024-09-03T08:01:52.957 | khan, mojammil | PS5 - Milestone D | 2026-07-04T06:53:34.000
PL-000335 | PS5-60-UR-8100C |  | C | M | 4.1:THE FUEL FILTER CONNECTING THREAD IS CORRODED | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | CHANGE THE CORRODED PART. | 2024-09-03T08:09:29.060 | khan, mojammil | PS5 - Milestone D
PL-000336 | PS5-60-UR-8100C |  | A | M | 4.2:THE BOTTOM HOLE ASSESORY IS DAMAGED | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | REPLACE THE PART | 2024-09-03T08:15:02.330 | khan, mojammil | PS5 - Milestone D
PL-000337 | PS5-60-UR-8100C |  | A | M | 4.3: TRANSMITTER ROD IS BEND AND OIL LEAKING | EPS UNATRAC | PS5-60-07 - Power Generation Package C | 2026-07-04T10:40:09.000 | Closed |  | CLEAN THE OIL AND TIGHT PROPERLY FOR LEAKING . | 2024-09-03T08:19:23.150 | khan, mojammil | PS5 - Milestone D | 2026-07-04T10:40:04.000
PL-000338 | PS5-60-UR-8100C |  | A | M | 4.4:OIL LEAKAGE FROM DRAINING POINT | EPS UNATRAC | PS5-60-07 - Power Generation Package C | 2026-07-04T10:40:40.000 | Closed |  | TIGHT PROPERLY | 2024-09-03T08:31:44.377 | khan, mojammil | PS5 - Milestone D | 2026-07-04T10:40:35.000
PL-000339 | PS5-60-UR-8100C |  | C | M | 4.5:GENERATOR PAINT IRREGULARITY. | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | TOUCH UP PAINTING REQUIRED | 2024-09-03T08:36:39.730 | khan, mojammil | PS5 - Milestone D
PL-000340 | PS5-60-UR-8100C |  | C | M | 4.6:BENDING OF THE HEAD CONNECTING PIPE IN ENGINE. | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | INSTALL PROPERLY. | 2024-09-03T08:41:24.890 | khan, mojammil | PS5 - Milestone D
PL-000341 | PS5-60-UR-8100C |  | C | M | 4.7: RUST IN MULTIPLE LOCATIONS | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | CLEAN IT WITH SAND PAPER AND APPLY GREASE. | 2024-09-03T08:44:33.457 | khan, mojammil | PS5 - Milestone D
PL-000342 | PS5-60-UR-8100C |  | C | M | 4.8:LIFTING POINT PAINT DAMAGE | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | TOUCH UP PAINTING REQUIRED. | 2024-09-03T08:52:28.897 | khan, mojammil | PS5 - Milestone D
PL-000343 | PS5-60-UR-8100B |  | A | M | 4:OIL LEAKAGE FROM SEVERAL PLACES OF GENERATOR.(TUBINGS,JOINTS) | EPS UNATRAC | PS5-60-04 - Power Generation Package B | 2026-07-04T10:41:09.000 | Closed |  | TIGHT PROPERLY THE JOINTS. | 2024-09-03T10:09:54.410 | khan, mojammil | PS5 - Milestone B | 2026-07-04T10:41:06.000
PL-000344 | PS5-60-UR-8100B |  | C | M | 4.1: RUST IN MULTIPLE AREAS | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  | CLEAN IT WITH SAND PAPER AND APPLY GREASE | 2024-09-03T10:17:18.007 | khan, mojammil | PS5 - Milestone B
PL-000345 | PS5-60-UR-8100B |  | C | M | 4.2:PAINT DAMAGED AT LIFTING POINT | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  | PAINT TOUCH UP REQUIRED | 2024-09-03T10:24:01.873 | khan, mojammil | PS5 - Milestone B
PL-000346 | PS5-60-UR-8100A |  | A | E | 4: A BUTTON ON GENERATOR CONTROL PANEL IS BROKEN | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  | REPLACE THE BUTTON IN CONTROL PANEL | 2024-09-03T10:35:16.897 | khan, mojammil | PS5 - Milestone B
PL-000347 | PS5-60-UR-8100A |  | C | M | 4.1:RUST IN COUPLING AND OTHER PLACES. | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  | CLEAN IT WITH SAND PAPER AND APPLY GREASE | 2024-09-03T10:43:20.693 | khan, mojammil | PS5 - Milestone B
PL-000348 | PS5-60-UR-8100A |  | A | M | 4.2:GENERATOR HAS MULTIPLE LEAKING POINTS.(JOINTS AND CONNECTIONS) | EPS UNATRAC | PS5-60-01 - Power Generation Package A | 2026-07-04T10:41:34.000 | Closed |  | TIGHT PROPERLY. | 2024-09-03T10:50:44.327 | khan, mojammil | PS5 - Milestone B | 2026-07-04T10:41:29.000
PL-000349 | PS5-60-UR-8100A |  | C | M | 4.3:LIFTING POINTS PAINT DAMAGED | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  | TOUCH UP PAINT REQUIRED | 2024-09-03T11:09:04.780 | khan, mojammil | PS5 - Milestone B
PL-000350 | PS5-60-UR-8100G |  | A | M | 4:LEAKAGE FROM MULTIPLE POINTS(JOINTS AND CONNECTIONS) | EPS UNATRAC | PS5-60-19 - Power Generation Package G | 2026-07-04T10:42:42.000 | Closed |  | TIGHT PROPERLY ALL THE LEAKING PARTS | 2024-09-03T11:20:14.057 | khan, mojammil | PS5 - Milestone E | 2026-07-04T10:42:36.000
PL-000351 | PS5-60-UR-8100G |  | C | M | 4.1:RUST IN MULTIPLE PLACES | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  | CLEAN IT WITH SAND PAPER AND APPLY GREASE | 2024-09-03T11:29:17.363 | khan, mojammil | PS5 - Milestone E
PL-000352 | PS5-60-UR-8100G |  | C | M | 4.2:LIFTING POINTS PAINT ARE DAMAGED | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  | TOUCH UP PAINT REQUIRED | 2024-09-03T11:33:31.003 | khan, mojammil | PS5 - Milestone E
PL-000353 | PS5-60-UR-8100A |  | A | E | 4.4: A jumper has been installed to short the CT at the alternator JB – Jumper to be removed once CTs will be connected and shorted at the CRO GCP via permanent cable. | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  | Jumper to be removed once permanent cable is connected. | 2024-09-03T13:19:51.893 | Thao-my, Alexandre | PS5 - Milestone B
PL-000354 | PS5-60-UR-8100A |  | A | E | 4.5: During preservation, VTs are disconnected in the cable terminal box to perform Insulation Resistance test. | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  | Any cable disconnected to be insulated and to be reconnected prior commissioning activities. | 2024-09-03T13:24:53.493 | Thao-my, Alexandre | PS5 - Milestone B
PL-000355 | PS5-60-UR-8100B |  | A | E | 4.3: A jumper has been installed to short the CT at the alternator JB – Jumper to be removed once CTs will be connected and shorted at the CRO GCP via permanent cable. | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  | Jumper to be removed once permanent cable is connected. | 2024-09-04T04:55:04.100 | Thao-my, Alexandre | PS5 - Milestone B
PL-000356 | PS5-60-UR-8100B |  | A | E | 4.4: During preservation, VTs are disconnected in the cable terminal box to perform Insulation Resistance test. | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  | Any cable disconnected to be insulated and to be reconnected prior commissioning activities. | 2024-09-04T04:56:48.277 | Thao-my, Alexandre | PS5 - Milestone B
PL-000357 | PS5-60-UR-8100C |  | A | E | 4.9: A jumper has been installed to short the CT at the alternator JB – Jumper to be removed once CTs will be connected and shorted at the CRO GCP via permanent cable. | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | Jumper to be removed once permanent cable is connected. | 2024-09-04T05:01:26.570 | Thao-my, Alexandre | PS5 - Milestone D
PL-000358 | PS5-60-UR-8100C |  | A | E | 4.10: During preservation, VTs are disconnected in the cable terminal box to perform Insulation Resistance test. | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | Any cable disconnected to be insulated and to be reconnected prior commissioning activities. | 2024-09-04T05:03:15.000 | Thao-my, Alexandre | PS5 - Milestone D
PL-000359 | PS5-60-UR-8100D |  | A | E | 4.5: A jumper has been installed to short the CT at the alternator JB – Jumper to be removed once CTs will be connected and shorted at the CRO GCP via permanent cable. | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  | Jumper to be removed once permanent cable is connected. | 2024-09-04T05:08:59.090 | Thao-my, Alexandre | PS5 - Milestone D
PL-000360 | PS5-60-UR-8100D |  | A | E | 4.6: During preservation, VTs are disconnected in the cable terminal box to perform Insulation Resistance test. | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  | Any cable disconnected to be insulated and to be reconnected prior commissioning activities. | 2024-09-04T05:10:13.133 | Thao-my, Alexandre | PS5 - Milestone D
PL-000361 | PS5-60-UR-8100G |  | A | E | 4.3: A jumper has been installed to short the CT at the alternator JB – Jumper to be removed once CTs will be connected and shorted at the CRO GCP via permanent cable. | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  | Jumper to be removed once permanent cable is connected. | 2024-09-04T05:12:29.257 | Thao-my, Alexandre | PS5 - Milestone E
PL-000362 | PS5-60-UR-8100G |  | A | E | 4.4: During preservation, VTs are disconnected in the cable terminal box to perform Insulation Resistance test. | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  | Any cable disconnected to be insulated and to be reconnected prior commissioning activities. | 2024-09-04T05:14:25.560 | Thao-my, Alexandre | PS5 - Milestone E
PL-000363 | PS5-25-VP-1100 |  | B | P | 2: Check for any damage during transportation. | EPS VENDOR | PS5-25-01 - Export Pipeline Pig Receiver | 2025-05-27T07:37:23.000 | Closed |  |  | 2024-09-04T07:51:58.000 | Zhang, Hui | PS5 - Milestone H
PL-000364 | PS5-25-VP-1100 |  | C | M | Some areas inside the pig receiver are rust | EPS VENDOR | PS5-25-01 - Export Pipeline Pig Receiver |  | Originated |  |  | 2024-09-04T07:51:58.000 | Zhang, Hui | PS5 - Milestone H
PL-000365 | PS5-25-VP-1200 |  | C | M | Some place in the pig lancher is rust | EPS VENDOR | PS5-25-07 - Export Pipeline Pig Launcher |  | Originated |  |  | 2024-09-04T07:51:59.000 | Zhang, Hui | PS5 - Milestone H
PL-000423 | PS5-60-UR-8100E |  | B | M | 4:EXHAUST FLANGE IS NOT PAINTED. | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | PAINT THE EXHAUST FLANGE (May not be required as per vendor) | 2024-10-07T12:09:13.110 | khan, mojammil | PS5 - Milestone D
PL-000424 | PS5-60-UR-8100E |  | A | M | 4.1:AIR INLET FILTER IS DAMAGED | EPS UNATRAC | PS5-60-13 - Power Generation Package E | 2026-07-04T10:44:50.000 | Closed |  |  | 2024-10-07T12:17:21.077 | khan, mojammil | PS5 - Milestone D | 2026-07-04T10:44:47.000
PL-000425 | PS5-60-UR-8100E |  | A | M | 4.2:THERE IS NO LUBE OIL INSIDE THE ALTERNATOR NON DRIVE END BEARING HOUSING. | EPS UNATRAC | PS5-60-13 - Power Generation Package E | 2026-07-04T10:45:29.000 | Closed |  | FILL THE LUBE OIL. | 2024-10-07T12:23:06.547 | khan, mojammil | PS5 - Milestone D | 2026-07-04T10:45:22.000
PL-000426 | PS5-60-UR-8100E |  | B | M | 4.3:THE FILTER HAS NO OIL INSIDE IT. | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | FILL THE OIL INSIDE THE FILTER can be carried out during commissioning stage | 2024-10-07T12:27:25.597 | khan, mojammil | PS5 - Milestone D
PL-000427 | PS5-60-UR-8100E |  | C | M | 4.4:THERE IS RUST INSIDE THE DAMPER AND SEVERAL PARTS OF THE GENERATOR . | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | CLEAN IT WITH SAND PAPER AND APPLY GREASE | 2024-10-07T12:30:27.423 | khan, mojammil | PS5 - Milestone D
PL-000428 | PS5-60-UR-8100E |  | A | M | 4.5:OIL LEAKAGE FROM MULTIPLE LOCATIONS | EPS UNATRAC | PS5-60-13 - Power Generation Package E | 2026-07-04T10:46:07.000 | Closed |  | TORQUE PROPERLY THEN CHECK AGAIN. | 2024-10-07T12:34:48.767 | khan, mojammil | PS5 - Milestone D | 2026-07-04T10:46:00.000
PL-000429 | PS5-60-UR-8100E |  | C | M | 4.6:PAINT DAMAGED FROM BODY OF THE GENERATOR | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | TOUCH UP PAINTING REQUIRED | 2024-10-07T12:39:01.547 | khan, mojammil | PS5 - Milestone D
PL-000430 | PS5-60-UR-8100E |  | C | M | 4.7:LIFTING POINT PAINT DAMAGED | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | TOUCH UP PAINTING REQUIRED | 2024-10-07T12:44:33.227 | khan, mojammil | PS5 - Milestone D
PL-000431 | PS5-60-UR-8100F |  | B | E | 4:Jacket water heater control box button is damaged | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  | REPLACE THE BUTTON | 2024-10-07T13:00:37.617 | khan, mojammil | PS5 - Milestone D
PL-000432 | PS5-60-UR-8100F |  | B | M | 4.1:unavailability of oil in the filter | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  | fill the oil. | 2024-10-07T13:03:08.310 | khan, mojammil | PS5 - Milestone D
PL-000433 | PS5-60-UR-8100F |  | A | M | 4.2:low oil level in the NDE end of alternator side glass. | EPS UNATRAC | PS5-60-16 - Power Generation Package F | 2026-07-04T10:46:34.000 | Closed |  | fill the lube oil. | 2024-10-07T13:10:53.597 | khan, mojammil | PS5 - Milestone D | 2026-07-04T10:46:30.000
PL-000434 | PS5-60-UR-8100F |  | C | M | 4.3:The head of the cam shaft cover plug bolt is damaged | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2024-10-07T13:15:45.470 | khan, mojammil | PS5 - Milestone D
PL-000435 | PS5-60-UR-8100F |  | C | M | 4.4:The generator has multiple rusts,Including damper | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  | CLEAN IT WITH SAND PAPER AND APPLY GREASE | 2024-10-07T13:18:59.607 | khan, mojammil | PS5 - Milestone D
PL-000436 | PS5-60-UR-8100F |  | A | M | 4.5:The generator has multiple leakages | EPS UNATRAC | PS5-60-16 - Power Generation Package F | 2026-07-04T10:46:59.000 | Closed |  | torque properly then check again. | 2024-10-07T13:23:08.790 | khan, mojammil | PS5 - Milestone D | 2026-07-04T10:46:55.000
PL-000437 | PS5-60-UR-8100F |  | C | M | 4.6:lifting points paint peeling; a little paint damage on the generator | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2024-10-07T13:26:43.333 | khan, mojammil | PS5 - Milestone D
PL-000467 | PS5-01-UK-6100 |  | C | M | 4:DOOR CANOPY IS DAMAGED | EPS VENDOR | PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100) |  | Originated |  | NEED TO FIX THE DOOR CANOPY | 2024-11-14T05:24:13.863 | khan, mojammil | PS5 - Milestone F
PL-000468 | PS5-01-UK-6100 |  | C | M | 4.1:THE KNOB OF THE EMERGENCY FIRE DOOR IS MISSING | EPS VENDOR | PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100) |  | Originated |  | NEED TO PROVIDE THE NEW KNOBS | 2024-11-14T05:28:46.823 | khan, mojammil | PS5 - Milestone F
PL-000469 | PS5-01-UK-6100 |  | C | M | 4.2: 4 DOOR KEYS ARE BEND | EPS VENDOR | PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100) |  | Originated |  | PROVIDE NEW KEYS | 2024-11-14T05:32:26.070 | khan, mojammil | PS5 - Milestone F
PL-000478 | PS5-25-MOV-0026 |  | B | I | Ensure that the mechanical stopper minimum flow through 25-MOV-0026 is higher than the export pump minimum flow. | EACOP | PS5-25-01 - Export Pipeline Pig Receiver |  | Originated |  | All Launcher/Receiver drawings modified accordingly. The minimum opening of the MOV-0026 to be confirmed during commissioning. | 2024-11-18T06:12:27.000 | Riima, Peter | PS5 - Milestone H
PL-000479 | PS5-25-MOV-0027 |  | B | I | Ensure that the mechanical stopper minimum flow through 25-MOV-0027 is higher than the export pump minimum flow. | EACOP | PS5-25-06 - Crude Oil Export Pumps Discharge |  | Originated |  | All Launcher/Receiver drawings modified accordingly. The minimum opening of the MOV-0027 to be confirmed during commissioning. | 2024-11-18T06:14:51.000 | Riima, Peter | PS5 - Milestone H
PL-000497 | PS5-05-UR-8100 |  | A | M | 4:THE TWO VIBRATION ISOLATORS, MEANT TO BE PLACED UNDER THE RADIATOR, HAVE BEEN MISTAKENLY INSTALLED BENEATH THE ENGINE. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T10:41:26.000 | Closed |  | NEED TO EXCHANGE THE VIBRATION ISOLATOR WITH THE RADIATOR ISOLATORS . | 2024-12-03T04:58:29.820 | khan, mojammil | PS5 - Milestone C
PL-000498 | PS5-05-UR-8100 |  | A | M | 4.1:LEVEL TRANSMITTER ON DIESEL TANK NOT INSTALLED. AND NOT FOUND ON LOCATION. REFERENCE PID TZ-MID-60-UTR2-130001_05. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T10:46:11.000 | Closed |  | INSTALL ONE TRANSMITTER | 2024-12-03T05:03:45.093 | khan, mojammil | PS5 - Milestone C
PL-000499 | PS5-05-UR-8100 |  | C | M | 4.2:CORROSION OBSERVED ON CASING OF THE TURBO CHARGER | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T10:47:47.000 | Closed |  |  | 2024-12-03T05:14:53.583 | khan, mojammil | PS5 - Milestone C
PL-000500 | PS5-05-UR-8100 |  | A | E | 4.3:THE EMERGENCY LIGHT IS SEVERELY DAMAGED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T10:48:31.000 | Closed |  |  | 2024-12-03T05:18:34.213 | khan, mojammil | PS5 - Milestone C
PL-000501 | PS5-05-UR-8100 |  | A | I | 4.4:THE FLAME DETECTOR IS NEITHER INSTALLED NOR SECURELY MOUNTED; INSTEAD, IT IS HANGING LOOSELY FROM THE CABLE TRAY IN DIESEL TANK ROOM. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-08-15T12:34:29.000 | Closed |  | to be installed properly | 2024-12-03T05:20:15.727 | khan, mojammil | PS5 - Milestone C | 2026-07-30T18:48:10.000
PL-000502 | PS5-05-UR-8100 |  | C | M | 4.5:AC FINS ARE PARTIALLY DAMAGED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T10:49:29.000 | Closed |  |  | 2024-12-03T05:22:46.257 | khan, mojammil | PS5 - Milestone C
PL-000503 | PS5-05-UR-8100 |  | C | M | 4.6:EXHAUST PIPE SEALANT IS DAMAGED. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:12:10.000 | Closed |  |  | 2024-12-03T05:24:34.790 | khan, mojammil | PS5 - Milestone C
PL-000504 | PS5-05-UR-8100 |  | C | M | 4.7:THE MONORAIL CRANE IS IMPROPERLY INSTALLED, WITH ITS WHEEL MISALIGNED AND OUT OF POSITION, CREATING A SIGNIFICANT RISK OF MALFUNCTION AND OPERATIONAL FAILURE | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Completed |  | to be rectified | 2024-12-03T05:27:51.857 | khan, mojammil | PS5 - Milestone C | 2026-07-30T18:51:52.000
PL-000505 | PS5-05-UR-8100 |  | C | M | 4.8:AC UNIT PLASTIC PIPE IS DEFORMED AND DAMAGED DUE TO THE CLAMP BEING OVERLY TIGHTENED. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:14:25.000 | Closed |  |  | 2024-12-03T05:32:44.223 | khan, mojammil | PS5 - Milestone C
PL-000508 | PS5-05-UR-8100 |  | C | M | 4.9:CANOPY RUBBER PROTECTION IS MISSING. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:14:49.000 | Closed |  |  | 2024-12-03T05:35:26.223 | khan, mojammil | PS5 - Milestone C
PL-000512 | PS5-05-UR-8100 |  | A | E | 4.10:2 EXTERNAL LIGHTS FOR MAIN DOORS (BRACKET BEND, LIGHT PROTECTION FALLEN OFF) | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:15:17.000 | Closed |  |  | 2024-12-03T05:43:08.980 | khan, mojammil | PS5 - Milestone C
PL-000513 | PS5-05-UR-8100 |  | C | M | 4.11:ENGINE RADIATOR TO VENTILATION OUTLET CHAMBER NOT SEALED PROPERLY. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:15:42.000 | Closed |  |  | 2024-12-03T05:45:24.420 | khan, mojammil | PS5 - Milestone C
PL-000514 | PS5-05-UR-8100 |  | C | M | 4.12:VENT OUTLET CHAMBER TO DAY TANK PARTITION WALL IS NOT PROPERLY SEALED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:16:08.000 | Closed |  |  | 2024-12-03T05:49:01.763 | khan, mojammil | PS5 - Milestone C
PL-000515 | PS5-05-UR-8100 |  | C | M | 4.13:SUPPORT BEAM (FOR MONORAIL BEAM) FLANGE FACE IS HAVING GAPS | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:16:34.000 | Closed |  |  | 2024-12-03T05:51:39.770 | khan, mojammil | PS5 - Milestone C
PL-000516 | PS5-05-UR-8100 |  | B | E | 4.14:EARTHING CABLE JUMPERS BETWEEN ELECTRICAL CABLE TRAYS ARE NOT EXISTING ON MANY LOCATIONS | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Completed |  | Earthing cable jumpers to be fixed properly | 2024-12-03T05:54:06.697 | khan, mojammil | PS5 - Milestone C | 2026-07-30T19:09:36.000
PL-000517 | PS5-05-UR-8100 |  | C | I | 4.15:INSTRUMENT CABLE RUNNING ON COOLING PIPE WITH TIE RODS | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2024-12-03T05:56:33.330 | khan, mojammil | PS5 - Milestone C
PL-000518 | PS5-05-UR-8100 |  | A | I | 4.16:INSTRUMENT CABLE TERMINATION TO RADIATOR IS NOT PROPERLY FIXED. (NO CABLE INSULATION ) | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-08-15T12:35:08.000 | Closed |  | to be fix. | 2024-12-03T06:00:28.753 | khan, mojammil | PS5 - Milestone C | 2026-07-30T19:14:07.000
PL-000519 | PS5-05-UR-8100 |  | C | M | 4.17:THERE IS NO TAG NUMBER ON TROLLEY BEAM ,MANUAL TROLLEY & CHAIN BLOCKS | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Completed |  | Tag number to be painted | 2024-12-03T06:03:17.083 | khan, mojammil | PS5 - Milestone C | 2026-07-30T19:16:41.000
PL-000520 | PS5-05-UR-8100 |  | A | M | 4.18:SPARE NOZZLE N3 ON DIESEL TANK HAS NO RATED BLIND, NO GASKET AND BOLT SETS. REFERENCE PID TZ-MID-60-UTR2-130001_05. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-07-05T07:32:05.000 | Closed |  |  | 2024-12-03T06:05:22.000 | khan, mojammil | PS5 - Milestone C | 2026-07-05T07:32:01.000
PL-000521 | PS5-05-UR-8100 |  | C | M | 4.19:NOZZLE 10 (FUEL FILLING WITH OVERFILL PREVENTION VALVE) FITTED WITH PTFE TAPE. REFERENCE PID TZ-MID-60-UTR2-130001_05. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2024-12-03T06:07:41.010 | khan, mojammil | PS5 - Milestone C
PL-000522 | PS5-05-UR-8100 |  | C | E | 4.20:LIGHTING JB DOES NOT HAVE TAG NUMBER JB DOES NOT HAVE MOISTURE ABSORBER (SUCH AS DESSICANT BAG- VPCI) | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2024-12-03T06:09:51.347 | khan, mojammil | PS5 - Milestone C
PL-000523 | PS5-05-UR-8100 |  | A | E | 4.21:THERE IS NO “AIR SHUT OFF BUTTON” THERE IS NO PROTECTION CAP ON CABLE TERMINATION POINT. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-08-20T04:38:19.000 | Closed |  |  | 2024-12-03T06:10:43.300 | khan, mojammil | PS5 - Milestone C | 2026-08-15T14:17:17.000
PL-000524 | PS5-05-UR-8100 |  | A | E | 4.22:KEYS FOR JB IS MISSING | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:20:32.000 | Closed |  |  | 2024-12-03T06:15:11.313 | khan, mojammil | PS5 - Milestone C
PL-000525 | PS5-05-UR-8100 |  | C | M | 4.23:THE DOOR LOCK YIELDS ONLY WHEN TURNS AT AN ABSURD ANGLE. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:20:58.000 | Closed |  |  | 2024-12-03T06:19:33.567 | khan, mojammil | PS5 - Milestone C
PL-000526 | PS5-05-UR-8100 |  | B | M | 4.24:THE AIR INLET HOOD FRAME IS SEVERELY DAMAGED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:21:22.000 | Closed |  |  | 2024-12-03T06:27:31.287 | khan, mojammil | PS5 - Milestone C
PL-000527 | PS5-05-UR-8100 |  | C | M | 4.25:THE GASKET FOR THE INLET HOOD IS COMPLETELY TORN AND COMPROMISED. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:21:49.000 | Closed |  |  | 2024-12-03T06:29:34.140 | khan, mojammil | PS5 - Milestone C
PL-000528 | PS5-05-UR-8100 |  | C | M | 4.26:AIR OUTLET HOOD FRAME IS SLIGHTLY BEND. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:22:09.000 | Closed |  |  | 2024-12-03T06:31:13.550 | khan, mojammil | PS5 - Milestone C
PL-000529 | PS5-05-UR-8100 |  | A | M | 4.27:GLYCERINE LEAKAGE FROM THE HYDRAULIC CABIN PRESSURE GAUGE. THE GLYCERINE LEVEL INSIDE THE PG IS LOW. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:24:00.000 | Closed |  |  | 2024-12-03T06:35:41.520 | khan, mojammil | PS5 - Milestone C
PL-000530 | PS5-05-UR-8100 |  | C | M | 4.28:OIL IS FOUND SPILLED ON THE BASE PLATE OF THE HYDRAULIC CABIN | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:24:51.000 | Closed |  |  | 2024-12-03T06:37:14.433 | khan, mojammil | PS5 - Milestone C
PL-000531 | PS5-05-UR-8100 |  | C | M | 4.29:THE DAMPER COVER IN THE HYDRAULIC CABIN IS BEND. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:25:25.000 | Closed |  |  | 2024-12-03T06:39:52.053 | khan, mojammil | PS5 - Milestone C
PL-000532 | PS5-05-UR-8100 |  | C | M | 4.30:HANDRAIL PAINT DAMAGED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:26:11.000 | Closed |  |  | 2024-12-03T06:43:33.890 | khan, mojammil | PS5 - Milestone C
PL-000533 | PS5-05-UR-8100 |  | B | M | 4.3INSULATION ON MUFFLER FLANGE AREA ARE DAMAGED, NOT PROPERLY SEALED. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:26:33.000 | Closed |  |  | 2024-12-03T06:45:51.887 | khan, mojammil | PS5 - Milestone C
PL-000534 | PS5-05-UR-8100 |  | B | M | 4.32:INSULATION DONE ON MUFFLER HAS MANY OPENING TO EXPOSED AIR. (SUCH AS LIFTING LUG, SUPPORT, CLADDING TO CLADDING AREAS) | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:27:10.000 | Closed |  |  | 2024-12-03T06:56:45.877 | khan, mojammil | PS5 - Milestone C
PL-000535 | PS5-05-UR-8100 |  | C | M | 4.33:MUFFLER BOLTS AND NUTS ARE FULLY RUSTED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:27:37.000 | Closed |  |  | 2024-12-03T06:58:05.293 | khan, mojammil | PS5 - Milestone C
PL-000536 | PS5-05-UR-8100 |  | C | M | 4.34:MUFFLER INSULATED SURFACES & FLANGES FOUND NOT PAINTED.IT SHOULD BE BLACK AS PER TZ-MID-60-UTR2-180023_02_AFC SECTION 4.6. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:28:01.000 | Closed |  |  | 2024-12-03T07:00:35.500 | khan, mojammil | PS5 - Milestone C
PL-000537 | PS5-05-UR-8100 |  | C | M | 4.35:THE WELDING AND GRINDING ON THE MUFFLER EXHAUST PIPE ARE OF POOR QUALITY. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:28:48.000 | Closed |  |  | 2024-12-03T07:03:05.657 | khan, mojammil | PS5 - Milestone C
PL-000540 | PS5-05-UR-8100 |  | C | M | 4.36:THE PIPE IN THE MUFFLER BOX , IS SHOWING SIGNS OF RUST AND IS UNPAINTED. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:29:16.000 | Closed |  |  | 2024-12-03T07:05:27.667 | khan, mojammil | PS5 - Milestone C
PL-000541 | PS5-05-UR-8100 |  | A | M | 4.37:WATER MIST CABINET N2 CYLINDERS DELIVERED WITH PRESSURE. (WE DONT KNOW WHAT TYPE OF GAS INSIDE) | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:30:23.000 | Closed |  |  | 2024-12-03T07:08:29.220 | khan, mojammil | PS5 - Milestone C
PL-000542 | PS5-05-UR-8100 |  | A | M | 4.38:WATER MIST CABINET PTFE TAPE USED FOR THREADED JOINTS. (CYLINDER – VALVE CONNECTIONS) | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:32:21.000 | Closed |  |  | 2024-12-03T07:10:35.490 | khan, mojammil | PS5 - Milestone C
PL-000546 | PS5-05-UR-8100 |  | A | M | 4.39:THE KEY SEEMS TO BE MALFUNCTIONING AND ISN'T OPENING THE DOOR | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:33:04.000 | Closed |  |  | 2024-12-03T07:13:35.710 | khan, mojammil | PS5 - Milestone C
PL-000547 | PS5-05-UR-8100 |  | C | M | 4.40:WATER MIST CABINET PAINTED IN WHITE. IT SHOULD BE RED AS PER TZ-MID-60-WPR2-120001 (SECTION 6.2, PAGE 11/39) | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:34:31.000 | Closed |  | No action required since as per latest project documendation | 2024-12-03T07:15:46.240 | khan, mojammil | PS5 - Milestone C
PL-000548 | PS5-05-UR-8100 |  | C | M | 4.41:THERE IS A CRACK IN THE WELD OF THE MIST CABIN | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:35:19.000 | Closed |  |  | 2024-12-03T07:21:55.260 | khan, mojammil | PS5 - Milestone C
PL-000549 | PS5-05-UR-8100 |  | C | M | 4.42:MIST CABIN AND MUFFLER PAINT DAMAGED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:35:51.000 | Closed |  |  | 2024-12-03T07:23:55.040 | khan, mojammil | PS5 - Milestone C
PL-000550 | PS5-05-UR-8100 |  | C | M | 4.43:SPARE INSULATION , CLADDING (TO INSULATE AND CLAD MUFFLER RELATED JOINTS), ATTACHMENT BOLT SET, NOT RECEIVED, AND DETAILED PACKING LIST IS NOT AVAILABLE. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2024-12-03T07:31:34.630 | khan, mojammil | PS5 - Milestone C
PL-000564 | PS5-61-IDH-3100A |  | A | E | Revision to Sulzer/NIDEC wiring for VSD for the General Alarm and General Trips. | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A | 2025-06-24T01:31:43.000 | Closed |  |  | 2024-12-16T06:05:26.997 | Thao-my, Alexandre | PS5 - Milestone H
PL-000565 | PS5-61-IDH-3100B |  | A | E | Revision to Sulzer/NIDEC wiring for VSD for the General Alarm and General Trips. | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B | 2025-06-24T01:32:58.000 | Closed |  |  | 2024-12-16T06:05:26.997 | Thao-my, Alexandre | PS5 - Milestone H
PL-000566 | PS5-61-IDH-3100C |  | A | E | Revision to Sulzer/NIDEC wiring for VSD for the General Alarm and General Trips. | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C | 2025-06-24T01:33:40.000 | Closed |  |  | 2024-12-16T06:05:26.997 | Thao-my, Alexandre | PS5 - Milestone H
PL-000612 | PS5-05-UR-8100 |  | A | M | Swapping of Radiator isolator/Engine isolator | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:42:31.000 | Closed |  | Unatrac shall do the reparation before commissioning | 2025-01-07T07:07:49.000 | Benyahia, Zied | PS5 - Milestone C
PL-000621 | PS5-60-UR-8100E |  | A | E | Potential transformer connection inside the alternator box | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | the cables shll be connected before commissioning | 2025-01-08T07:17:02.000 | Benyahia, Zied | PS5 - Milestone D
PL-000622 | PS5-60-UR-8100E |  | A | E | CTs at the alternator Juncon Box Jumpered (2CT1/2CT2) | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | Jumper will be removed during the installation of the respective interconnecting cables. | 2025-01-08T07:21:03.000 | Benyahia, Zied | PS5 - Milestone D
PL-000623 | PS5-60-UR-8100F |  | A | E | Potential transformer connections inside the | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  | the cables shall be connected before commissioning | 2025-01-08T07:28:51.000 | Benyahia, Zied | PS5 - Milestone D
PL-000624 | PS5-60-UR-8100F |  | A | E | CTs at the alternator Juncon Box are Jumpered (2CT1/2CT2) | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  | Jumper will be removed during the installation of the respective interconnecting cables | 2025-01-08T10:23:35.000 | Benyahia, Zied | PS5 - Milestone D
PL-000702 | PS5-61-IU-3100A |  | C | M | 4:Found radiator bottom and top angle bar support bolt & nuts need to be tighted properly. | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | need to tight properly | 2025-02-14T06:37:09.690 | khan, mojammil | PS5 - Milestone H
PL-000703 | PS5-61-IU-3100A |  | C | M | 4.1:Found all transformer radiator support paint need to be provided | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-02-14T06:42:56.640 | khan, mojammil | PS5 - Milestone H
PL-000704 | PS5-61-IU-3100B |  | C | M | 4:Found radiator bottom area unpainted steel angle bar support need to be painted | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-02-14T06:48:12.390 | khan, mojammil | PS5 - Milestone H
PL-000705 | PS5-61-IU-3100B |  | C | M | 4.1:Found all transformer radiator support paint need to be provided | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-02-14T06:50:24.463 | khan, mojammil | PS5 - Milestone H
PL-000706 | PS5-61-IU-3100C |  | C | M | 4:Found radiator bottom and top angle bar support bolt & nuts need to be tighted properly. | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-02-14T06:53:08.087 | khan, mojammil | PS5 - Milestone H
PL-000707 | PS5-61-IU-3100C |  | C | M | 4.1:Found all transformer radiator support paint need to be provided | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-02-14T06:54:32.710 | khan, mojammil | PS5 - Milestone H
PL-000711 | PS5-71-PA-3100A |  | A | M | 4:CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | CPP AGI | PS5-71-16 - Diesel Fuel Supply Pump A/B |  | Originated |  |  | 2025-02-17T06:20:18.973 | khan, mojammil | PS5 - Milestone F
PL-000712 | PS5-71-PA-3100B |  | A | M | 4:CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | CPP AGI | PS5-71-16 - Diesel Fuel Supply Pump A/B |  | Originated |  |  | 2025-02-17T06:23:09.200 | khan, mojammil | PS5 - Milestone F
PL-000713 | PS5-71-PA-3200 |  | A | M | 4:CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | CPP AGI | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-17T06:28:05.110 | khan, mojammil | PS5 - Milestone F
PL-000720 | PS5-60-UA-5100 |  | C | M | 4:THE WOODEN CRATE IS COMPLETELY SHATTERED. | EPS UNATRAC | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  |  | 2025-02-17T12:20:22.593 | khan, mojammil | PS5 - Milestone B
PL-000721 | PS5-60-UA-5100 |  | B | M | 4.1:THE PRESSURE GAUGE IS SLIGHTLY BENT DUE TO THE IMPACT FROM THE BROKEN WOODEN CRATE. | EPS UNATRAC | PS5-60-27 - Compressed Air Starting Skid | 2026-07-09T12:18:56.000 | Closed |  |  | 2025-02-17T12:32:46.813 | khan, mojammil | PS5 - Milestone B | 2026-07-09T12:18:50.000
PL-000722 | PS5-60-UA-5100 |  | C | M | 4.2:SOME OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  |  | 2025-02-17T12:34:41.193 | khan, mojammil | PS5 - Milestone B
PL-000723 | PS5-60-UA-5100 |  | A | M | 4.3:THE HEAT EXCHANGER PIPE IS BROKEN FROM THE COMPRESSOR HEAD. | EPS UNATRAC | PS5-60-27 - Compressed Air Starting Skid | 2026-07-04T11:06:38.000 | Closed |  |  | 2025-02-17T12:36:18.733 | khan, mojammil | PS5 - Milestone B | 2026-07-04T11:06:34.000
PL-000724 | PS5-60-UA-5100 |  | B | M | 4.4:NO PROPER PACKING LIST PROVIDED FOR COMMISSIONING SPARES | EPS UNATRAC | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  |  | 2025-02-17T12:37:28.093 | khan, mojammil | PS5 - Milestone B
PL-000725 | PS5-60-UA-5100 |  | C | M | 4.5:TRACES OF COOLANT FOUND ON THE TOP OF THE COOLANT TANK | EPS UNATRAC | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  |  | 2025-02-17T12:38:50.090 | khan, mojammil | PS5 - Milestone B
PL-000726 | PS5-60-UA-5100 |  | C | M | 4.6:SOME PARTS ARE COMPLETELY RUSTED | EPS UNATRAC | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  |  | 2025-02-17T12:40:08.083 | khan, mojammil | PS5 - Milestone B
PL-000727 | PS5-60-UO-81100A |  | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A |  | Completed |  | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | 2025-02-17T13:42:54.767 | khan, mojammil | PS5 - Milestone B | 2026-08-13T10:46:27.000
PL-000728 | PS5-60-UO-81100B |  | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B |  | Completed |  | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | 2025-02-17T13:46:54.337 | khan, mojammil | PS5 - Milestone B | 2026-08-13T10:46:55.000
PL-000729 | PS5-60-UO-81100C |  | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C |  | Completed |  | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | 2025-02-17T13:50:18.140 | khan, mojammil | PS5 - Milestone D | 2026-08-13T10:48:22.000
PL-000730 | PS5-60-UO-81100D |  | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D |  | Completed |  | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | 2025-02-17T13:52:20.320 | khan, mojammil | PS5 - Milestone D | 2026-08-13T10:48:54.000
PL-000731 | PS5-60-UO-81100E |  | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-60-53 - Lube Oil Separator Module PS5-60-UO-81100E |  | Completed |  | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | 2025-02-17T13:54:24.543 | khan, mojammil | PS5 - Milestone D | 2026-08-13T10:49:29.000
PL-000732 | PS5-60-UO-81100F |  | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-60-54 - Lube Oil Separator Module PS5-60-UO-81100F |  | Completed |  | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | 2025-02-17T13:56:15.013 | khan, mojammil | PS5 - Milestone D | 2026-08-13T10:50:00.000
PL-000733 | PS5-60-UO-81100G |  | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-60-55 - Lube Oil Separator Module PS5-60-UO-81100G |  | Completed |  | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | 2025-02-17T13:58:01.927 | khan, mojammil | PS5 - Milestone E | 2026-08-13T10:50:32.000
PL-000734 | PS5-60-UZ-8200A |  | C | M | 4:THE PAINT ON THE INJECTOR TIP COOLING MODULE FLANGE IS CRACKED | EPS UNATRAC | PS5-60-35 - Injector Tip Cooling Module A |  | Originated |  |  | 2025-02-18T07:18:51.850 | khan, mojammil | PS5 - Milestone B
PL-000735 | PS5-60-UZ-8200A |  | C | M | 4.1:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | EPS UNATRAC | PS5-60-35 - Injector Tip Cooling Module A |  | Originated |  |  | 2025-02-18T07:21:14.343 | khan, mojammil | PS5 - Milestone B
PL-000736 | PS5-60-UZ-8200B |  | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | EPS UNATRAC | PS5-60-36 - Injector Tip Cooling Module B |  | Originated |  |  | 2025-02-18T07:24:26.520 | khan, mojammil | PS5 - Milestone B
PL-000737 | PS5-60-UZ-8200C |  | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | EPS UNATRAC | PS5-60-37 - Injector Tip Cooling Module C |  | Originated |  |  | 2025-02-18T07:45:32.113 | khan, mojammil | PS5 - Milestone D
PL-000738 | PS5-60-UZ-8200D |  | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | EPS UNATRAC | PS5-60-38 - Injector Tip Cooling Module D |  | Originated |  |  | 2025-02-18T07:47:51.383 | khan, mojammil | PS5 - Milestone D
PL-000739 | PS5-60-UZ-8200E |  | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | EPS UNATRAC | PS5-60-39 - Injector Tip Cooling Module E |  | Originated |  |  | 2025-02-18T07:51:00.700 | khan, mojammil | PS5 - Milestone D
PL-000740 | PS5-60-UZ-8200F |  | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | EPS UNATRAC | PS5-60-40 - Injector Tip Cooling Module F |  | Originated |  |  | 2025-02-18T07:53:08.670 | khan, mojammil | PS5 - Milestone D
PL-000741 | PS5-60-VS-9100A |  | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | EPS UNATRAC | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A | 2026-07-09T12:19:52.000 | Closed |  |  | 2025-02-18T08:06:35.387 | khan, mojammil | PS5 - Milestone B | 2026-07-09T12:19:48.000
PL-000742 | PS5-60-VS-9100B |  | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | EPS UNATRAC | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B | 2026-07-09T12:20:30.000 | Closed |  |  | 2025-02-18T08:09:43.510 | khan, mojammil | PS5 - Milestone B | 2026-07-09T12:20:26.000
PL-000743 | PS5-60-VS-9100B |  | B | M | 4.1:WATER INGRESS HAS BEEN DETECTED INSIDE THE MIST ELIMINATOR AND THE MOTOR | EPS UNATRAC | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B |  | Originated |  |  | 2025-02-18T08:11:54.570 | khan, mojammil | PS5 - Milestone B
PL-000744 | PS5-60-VS-9100C |  | B | M | 4:WATER INGRESS HAS BEEN DETECTED INSIDE THE MIST ELIMINATOR AND THE MOTORS. | EPS UNATRAC | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C |  | Originated |  |  | 2025-02-18T08:15:07.650 | khan, mojammil | PS5 - Milestone D
PL-000745 | PS5-60-VS-9100C |  | B | M | 4.1:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | EPS UNATRAC | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C |  | Originated |  |  | 2025-02-18T08:18:23.187 | khan, mojammil | PS5 - Milestone D
PL-000746 | PS5-60-VS-9100D |  | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | EPS UNATRAC | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D |  | Originated |  |  | 2025-02-18T08:22:04.193 | khan, mojammil | PS5 - Milestone D
PL-000747 | PS5-60-VS-9100E |  | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | EPS UNATRAC | PS5-60-46 - Oil Mist Separator Skid PS5-60-VS-9100E |  | Originated |  |  | 2025-02-18T08:24:41.093 | khan, mojammil | PS5 - Milestone D
PL-000748 | PS5-60-VS-9100F |  | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | EPS UNATRAC | PS5-60-47 - Oil Mist Separator Skid PS5-60-VS-9100F |  | Originated |  |  | 2025-02-18T08:27:15.503 | khan, mojammil | PS5 - Milestone D
PL-000749 | PS5-60-VS-9100G |  | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | EPS UNATRAC | PS5-60-48 - Oil Mist Separator Skid PS5-60-VS-9100G |  | Originated |  |  | 2025-02-18T08:29:31.590 | khan, mojammil | PS5 - Milestone E
PL-000750 | PS5-71-UZ-6500 |  | A | E | 4:THE JB DOOR OF THE DO SEPARATOR IS NOT FIXED, AND THE BOLTS ARE MISSING. | EPS UNATRAC | PS5-71-18 - Diesel Separator Module |  | Originated |  |  | 2025-02-18T08:38:17.447 | khan, mojammil | PS5 - Milestone F
PL-000751 | PS5-71-UZ-6800A |  | C | M | 4:SOME OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  |  | 2025-02-18T08:49:40.807 | khan, mojammil | PS5 - Milestone H
PL-000752 | PS5-71-UZ-6800A |  | B | M | 4.1:THE PSV AND FIT WERE IMPROPERLY SECURED, AND WE DISCOVERED THE PSV CARELESSLY DISPLACED, LYING UPSIDE DOWN ON THE GROUND.(NEED TO BE INSTALLED) | EPS UNATRAC | PS5-71-06 - Crude Fuel Separation Module | 2026-07-04T11:17:42.000 | Closed |  |  | 2025-02-18T08:51:42.630 | khan, mojammil | PS5 - Milestone H | 2026-07-04T11:17:31.000
PL-000753 | PS5-71-UZ-6800A |  | A | M | 4.2:THE FCV IS NOT CONNECTED ON A SINGLE SIDE. | EPS UNATRAC | PS5-71-06 - Crude Fuel Separation Module | 2026-07-04T11:18:27.000 | Closed |  |  | 2025-02-18T08:55:07.910 | khan, mojammil | PS5 - Milestone H | 2026-07-04T11:18:21.000
PL-000754 | PS5-71-UZ-6800A |  | A | E | 4.3:Control panel key is missing. | EPS UNATRAC | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  |  | 2025-02-18T08:57:25.680 | khan, mojammil | PS5 - Milestone H
PL-000755 | PS5-71-UZ-6800B |  | A | E | 4:CONTROL PANEL KEY IS MISSING | EPS UNATRAC | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  |  | 2025-02-18T10:48:36.073 | khan, mojammil | PS5 - Milestone H
PL-000756 | PS5-71-UZ-6800B |  | B | M | 4.1:NO LUBE OIL AVAILABLE AT THE VIEWING GLASS. | EPS UNATRAC | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  |  | 2025-02-18T10:53:05.193 | khan, mojammil | PS5 - Milestone H
PL-000757 | PS5-71-UZ-6800B |  | C | M | 4.2:A LOT OF OPENINGS ARE NOT PROPERLY PLUGGED | EPS UNATRAC | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  |  | 2025-02-18T10:54:31.563 | khan, mojammil | PS5 - Milestone H
PL-000758 | PS5-71-UZ-6800B |  | A | M | 4.3:THE PSV, FLOW GAUGE, AND SPOOLS ARE NOT INSTALLED AND LYING ON THE GROUND. (NEED TO BE INSTALLED) | EPS UNATRAC | PS5-71-06 - Crude Fuel Separation Module | 2026-07-04T11:19:11.000 | Closed |  |  | 2025-02-18T10:55:58.000 | khan, mojammil | PS5 - Milestone H | 2026-07-04T11:18:53.000
PL-000759 | PS5-60-UZ-8200G |  | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED. | EPS UNATRAC | PS5-60-41 - Injector Tip Cooling Module G |  | Originated |  |  | 2025-02-18T11:09:48.873 | khan, mojammil | PS5 - Milestone E
PL-000760 | PS5-28-VDC-1100 |  | A | M | 4:THE INSULATION RING FOR THE CLOSED DRAIN DRUM IS DAMAGED. | EPS VENDOR | PS5-28-03 - Closed Drain Drum and Pump 01 | 2025-05-27T07:22:04.000 | Closed |  |  | 2025-02-18T11:15:39.000 | khan, mojammil | PS5 - Milestone G
PL-000761 | PS5-28-VDC-1100 |  | C | M | 4.1:THE CLOSED DRAIN DRUM EXHIBITS PAINT DAMAGE. | EPS VENDOR | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  |  | 2025-02-18T11:27:39.877 | khan, mojammil | PS5 - Milestone G
PL-000762 | PS5-28-VDC-1100 |  | B | M | 4.2:NO PACKING NOTE AVAILABLE FOR COMM. & STARTUP SPARES . FOUND- 4INCH 150 ASME GASKET(QUANTITY-1), REGULATOR KNOB, 1 BOLT, 10 STUD BOLT & 20 HEX NUT, 4INCH 150 ASME GASKET(QUANTITY -6) 2 MANUAL. | EPS VENDOR | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  |  | 2025-02-18T11:30:24.337 | khan, mojammil | PS5 - Milestone G
PL-000763 | PS5-71-UZ-6200 |  | C | M | 4:THE CONTAINER IS DAMAGED | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:27:13.087 | khan, mojammil | PS5 - Milestone F
PL-000764 | PS5-71-UZ-6200 |  | C | M | 4.1:THE CONTAINER HAS SIGNIFICANT PAINT DAMAGE. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:32:07.203 | khan, mojammil | PS5 - Milestone F
PL-000765 | PS5-71-UZ-6200 |  | A | E | 4.2:THE TUBE LIGHT FELL FROM ITS ORIGINAL POSITION AND GOT DAMAGED | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:33:14.560 | khan, mojammil | PS5 - Milestone F
PL-000766 | PS5-71-UZ-6200 |  | C | M | 4.3:THE SPOOL FROM THE DISPENSER HAS PAINT DAMAGE. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:35:41.190 | khan, mojammil | PS5 - Milestone F
PL-000767 | PS5-71-UZ-6200 |  | A | M | 4.4:THE METALLIC FLEXIBLE CONNECTION IS BROKEN AND DAMAGED. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:36:53.570 | khan, mojammil | PS5 - Milestone F
PL-000768 | PS5-71-UZ-6200 |  | C | M | 4.5:THE DISPENSER COVERS ARE NOT PROPERLY MOUNTED AND HAVE FALLEN TO THE GROUND. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Completed |  | 4.5:THE DISPENSER COVERS ARE NOT PROPERLY MOUNTED AND HAVE FALLEN TO THE GROUND. | 2025-02-19T10:38:22.530 | khan, mojammil | PS5 - Milestone F | 2026-07-14T12:55:40.000
PL-000769 | PS5-71-UZ-6200 |  | B | M | 4.6:THE GASKET FOR THE SIDE VIEWING GLASS IS DAMAGED. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:41:07.920 | khan, mojammil | PS5 - Milestone F
PL-000770 | PS5-71-UZ-6200 |  | C | M | 4.7:THE NUT & BOLT FOR THE SIDE VIEWING GLASS IS MISSING. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:43:35.527 | khan, mojammil | PS5 - Milestone F
PL-000771 | PS5-71-UZ-6200 |  | C | M | 4.8:THE ROLLING WIRE IS COMPRESSED BENEATH THE STRUCTURE. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:46:10.960 | khan, mojammil | PS5 - Milestone F
PL-000772 | PS5-71-UZ-6200 |  | C | M | 4.9:THE FLOW INDICATOR TRANSMITTER IS NOT MOUNTED OR BOLTED SECURELY. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:47:26.793 | khan, mojammil | PS5 - Milestone F
PL-000773 | PS5-71-UZ-6200 |  | B | M | 4.10:OPENED THE ROOF HATCH, BUT THE KEY IS STILL NOT WORKING; LOCK & KEY NEEDS TO BE REPLACED | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:48:39.033 | khan, mojammil | PS5 - Milestone F
PL-000774 | PS5-71-UZ-6200 |  | C | M | 4.11:THE INLET SPOOL FOR THE VESSEL IS NOT MOUNTED PROPERLY. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:50:22.877 | khan, mojammil | PS5 - Milestone F
PL-000775 | PS5-71-UZ-6200 |  | B | E | 4.12:THE CABLE LAID IN THE WALKWAY NEEDS TO BE REMOVED AND PROPERLY ORGANIZED IN THE CABLE TRAY/CHANNEL. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:53:29.367 | khan, mojammil | PS5 - Milestone F
PL-000776 | PS5-71-UZ-6200 |  | A | E | 4.13:THE CABLE NEEDS TO BE PROTECTED FROM SHARP EDGES. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:55:25.610 | khan, mojammil | PS5 - Milestone F
PL-000777 | PS5-71-UZ-6200 |  | C | M | 4.14:THE CHANNEL SHOULD BE FIXED SECURELY ON BOTH ENDS WITH SCREWS, AND A WIRE TAG SHOULD BE PROVIDED | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:56:38.763 | khan, mojammil | PS5 - Milestone F
PL-000778 | PS5-71-UZ-6200 |  | C | E | 4.15:ALL THE PAPER TAG SHOULD BE REPLACED WITH A STAINLESS STEEL (SS) TAG | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:58:16.937 | khan, mojammil | PS5 - Milestone F
PL-000779 | PS5-71-UZ-6200 |  | C | E | 4.16:ALL INSTRUMENT HANGING TAG (SS TAG) SHOULD BE PROVIDED. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:59:32.210 | khan, mojammil | PS5 - Milestone F
PL-000780 | PS5-71-UZ-6200 |  | C | M | 4.17:THE DISPENSER IS NOT SECURELY FIXED AND IS SHAKING. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T11:01:08.537 | khan, mojammil | PS5 - Milestone F
PL-000781 | PS5-71-UZ-6200 |  | B | M | 4.18:OPENED THE TECHNICAL ROOM DOOR; THE DOOR LOCK WAS JAMMED AND NOW IS WORKING, BUT NOT SMOOTHLY. THE LOCK COVER IS DAMAGED AND NEED TO BE REPLACED, AND THE DOOR FRAME IS NOT FIXED PROPERLY, RESULTING IN HEAVY SHAKING. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T11:02:33.907 | khan, mojammil | PS5 - Milestone F
PL-000782 | PS5-71-UZ-6200 |  | A | E | 4.19:THE TUBE LIGHT HAS FALLEN FROM ITS ORIGINAL POSITION AND IS HANGING IN THE TECHNICAL ROOM. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T11:04:15.070 | khan, mojammil | PS5 - Milestone F
PL-000783 | PS5-71-UZ-6200 |  | C | M | 4.20:TWO NUT BOLTS ARE MISSING FROM THE M LADDER SUPPORT. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T11:05:30.007 | khan, mojammil | PS5 - Milestone F
PL-000812 | PS5-60-UR-8100A |  | C | M | 4:THERE IS A SLIGHT BEND ON THE BODY OF THE ADAPTOR(ADAPTOR Ø650 to Øout 508 L1280 - inlet engine ) | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T05:25:22.300 | khan, mojammil | PS5 - Milestone B
PL-000813 | PS5-60-UR-8100A |  | C | M | 4.1:TWO OF THE STRAIGHT LENGTHS ARE BENT IN THREE PLACES(ADJUSTABLE STRAIGHT LENGTH L2850- 3000mm Ø650) | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T05:29:17.157 | khan, mojammil | PS5 - Milestone B
PL-000814 | PS5-60-UR-8100A |  | C | M | 4.2:FOUND MINOR SCRATCHES, GAPS ON THE OUTER COVER THAT COULD ALLOW WATER ENTRY INTO THE INSULATED AREA ,Gaps not properly filled/sealed, Partially used mastic to seal which have not working(STRAIGHT LENGTH L10000mm DIA 950/1150 EXHAUST LINE) | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T05:47:51.933 | khan, mojammil | PS5 - Milestone B
PL-000815 | PS5-60-UR-8100A |  | B | M | 4.3:A SMALL CUT WAS FOUND ON THE OUTER COVER OF THE STRAIGHT LENGTH L10000mm DIA 950/1150 EXHAUST LINE | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T05:52:30.180 | khan, mojammil | PS5 - Milestone B
PL-000816 | PS5-60-UR-8100A |  | C | M | 4.4:FOUND MINOR SCRATCHES, GAPS ON THE OUTER COVER THAT COULD ALLOW WATER ENTRY INTO THE INSULATED AREA , AND SMALL CUTS .(Gaps not properly filled/sealed, Partially used mastic to seal which have not working)this is general comment for SRN 302 | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T06:07:30.993 | khan, mojammil | PS5 - Milestone B
PL-000817 | PS5-60-UR-8100A |  | C | M | 4.6:FOUND MINOR SCRATCHES, GAPS ON THE OUTER COVER THAT COULD ALLOW WATER ENTRY INTO THE INSULATED AREA , AND SMALL CUTS .(Gaps not properly filled/sealed, Partially used mastic to seal which have not working)-STRAIGHT LENGTH L1250mm DIA 450/650 EXHAUST LINE | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T06:15:35.330 | khan, mojammil | PS5 - Milestone B
PL-000818 | PS5-60-UR-8100A |  | C | M | 4.7:FOUND MINOR SCRATCHES, GAPS ON THE OUTER COVER THAT COULD ALLOW WATER ENTRY INTO THE INSULATED AREA .(Gaps not properly filled/sealed, Partially used mastic to seal which have not working)-ADJUSTABLE LENGTH L6000-6250mm DIA 950/1150 EXHAUST LINE | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T06:21:06.760 | khan, mojammil | PS5 - Milestone B
PL-000819 | PS5-60-UR-8100A |  | B | M | 4.8:NO PROPER PACKING LIST/NOTE AVAILABLE FOR SRN 303 FASTNERS. FOUND BOLT- M12*60=3500, M16*80=450, M30*80=670, M36*80=690, M36*90=60 NUT- M36=750, M12=3500, M16=450 ,, M30=30 WASHER- M36=1500, M13=7000 ,M16=900, M31=700 | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T06:23:27.207 | khan, mojammil | PS5 - Milestone B
PL-000820 | PS5-60-UR-8100A |  | C | M | 4.9:FOUND SOME EXTRA MATERIAL IN SRN 303 (Not mentioned in PL) SILICON NEUTRA- 72 PCS. RIVETS -6 BOX PROETEX PTFE TAPE - 15 PCS ROPE SEAL - 1 PACKET | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T06:26:43.840 | khan, mojammil | PS5 - Milestone B
PL-000821 | PS5-60-UR-8100A |  | B | M | 4.10:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100A | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T06:43:19.377 | khan, mojammil | PS5 - Milestone B
PL-000822 | PS5-60-UR-8100C |  | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100C | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  |  | 2025-02-22T06:46:41.200 | khan, mojammil | PS5 - Milestone D
PL-000823 | PS5-60-UR-8100D |  | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100D | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-02-22T06:49:20.223 | khan, mojammil | PS5 - Milestone D
PL-000824 | PS5-60-UR-8100E |  | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100E | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2025-02-22T06:52:01.410 | khan, mojammil | PS5 - Milestone D
PL-000825 | PS5-60-UR-8100G |  | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100G | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-02-22T06:54:21.090 | khan, mojammil | PS5 - Milestone E
PL-000826 | PS5-60-UR-8100F |  | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100F | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-02-22T06:56:29.570 | khan, mojammil | PS5 - Milestone D
PL-000827 | PS5-60-UR-8100B |  | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100B | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2025-02-22T06:58:22.300 | khan, mojammil | PS5 - Milestone B
PL-000828 | PS5-60-UR-8100G |  | B | E | 4.1: THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41700A/B) | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-02-22T07:08:39.053 | khan, mojammil | PS5 - Milestone E
PL-000829 | PS5-60-UR-8100A |  | B | M | 4.11:THERE IS NO PROPER PACKING LIST, AND ACCORDING TO THE COLLI LIST, 1 REGULATING RING IS MISSING. ONLY 5 RINGS WERE FOUND ACROSS ALL THE BOXES.-SHIPPED LOOSE ITEM SRN 311 | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T07:12:22.210 | khan, mojammil | PS5 - Milestone B
PL-000830 | PS5-60-UR-8100A |  | B | M | 4.12:NO PROPER PACKING LIST AVAILABLE- SRN 311 CAPITAL SPARES | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T07:16:23.553 | khan, mojammil | PS5 - Milestone B
PL-000831 | PS5-60-UR-8100A |  | B | M | 4.13:THE DRYER COVER IS DAMAGED- INSTRUMENTATION AIR STATION PS5-60-UA-5200 | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T07:19:47.480 | khan, mojammil | PS5 - Milestone B
PL-000832 | PS5-60-UR-8100A |  | A | M | 4.14:2 OF THE FLEXIBLE HOSES ARE DAMAGED AND NEEDS REPLACEMENT-INSTRUMENTATION AIR STATION PS5-60-UA-5200 | EPS UNATRAC | PS5-60-01 - Power Generation Package A | 2026-07-04T10:47:37.000 | Closed |  |  | 2025-02-22T07:26:54.290 | khan, mojammil | PS5 - Milestone B | 2026-07-04T10:47:33.000
PL-000833 | PS5-60-UR-8100A |  | A | M | 4.15:THE SPRINGS HAVE BEEN DISPLACED FROM THE BOTTOM OF THE EQUIPMENT.-INSTRUMENTATION AIR STATION PS5-60-UA-5200 | EPS UNATRAC | PS5-60-01 - Power Generation Package A | 2026-07-04T10:54:36.000 | Closed |  |  | 2025-02-22T07:30:38.563 | khan, mojammil | PS5 - Milestone B | 2026-07-04T10:54:30.000
PL-000834 | PS5-60-UR-8100A |  | B | M | 4.16:THE COMPRESSOR COVER GUIDE IS DAMAGED-INSTRUMENTATION AIR STATION PS5-60-UA-5200 | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T07:33:04.730 | khan, mojammil | PS5 - Milestone B
PL-000835 | PS5-60-UR-8100A |  | B | M | 4.17:THE PRV 5206 OUTLET IS NOT PLUGGED.-INSTRUMENTATION AIR STATION PS5-60-UA-5200 | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T07:35:14.213 | khan, mojammil | PS5 - Milestone B
PL-000836 | PS5-60-UR-8100A |  | B | M | 4.18: THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41100A/B) | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T07:49:48.420 | khan, mojammil | PS5 - Milestone B
PL-000837 | PS5-60-UR-8100C |  | B | E | 4.1: THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41300A/B) | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  |  | 2025-02-22T07:52:35.660 | khan, mojammil | PS5 - Milestone D
PL-000838 | PS5-60-UR-8100D |  | B | E | 4.1:THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41400A/B) | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-02-22T07:54:24.980 | khan, mojammil | PS5 - Milestone D
PL-000839 | PS5-60-UR-8100E |  | B | E | 4.1:THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41500A/B) | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2025-02-22T07:56:41.940 | khan, mojammil | PS5 - Milestone D
PL-000840 | PS5-60-UR-8100F |  | B | E | 4.1:THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41600A/B) | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-02-22T07:59:13.960 | khan, mojammil | PS5 - Milestone D
PL-000841 | PS5-60-UR-8100B |  | B | E | 4.1:THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41200A/B) | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2025-02-22T08:01:25.277 | khan, mojammil | PS5 - Milestone B
PL-000842 | PS5-60-UR-8100A |  | C | M | 4.19:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T08:07:59.240 | khan, mojammil | PS5 - Milestone B
PL-000843 | PS5-60-UR-8100C |  | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  |  | 2025-02-22T08:09:48.010 | khan, mojammil | PS5 - Milestone D
PL-000844 | PS5-60-UR-8100D |  | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-02-22T08:13:36.607 | khan, mojammil | PS5 - Milestone D
PL-000845 | PS5-60-UR-8100E |  | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2025-02-22T08:15:48.273 | khan, mojammil | PS5 - Milestone D
PL-000846 | PS5-60-UR-8100G |  | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-02-22T08:19:28.137 | khan, mojammil | PS5 - Milestone E
PL-000847 | PS5-60-UR-8100F |  | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-02-22T08:21:41.097 | khan, mojammil | PS5 - Milestone D
PL-000848 | PS5-60-UR-8100B |  | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2025-02-22T08:23:21.210 | khan, mojammil | PS5 - Milestone B
PL-000849 | PS5-60-UR-8100G |  | C | M | 4.3:THE Y-PIECE IS BENT AT A CERTAIN POINT. | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-02-22T08:26:05.923 | khan, mojammil | PS5 - Milestone E
PL-000850 | PS5-60-UR-8100A |  | C | M | 4.20:Found Electric compressor motor solenoid valve power and earthing cable damaged for Instrumentation air station package (PS5-60-UA-5200). | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T08:28:41.483 | khan, mojammil | PS5 - Milestone B
PL-000851 | PS5-60-UR-8100A |  | C | M | 4.21:All CO Control panel tag no need to be corrected as per building layout drawing- SRN 311 CO CONTROL CABINET | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T08:31:49.980 | khan, mojammil | PS5 - Milestone B
PL-000852 | PS5-60-UR-8100A |  | C | M | 4.22:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T08:36:49.500 | khan, mojammil | PS5 - Milestone B
PL-000853 | PS5-60-UR-8100C |  | C | M | 4.3:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  |  | 2025-02-22T08:39:39.737 | khan, mojammil | PS5 - Milestone D
PL-000854 | PS5-60-UR-8100D |  | C | M | 4.3:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-02-22T08:41:51.480 | khan, mojammil | PS5 - Milestone D
PL-000855 | PS5-60-UR-8100E |  | C | M | 4.3:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2025-02-22T08:44:07.410 | khan, mojammil | PS5 - Milestone D
PL-000856 | PS5-60-UR-8100G |  | C | M | 4.4:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-02-22T08:48:28.860 | khan, mojammil | PS5 - Milestone E
PL-000857 | PS5-60-UR-8100F |  | C | M | 4.3:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-02-22T08:50:47.640 | khan, mojammil | PS5 - Milestone D
PL-000858 | PS5-60-UR-8100B |  | C | M | 4.3:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2025-02-22T08:54:01.853 | khan, mojammil | PS5 - Milestone B
PL-000859 | PS5-60-UR-8100A |  | B | M | 4.23:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100A | EPS UNATRAC | PS5-60-01 - Power Generation Package A | 2026-07-09T12:22:56.000 | Closed |  |  | 2025-02-22T09:01:14.297 | khan, mojammil | PS5 - Milestone B | 2026-07-09T12:22:52.000
PL-000860 | PS5-60-UR-8100C |  | B | M | 4.4:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100C | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Completed |  |  | 2025-02-22T09:03:39.000 | khan, mojammil | PS5 - Milestone D | 2026-07-09T12:23:32.000
PL-000861 | PS5-60-UR-8100D |  | B | M | 4.4:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100D | EPS UNATRAC | PS5-60-10 - Power Generation Package D | 2026-07-09T12:24:06.000 | Closed |  |  | 2025-02-22T09:06:07.050 | khan, mojammil | PS5 - Milestone D | 2026-07-09T12:24:02.000
PL-000862 | PS5-60-UR-8100E |  | B | M | 4.4:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100E | EPS UNATRAC | PS5-60-13 - Power Generation Package E | 2026-07-09T12:24:31.000 | Closed |  |  | 2025-02-22T09:55:57.997 | khan, mojammil | PS5 - Milestone D | 2026-07-09T12:24:28.000
PL-000863 | PS5-60-UR-8100G |  | B | M | 4.5:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100G | EPS UNATRAC | PS5-60-19 - Power Generation Package G | 2026-07-09T12:24:56.000 | Closed |  |  | 2025-02-22T09:58:29.210 | khan, mojammil | PS5 - Milestone E | 2026-07-09T12:24:52.000
PL-000864 | PS5-60-UR-8100F |  | B | M | 4.4:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100F | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-02-22T10:00:45.063 | khan, mojammil | PS5 - Milestone D
PL-000865 | PS5-60-UR-8100B |  | B | M | 4.4:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100B | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2025-02-22T10:03:05.663 | khan, mojammil | PS5 - Milestone B
PL-000866 | PS5-60-UR-8100E |  | A | M | 4.5:THE AIR STARTING RECEIVER PS5-60-VA-5100E SOLENOID VALVE IS DISCONNECTED AND LYING ON THE GROUND. | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2025-02-22T10:06:26.263 | khan, mojammil | PS5 - Milestone D
PL-000867 | PS5-60-UR-8100F |  | C | M | 4.5:THE MATERIAL OF THE VESSEL IS UNEVEN AND IRREGULAR.(AIR STARTING RECEIVER PS5-60-VA-5100F) | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-02-22T10:09:50.293 | khan, mojammil | PS5 - Milestone D
PL-000868 | PS5-60-UR-8100A |  | B | M | 4.24:THE AIR RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED(PS5-60-VA-5200) | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T10:13:32.147 | khan, mojammil | PS5 - Milestone B
PL-000870 | PS5-28-UZ-8100 |  | B | M | 4:FOUND TYRES WITH BUMPS(H150 PUMP SET +MOTOR+ MOBILE TROLLEY) | EPS VENDOR | PS5-28-10 - Oil Skimmer Package |  | Originated |  |  | 2025-02-24T07:08:52.820 | khan, mojammil | PS5 - Milestone I
PL-000871 | PS5-28-UZ-8100 |  | B | M | 4.1:THE H150 PUMPSET HAS OPENINGS THAT ARE NOT PROPERLY PLUGGED. | EPS VENDOR | PS5-28-10 - Oil Skimmer Package |  | Originated |  |  | 2025-02-24T07:12:47.160 | khan, mojammil | PS5 - Milestone I
PL-000872 | PS5-28-UZ-8100 |  | C | M | 4.2:THE TERMINAL BOX EXHIBITS PAINT DAMAGE.(H150 PUMP SET +MOTOR+ MOBILE TROLLEY) | EPS VENDOR | PS5-28-10 - Oil Skimmer Package |  | Originated |  |  | 2025-02-24T07:14:19.530 | khan, mojammil | PS5 - Milestone I
PL-000873 | PS5-28-UZ-8100 |  | B | M | 4.3:START-UP SPARES ARE NOT AVAILABLE. | EPS VENDOR | PS5-28-10 - Oil Skimmer Package |  | Originated |  |  | 2025-02-24T07:16:39.153 | khan, mojammil | PS5 - Milestone I
PL-000874 | PS5-28-UZ-8100 |  | B | M | 4.4:OVERAGE-FOUND INDUSTRIAL PLUG & SOCKET- OUTLETS DECONTACTOR AND BOXES,CLOSING MECHANISM & SOCKET DXN6. | EPS VENDOR | PS5-28-10 - Oil Skimmer Package |  | Originated |  |  | 2025-02-24T07:18:26.523 | khan, mojammil | PS5 - Milestone I
PL-001011 | PS5-60-IH-0002 |  | C | E | Panel Tag Number need to be provided for PS5-60-IH-0002/1&2 | EPS UNATRAC | PS5-60-22 - Power Gen Master UCP |  | Originated |  |  | 2025-04-01T14:51:16.000 | thurai, Sivakumar | PS5 - Milestone B
PL-001012 | PS5-60-IE-0002A |  | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002A | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-04-02T14:17:32.000 | thurai, Sivakumar | PS5 - Milestone B
PL-001013 | PS5-60-IE-0002B |  | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002B | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2025-04-02T14:22:12.000 | thurai, Sivakumar | PS5 - Milestone B
PL-001014 | PS5-60-IE-0002C |  | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002C | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  |  | 2025-04-02T14:33:50.000 | thurai, Sivakumar | PS5 - Milestone D
PL-001015 | PS5-60-IE-0002D |  | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002D | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-04-02T14:35:35.000 | thurai, Sivakumar | PS5 - Milestone D
PL-001016 | PS5-60-IE-0002E |  | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002E | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2025-04-02T14:37:30.000 | thurai, Sivakumar | PS5 - Milestone D
PL-001017 | PS5-60-IE-0002F |  | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002F | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-04-02T14:40:36.000 | thurai, Sivakumar | PS5 - Milestone D
PL-001018 | PS5-60-IE-0002G |  | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002G | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-04-02T14:42:09.000 | thurai, Sivakumar | PS5 - Milestone E
PL-001019 | PS5-60-IE-0004 |  | B | E | Panel key need to be provided for PS5-60-IE-0004 | EPS UNATRAC | PS5-60-22 - Power Gen Master UCP |  | Originated |  |  | 2025-04-02T14:44:38.000 | thurai, Sivakumar | PS5 - Milestone B
PL-001050 | PS5-60-IH-0001B |  | B | E | Damaged bottom plinth needs to be fixed properly for PS5-60-IH-0001B/3&4 | EPS UNATRAC | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs |  | Originated |  |  | 2025-04-03T08:52:18.000 | thurai, Sivakumar | PS5 - Milestone B
PL-001051 | PS5-60-IH-0001B |  | B | E | Panel C4 compartment door not open need to be rectified for PS5-60-IH-0001B/3&4 | EPS UNATRAC | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs |  | Originated |  |  | 2025-04-03T08:55:08.000 | thurai, Sivakumar | PS5 - Milestone B
PL-001052 | PS5-60-IE-0004 |  | A | E | Workstation desktop package inside mouse missing and need to be provided (4CE251CSBC) | EPS UNATRAC | PS5-60-22 - Power Gen Master UCP |  | Originated |  |  | 2025-04-03T09:04:33.000 | thurai, Sivakumar | PS5 - Milestone B
PL-001228 | PS5-28-VSP-1300A |  | C | M | 4:FOUR JACKING BOLTS ARE FOUND MISSING FROM THE SEAL OIL DRAIN DRUM | EPS VENDOR | PS5-28-13 - Seal Oil Drain Drum & Pump A |  | Originated |  |  | 2025-05-05T13:57:12.470 | khan, mojammil | PS5 - Milestone H
PL-001229 | PS5-28-VSP-1300B |  | C | M | 4:FOUR JACKING BOLTS ARE FOUND MISSING FROM THE SEAL OIL DRAIN DRUM | EPS VENDOR | PS5-28-14 - Seal Oil Drain Drum & Pump B |  | Originated |  |  | 2025-05-05T14:04:56.547 | khan, mojammil | PS5 - Milestone H
PL-001230 | PS5-28-VSP-1300C |  | C | M | 4:FOUR JACKING BOLTS ARE FOUND MISSING FROM THE SEAL OIL DRAIN DRUM | EPS VENDOR | PS5-28-15 - Seal Oil Drain Drum & Pump C |  | Originated |  |  | 2025-05-05T14:06:44.927 | khan, mojammil | PS5 - Milestone H
PL-001231 | PS5-25-PA-3100A |  | B | M | 4:IN THE PACKING LIST, THE M32 CABLE GLAND AND SHROUD SHOULD BE 3, BUT WE RECEIVED ONLY 2 | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:07:41.003 | khan, mojammil | PS5 - Milestone H
PL-001232 | PS5-25-PA-3100A |  | C | M | 4.1:THE PLUGS FOR GATE VALVE 130 AND 134 ARE MISSING | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Completed |  | 4.1:THE PLUGS FOR GATE VALVE 130 AND 134 ARE MISSING | 2025-05-06T08:14:09.707 | khan, mojammil | PS5 - Milestone H | 2026-07-14T13:20:57.000
PL-001233 | PS5-25-PA-3100A |  | B | M | 4.2:PSV 104 CALIBRATION SEAL WIRE IS BROKEN | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:16:34.480 | khan, mojammil | PS5 - Milestone H
PL-001234 | PS5-25-PA-3100A |  | C | M | 4.3:MOTOR TERMINAL BOX SUPPORT IS MISSING | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A | 2025-06-24T01:41:28.000 | Closed |  |  | 2025-05-06T08:22:21.750 | khan, mojammil | PS5 - Milestone H
PL-001235 | PS5-25-PA-3100A |  | A | M | 4.4:FLANGE CONNECTION TO FO 103 – NUT BOLT MISSING | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Completed |  | 4.4:FLANGE CONNECTION TO FO 103 – NUT BOLT MISSING | 2025-05-06T08:23:32.960 | khan, mojammil | PS5 - Milestone H | 2026-07-14T13:23:25.000
PL-001236 | PS5-25-PA-3100A |  | C | E | 4.5:PS5-25-TE-8103A TRAFFOLYTE TAG IS DAMAGED | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:27:45.890 | khan, mojammil | PS5 - Milestone H
PL-001237 | PS5-25-PA-3100A |  | C | M | 4.6:SOME OF THE BOLTS IN THE PUMP BEARING HOUSING ARE RUSTED | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:28:53.153 | khan, mojammil | PS5 - Milestone H
PL-001238 | PS5-25-PA-3100A |  | C | E | 4.7:JB KEYS NOT FOUND | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:30:55.900 | khan, mojammil | PS5 - Milestone H
PL-001239 | PS5-25-PA-3100A |  | B | E | 4.8:TIT 3012 SENSOR NOT PROPERLY SECURE, THE SENSOR IS EXPOSED , NEED TO BE INSTALLED | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:32:18.330 | khan, mojammil | PS5 - Milestone H
PL-001240 | PS5-25-PA-3100A |  | A | E | 4.9:EARTHING POINTS MISSING GROUNDING CONNECTIONS | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:34:24.987 | khan, mojammil | PS5 - Milestone H
PL-001241 | PS5-25-PA-3100A |  | C | E | 4.10:CABLE TAG FOR ORANGE CABLE MISSING(PS5-79-IP-0001) | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:36:05.060 | khan, mojammil | PS5 - Milestone H
PL-001242 | PS5-25-PA-3100A |  | B | M | 4.11:CANOPY & CANOPY SUPPORT MISSING(PS5-25-LIT-8102A) | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:39:29.907 | khan, mojammil | PS5 - Milestone H
PL-001243 | PS5-25-PA-3100A |  | B | M | 4.12:CANOPY MISSING(PS5-25-PIT-8102A) | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:40:54.143 | khan, mojammil | PS5 - Milestone H
PL-001244 | PS5-25-PA-3100A |  | C | E | 4.13:CABLE TAG MISSING FOR ALL IP DEVICES (PS5-79-IP-9902/9003/9004/0003 ) | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:43:08.520 | khan, mojammil | PS5 - Milestone H
PL-001245 | PS5-25-PA-3100A |  | C | M | 4.14:CANOPY NOT PROVIDED FOR JB AS ELECTRONIC COMPONENTS ARE PRESENT INSIDE THE JB(PS5-25-BI-1801A) | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Completed |  | 4.14:CANOPY NOT PROVIDED FOR JB AS ELECTRONIC COMPONENTS ARE PRESENT INSIDE THE JB(PS5-25-BI-1801A) | 2025-05-06T08:45:03.450 | khan, mojammil | PS5 - Milestone H | 2026-07-14T12:58:04.000
PL-001246 | PS5-25-PA-3100B |  | B | M | 4:IN THE PACKING LIST, THE M32 CABLE GLAND AND SHROUD SHOULD BE 3, BUT WE RECEIVED ONLY 2 | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:18:56.730 | khan, mojammil | PS5 - Milestone H
PL-001247 | PS5-25-PA-3100B |  | A | M | 4.1:THE PIPE FLANGE TO THE LUBE OIL COOLER IS MISSING 4 NUTS, BOLTS, AND A GASKET | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Completed |  | 4.1:THE PIPE FLANGE TO THE LUBE OIL COOLER IS MISSING 4 NUTS, BOLTS, AND A GASKET | 2025-05-06T11:21:23.837 | khan, mojammil | PS5 - Milestone H | 2026-07-14T13:00:45.000
PL-001248 | PS5-25-PA-3100B |  | C | M | 4.2:THE MOTOR DM 102 IS NOT SECURED AND IS SHAKING , 2 SCREWS ARE MISSING | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:27:21.360 | khan, mojammil | PS5 - Milestone H
PL-001249 | PS5-25-PA-3100B |  | C | M | 4.3:SOME OF THE BOLTS IN THE PUMP BEARING HOUSING ARE RUSTED | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:29:02.780 | khan, mojammil | PS5 - Milestone H
PL-001250 | PS5-25-PA-3100B |  | C | M | 4.4:THE PLUGS FOR GATE VALVE 132 AND 133 ARE MISSING | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Completed |  | 4.4:THE PLUGS FOR GATE VALVE 132 AND 133 ARE MISSING | 2025-05-06T11:32:12.900 | khan, mojammil | PS5 - Milestone H | 2026-07-14T13:36:12.000
PL-001251 | PS5-25-PA-3100B |  | C | M | 4.5:PSV STUD BOLT IS MISSING | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:33:37.533 | khan, mojammil | PS5 - Milestone H
PL-001252 | PS5-25-PA-3100B |  | C | M | 4.6:MOTOR TERMINAL BOX SUPPORT IS MISSING | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B | 2025-06-24T01:42:20.000 | Closed |  |  | 2025-05-06T11:34:49.033 | khan, mojammil | PS5 - Milestone H
PL-001253 | PS5-25-PA-3100B |  | B | E | 4.7:TIT 3012 SENSOR NOT PROPERLY SECURE, THE SENSOR IS EXPOSED , NEED TO BE INSTALLED | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:36:04.753 | khan, mojammil | PS5 - Milestone H
PL-001255 | PS5-25-PA-3100B |  | C | E | 4.8:JB KEYS NOT FOUND | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:38:10.860 | khan, mojammil | PS5 - Milestone H
PL-001256 | PS5-25-PA-3100B |  | A | M | 4.9:THE TEMP GAUGE, PROVIDED AS A LOOSE ITEM, HAS NO LOCK NUT | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B | 2026-07-04T11:23:18.000 | Closed |  |  | 2025-05-06T11:39:34.617 | khan, mojammil | PS5 - Milestone H | 2026-07-04T11:23:13.000
PL-001257 | PS5-25-PA-3100B |  | A | E | 4.10:EARTHING POINTS MISSING GROUNDING CONNECTIONS | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:40:46.253 | khan, mojammil | PS5 - Milestone H
PL-001258 | PS5-25-PA-3100B |  | C | E | 4.11:CABLE TAG FOR ORANGE CABLE MISSING (PS5-79-IP-0002) | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:42:40.713 | khan, mojammil | PS5 - Milestone H
PL-001259 | PS5-25-PA-3100B |  | B | M | 4.12:CANOPY & CANOPY SUPPORT MISSING (PS5-25-LIT-8102B) | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:43:40.090 | khan, mojammil | PS5 - Milestone H
PL-001260 | PS5-25-PA-3100B |  | B | M | 4.13:CANOPY MISSING (PS5-25-PIT-8102B) | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:44:50.917 | khan, mojammil | PS5 - Milestone H
PL-001261 | PS5-25-PA-3100B |  | C | E | 4.14:CABLE TAG MISSING FOR ALL IP DEVICES (PS5-79-IP-9902/9003/9004/0003) | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:46:02.690 | khan, mojammil | PS5 - Milestone H
PL-001262 | PS5-25-PA-3100B |  | C | M | 4.15:CANOPY NOT PROVIDED FOR JB AS ELECTRONIC COMPONENTS ARE PRESENT INSIDE THE JB .(PS5-25-BI-1801B) | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Completed |  | 4.15:CANOPY NOT PROVIDED FOR JB AS ELECTRONIC COMPONENTS ARE PRESENT INSIDE THE JB .(PS5-25-BI-1801B) | 2025-05-06T11:47:04.653 | khan, mojammil | PS5 - Milestone H | 2026-07-14T13:02:48.000
PL-001263 | PS5-25-PA-3100C |  | B | M | 4:IN THE PACKING LIST, THE M32 CABLE GLAND AND SHROUD SHOULD BE 3, BUT WE RECEIVED ONLY 2 | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:03:17.573 | khan, mojammil | PS5 - Milestone H
PL-001264 | PS5-25-PA-3100C |  | C | M | 4.1:PSV STUD BOLT IS MISSING | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:04:47.263 | khan, mojammil | PS5 - Milestone H
PL-001265 | PS5-25-PA-3100C |  | B | E | 4.2:TIT 3012 SENSOR IS SLIGHTLY BEND AND NOT PROPERLY SECURED, THE SENSOR IS EXPOSED . NEED TO BE INSTALLED | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:09:28.130 | khan, mojammil | PS5 - Milestone H
PL-001266 | PS5-25-PA-3100C |  | C | E | 4.3:JB KEYS NOT FOUND | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:11:18.933 | khan, mojammil | PS5 - Milestone H
PL-001267 | PS5-25-PA-3100C |  | A | M | 4.4:THE TEMP GAUGE, PROVIDED AS A LOOSE ITEM, HAS NO LOCK NUT | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C | 2026-07-04T11:23:55.000 | Closed |  |  | 2025-05-06T12:12:26.217 | khan, mojammil | PS5 - Milestone H | 2026-07-04T11:23:49.000
PL-001268 | PS5-25-PA-3100C |  | C | M | 4.5:THE PLUGS FOR GATE VALVE 132 IS MISSING | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Completed |  | 4.5:THE PLUGS FOR GATE VALVE 132 IS MISSING | 2025-05-06T12:13:40.227 | khan, mojammil | PS5 - Milestone H | 2026-07-14T13:39:30.000
PL-001269 | PS5-25-PA-3100C |  | A | E | 4.6:EARTHING POINTS MISSING GROUNDING CONNECTIONS | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:15:46.017 | khan, mojammil | PS5 - Milestone H
PL-001270 | PS5-25-PA-3100C |  | C | E | 4.7:CABLE TAG FOR ORANGE CABLE MISSING (PS5-79-IP-0003) | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:17:22.493 | khan, mojammil | PS5 - Milestone H
PL-001271 | PS5-25-PA-3100C |  | B | M | 4.8:CANOPY & CANOPY SUPPORT MISSING (PS5-25-LIT-8102C) | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:18:11.450 | khan, mojammil | PS5 - Milestone H
PL-001272 | PS5-25-PA-3100C |  | B | M | 4.9:CANOPY MISSING (PS5-25-PIT-8102C) | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:20:21.223 | khan, mojammil | PS5 - Milestone H
PL-001273 | PS5-25-PA-3100C |  | C | E | 4.10:CABLE TAG MISSING FOR ALL IP DEVICES (PS5-79-IP-9902/9003/9004/0003 ) | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:23:26.277 | khan, mojammil | PS5 - Milestone H
PL-001274 | PS5-25-PA-3100C |  | C | M | 4.11:JB CANOPY MISSING (PS5-25-BI-1274C) | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Completed |  | 4.11:JB CANOPY MISSING (PS5-25-BI-1274C) | 2025-05-06T12:24:24.577 | khan, mojammil | PS5 - Milestone H | 2026-07-14T13:04:55.000
PL-001275 | PS5-25-PA-3100C |  | C | M | 4.12:CANOPY NOT PROVIDED FOR JB AS ELECTRONIC COMPONENTS ARE PRESENT INSIDE THE JB. (PS5-25-BI-1801C) | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Completed |  | 4.12:CANOPY NOT PROVIDED FOR JB AS ELECTRONIC COMPONENTS ARE PRESENT INSIDE THE JB. (PS5-25-BI-1801C) | 2025-05-06T12:25:15.103 | khan, mojammil | PS5 - Milestone H | 2026-07-14T13:06:32.000
PL-001276 | PS5-25-PA-3100C |  | C | M | 4.13:MOTOR TERMINAL BOX SUPPORT IS MISSING | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C | 2025-06-24T01:43:13.000 | Closed |  |  | 2025-05-06T13:03:11.203 | khan, mojammil | PS5 - Milestone H
PL-001303 | PS5-25-UJ-6100 |  | A | M | 4:As per the packing list, 3 PGs were listed, but only 2 were received. One PG is missing. | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A | 2026-07-04T11:24:50.000 | Closed |  |  | 2025-05-08T06:46:41.567 | khan, mojammil | PS5 - Milestone H | 2026-07-04T11:24:46.000
PL-001304 | PS5-25-UJ-6100 |  | B | M | 4.1:Received 2 pressure gauges, both of which are leaking from the dial. Replacement or refilling by the vendor is required | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-08T06:48:38.173 | khan, mojammil | PS5 - Milestone H
PL-001305 | PS5-25-UJ-6100 |  | B | M | 4.2: Missing as per packing list ( 60. Rubber metal cushion, 65.Stud, 70.Wear insert, 80. Hexagon nut not found) | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-08T06:54:43.763 | khan, mojammil | PS5 - Milestone H
PL-001306 | PS5-25-UJ-6100 |  | C | M | 4.3:Overage material (control gear unit received which is not showing in PL) | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-08T07:10:19.573 | khan, mojammil | PS5 - Milestone H
PL-001312 | PS5-71-HE-2400A |  | C | M | 4:FOUND 6 nos CABLE GLANDS 4 nos RTJ GASKETS WHICH ARE NOT SHOWING IN PACKING LIST , 2 nos SLIDING PLATE (OVERAGE) | EPS VENDOR | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-05-08T12:17:13.307 | khan, mojammil | PS5 - Milestone H
PL-001313 | PS5-71-HE-2400A |  | B | M | 4.1:4NOS. GASKETS MISSING (AS PER PL 8NOS.) | EPS VENDOR | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-05-08T12:18:28.107 | khan, mojammil | PS5 - Milestone H
PL-001314 | PS5-71-HE-2400A |  | B | M | 4.2:6NOS. BOLTS MISSING (AS PER PL 12NOS.) | EPS VENDOR | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-05-08T12:19:53.313 | khan, mojammil | PS5 - Milestone H
PL-001315 | PS5-71-HE-2400A |  | B | M | 4.3:12 NOS. NUTS MISSING (AS PER PL 24NOS.) | EPS VENDOR | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-05-08T12:21:21.367 | khan, mojammil | PS5 - Milestone H
PL-001316 | PS5-71-HE-2400A |  | B | M | 4.4:12 NOS. WASHERS MISSING (AS PER PL 24NOS.) | EPS VENDOR | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-05-08T12:24:00.053 | khan, mojammil | PS5 - Milestone H
PL-001317 | PS5-71-HE-2400A |  | C | E | 4.5:ELECTRICAL CABLE ENTRIES WERE NOT PLUGGED | EPS VENDOR | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-05-08T12:24:50.393 | khan, mojammil | PS5 - Milestone H
PL-001318 | PS5-71-HE-2400A |  | B | M | 4.6:4 EACH BOLTS MISSING ON 2 FLANGES | EPS VENDOR | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-05-08T12:26:23.150 | khan, mojammil | PS5 - Milestone H
PL-001319 | PS5-71-HE-2400B |  | B | M | 4:TOTAL 8 BOLTS MISSING ON 2 FLANGES | EPS VENDOR | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-05-08T12:31:46.353 | khan, mojammil | PS5 - Milestone H
PL-001320 | PS5-53-PA-3100A |  | C | M | 4:PAINT DAMAGE IN THE MOTOR TERMINAL BOX | EPS VENDOR | PS5-53-02 - Water Distribution Pump A/B |  | Originated |  |  | 2025-05-08T12:41:56.537 | khan, mojammil | PS5 - Milestone E
PL-001321 | PS5-53-PA-3100B |  | C | M | 4:PAINT DAMAGE IN THE MOTOR TERMINAL BOX | EPS VENDOR | PS5-53-02 - Water Distribution Pump A/B |  | Originated |  |  | 2025-05-08T12:44:29.703 | khan, mojammil | PS5 - Milestone E
PL-001322 | PS5-28-PA-3300 |  | C | M | 4:We received two vertical pumps, but the plugs are not available | EPS VENDOR | PS5-28-06 - Relief Drum and Pump | 2025-07-15T10:31:12.000 | Closed |  |  | 2025-05-08T12:50:38.777 | khan, mojammil | PS5 - Milestone G
PL-001323 | PS5-28-PA-3400 |  | C | M | 4:We received two vertical pumps, but the plugs are not available. | EPS VENDOR | PS5-28-03 - Closed Drain Drum and Pump 01 | 2025-07-15T10:32:56.000 | Closed |  |  | 2025-05-08T12:54:53.423 | khan, mojammil | PS5 - Milestone G
PL-001324 | PS5-25-ZS-1201 |  | B | M | 4:PIG SIGNALLER FLANGE SURFACE IS RUSTED | EPS VENDOR | PS5-25-07 - Export Pipeline Pig Launcher |  | Originated |  |  | 2025-05-08T13:05:11.937 | khan, mojammil | PS5 - Milestone H
PL-001328 | PS5-71-PA-3500A |  | B | M | 4:Oil leakage detected from the pump (PS5-71-PA-3500A) | EPS VENDOR | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  |  | 2025-05-09T11:33:45.840 | khan, mojammil | PS5 - Milestone B
PL-001329 | PS5-71-PA-3500B |  | B | M | 4:Oil leakage detected from the pump (PS5-71-PA-3500B) | EPS VENDOR | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  |  | 2025-05-09T11:41:48.970 | khan, mojammil | PS5 - Milestone B
PL-001330 | PS5-28-PA-3700A |  | B | M | 4:Oil leakage detected from the pump (PS5-28-PA-3700A) | EPS VENDOR | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  |  | 2025-05-09T11:46:39.397 | khan, mojammil | PS5 - Milestone E
PL-001331 | PS5-28-PA-3700A |  | C | M | 4.1:Pump body flanges are rusted (PS5-28-PA-3700A) | EPS VENDOR | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  |  | 2025-05-09T11:49:34.637 | khan, mojammil | PS5 - Milestone E
PL-001332 | PS5-28-PA-3700B |  | B | M | 4:Oil leakage detected from the pump (PS5-28-PA-3700B) | EPS VENDOR | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  |  | 2025-05-09T11:52:20.400 | khan, mojammil | PS5 - Milestone E
PL-001333 | PS5-53-TR-4100 |  | C | M | 4:(PACKAGE NO :6) 10000 X 2000= 2 pcs OVERAGE | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank |  | Originated |  |  | 2025-05-09T12:19:47.953 | khan, mojammil | PS5 - Milestone C
PL-001334 | PS5-53-TR-4100 |  | C | M | 4.1:(PACKAGE NO :10), 120X120X8 = 2000MM LENGTH 1 pcs OVERAGE | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank |  | Originated |  |  | 2025-05-09T12:20:57.993 | khan, mojammil | PS5 - Milestone C
PL-001335 | PS5-53-TR-4100 |  | C | M | 4.2:(PACKAGE: 6 & 7 ) 2 PLATE DAMAGE | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank |  | Completed |  | 4.2:(PACKAGE: 6 & 7 ) 2 PLATE DAMAGE | 2025-05-09T12:21:47.843 | khan, mojammil | PS5 - Milestone C | 2026-08-11T08:55:36.000
PL-001336 | PS5-53-TR-4100 |  | C | M | 4.3:(PACKAGE:14 ) 2 ROOF PLATE DAMAGE | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank |  | Completed |  | 4.3:(PACKAGE:14 ) 2 ROOF PLATE DAMAGE | 2025-05-09T12:24:41.597 | khan, mojammil | PS5 - Milestone C | 2026-08-11T08:56:31.000
PL-001337 | PS5-53-TR-4100 |  | C | M | 4.4:(PACKAGE:15 ) 1 ROOF PLATE DAMAGE | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank |  | Completed |  | 4.4:(PACKAGE:15 ) 1 ROOF PLATE DAMAGE | 2025-05-09T12:26:57.083 | khan, mojammil | PS5 - Milestone C | 2026-08-11T12:32:52.000
PL-001338 | PS5-53-TR-4100 |  | B | M | 4.5:(PACKAGE:10) CURB ANGLE FOUND BEND | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank | 2026-07-09T12:27:31.000 | Closed |  |  | 2025-05-09T12:29:57.073 | khan, mojammil | PS5 - Milestone C | 2026-07-09T12:27:26.000
PL-001339 | PS5-53-TR-4100 |  | A | M | 4.6:THE MG TANK ANODE SHOULD BE SUPPLIED WITH U BOLT, MOUNTING BRACKET, DOUBLE NUT, FLAT WASHER, AND LOCK WASHER; HOWEVER, WE ONLY RECEIVED THE ANODES.(CP SYSTEM MATERIAL , SRN-517) | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank | 2026-07-04T11:27:52.000 | Closed |  |  | 2025-05-09T12:31:25.117 | khan, mojammil | PS5 - Milestone C | 2026-07-04T11:27:46.000
PL-001397 | PS5-78-JC-9100A |  | C | M | 4:ROPE DRUM (GROOVE OF THE STEEL ROPE) OF THE HOIST IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-07T10:56:07.000 | Closed |  |  | 2025-05-10T13:40:29.703 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:13:02.000
PL-001398 | PS5-78-JC-9100A |  | C | M | 4.1:HOOK IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-07T10:56:34.000 | Closed |  |  | 2025-05-10T13:45:40.750 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:13:24.000
PL-001407 | PS5-78-JC-9100A |  | B | E | 4.2:ELECTRICAL PANEL BOARD IS DAMAGED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2025-05-12T05:21:33.850 | khan, mojammil | PS5 - Milestone E
PL-001408 | PS5-78-JC-9100A |  | B | M | 4.3:2 BOLTS MISSING IN PANNEL AT TROLLEY BUMBER | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-07T10:56:58.000 | Closed |  |  | 2025-05-12T05:23:09.017 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:12:23.000
PL-001409 | PS5-78-JC-9100A |  | B | E | 4.4: GROUNTING / EARTHING POINT NOT PROVIDED FOR THE PANNEL BOXES | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-07T10:59:05.000 | Closed |  |  | 2025-05-12T05:25:57.637 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:15:54.000
PL-001410 | PS5-78-JC-9100A |  | B | E | 4.5:CABLE FERRULES NEED TO BE PROVIDED FOR ALL THE PANNEL BOXES | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2025-05-12T05:28:54.887 | khan, mojammil | PS5 - Milestone E
PL-001411 | PS5-78-JC-9100A |  | C | M | 4.6:TAG NUMBERS OF ALL THE PANEL BOX/JBS NEED TO BE FIXED PROPERLY(WITH REVETS OR SCREWS) | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:19:31.000 | Closed |  |  | 2025-05-12T05:30:34.353 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:18:32.000
PL-001412 | PS5-78-JC-9100A |  | A | M | 4.7: PENDANT TRACK IS BEND | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:57:01.000 | Closed |  |  | 2025-05-12T05:39:09.247 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:20:30.000
PL-001413 | PS5-78-JC-9100A |  | B | M | 4.8:PAINT DAMAGE / PARENT METAL DAMAGE FOUND ON GIRDER. | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:19:55.000 | Closed |  |  | 2025-05-12T05:41:30.667 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:22:58.000
PL-001414 | PS5-78-JC-9100A |  | B | M | 4.9:PLATFORM DAMAGED (PAINT AND METAL DAMAGES, SEVERE BENDS ON THE PLATFORM) | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:20:12.000 | Closed |  |  | 2025-05-12T05:43:02.063 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:26:55.000
PL-001415 | PS5-78-JC-9100A |  | B | M | 4.10:THE HANDRAIL HAS PAINT DAMAGE AND IS SEVERELY BENT DUE TO MISHANDLING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:20:26.000 | Closed |  |  | 2025-05-12T05:45:23.443 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:28:52.000
PL-001416 | PS5-78-JC-9100A |  | B | M | 4.11:DOOR LOCK HANDLE IS MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2025-05-12T05:47:40.307 | khan, mojammil | PS5 - Milestone E
PL-001417 | PS5-78-JC-9100A |  | C | M | 4.12:HAND RAIL PAINT DAMAGE | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:20:45.000 | Closed |  |  | 2025-05-12T05:50:16.040 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:30:24.000
PL-001418 | PS5-78-JC-9100A |  | C | M | 4.13:HANDRAIL BOLT NUT MISSING (6 NOS) | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:20:58.000 | Closed |  |  | 2025-05-12T05:51:18.440 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:31:30.000
PL-001419 | PS5-78-JC-9100A |  | C | M | 4.14:CABLE TROLLEYS UNIT IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:21:11.000 | Closed |  |  | 2025-05-12T05:53:34.200 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:33:08.000
PL-001420 | PS5-78-JC-9100A |  | A | M | 4.15:DOOR FIXING SCREWS ARE MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:57:53.000 | Closed |  |  | 2025-05-12T05:55:31.950 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:37:26.000
PL-001421 | PS5-78-JC-9100A |  | A | M | 4.16:C HANGERS NOT RECEIVED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:58:09.000 | Closed |  |  | 2025-05-12T05:56:47.167 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:49:22.000
PL-001422 | PS5-78-JC-9100A |  | C | M | 4.17:THE TRACK ON TOP OF THE OVER HEAD CRANE GIRDER IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:21:39.000 | Closed |  |  | 2025-05-12T05:57:16.187 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:51:12.000
PL-001425 | PS5-78-JC-9100B |  | C | M | 4:ROPE DRUM (GROOVE OF THE STEEL ROPE) OF THE HOIST IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:21:54.000 | Closed |  |  | 2025-05-12T06:28:39.530 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:52:44.000
PL-001426 | PS5-78-JC-9100B |  | C | M | 4.1:PS5-78-DE-352008 HOISTING UNIT PAINT IS DAMAGED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:22:05.000 | Closed |  |  | 2025-05-12T06:29:57.507 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:54:50.000
PL-001427 | PS5-78-JC-9100B |  | B | E | 4.2:GROUNTING / EARTHING PONINT NOT PROVIDED FOR THE PANNEL | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:22:17.000 | Closed |  |  | 2025-05-12T10:44:40.090 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:56:54.000
PL-001428 | PS5-78-JC-9100B |  | B | E | 4.3:CABLE FERRULES NEED TO BE PROVIDED FOR ALL THE PANNEL BOXES | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2025-05-12T10:46:14.990 | khan, mojammil | PS5 - Milestone E
PL-001429 | PS5-78-JC-9100B |  | C | E | 4.4:TAG NUMBERS OF ALL THE PANEL BOX/JBS NEED TO BE FIXED PROPERLY | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:22:36.000 | Closed |  |  | 2025-05-12T12:55:35.047 | khan, mojammil | PS5 - Milestone E | 2026-03-03T11:58:18.000
PL-001430 | PS5-78-JC-9100B |  | B | M | 4.5:PAINT DAMAGE / PARENT METAL DAMAGE FOUND ON GIRDER | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:22:50.000 | Closed |  |  | 2025-05-12T12:57:06.240 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:01:08.000
PL-001431 | PS5-78-JC-9100B |  | C | M | 4.6:HAND RAIL AND PLATFORM PAINT IS DAMAGED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:23:08.000 | Closed |  |  | 2025-05-12T13:04:23.200 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:02:36.000
PL-001432 | PS5-78-JC-9100B |  | B | M | 4.7:DOOR LOCK MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2025-05-12T13:05:43.693 | khan, mojammil | PS5 - Milestone E
PL-001433 | PS5-78-JC-9100B |  | B | M | 4.8:HAND RAIL IS SEVERELY BEND | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:23:22.000 | Closed |  |  | 2025-05-12T13:06:50.373 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:04:49.000
PL-001435 | PS5-78-JC-9100B |  | A | M | 4.9:14 C HANGERS NOT RECEIVED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:58:38.000 | Closed |  |  | 2025-05-12T13:08:38.560 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:06:25.000
PL-001436 | PS5-78-JC-9100B |  | C | M | 4.10:CABLE TROLLEY UNIT IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Completed |  |  | 2025-05-12T13:09:19.490 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:07:28.000
PL-001438 | PS5-78-JC-9100B |  | C | M | 4.11:SWITCH STOP UNIT PAINT IS DAMAGED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Completed |  |  | 2025-05-12T13:13:41.997 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:09:01.000
PL-001447 | PS5-78-JC-9100B |  | C | M | 4.12:6 HAND RAIL BOLTS MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Completed |  |  | 2025-05-12T13:50:59.727 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:09:53.000
PL-001448 | PS5-78-JC-9100B |  | A | M | 4.13:DOOR FIXING SCREWS ARE MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:58:50.000 | Closed |  |  | 2025-05-12T13:52:39.087 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:11:44.000
PL-001449 | PS5-78-JC-9100B |  | B | M | 4.14:2 BOLTS MISSING IN PANNEL AT TROLLEY BUMBER | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:23:43.000 | Closed |  |  | 2025-05-12T13:55:08.380 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:13:22.000
PL-001450 | PS5-78-JC-9100B |  | C | M | 4.15:THE TRACK ON TOP OF THE OVER HEAD CRANE GIRDER IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:24:02.000 | Closed |  |  | 2025-05-12T13:56:35.043 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:15:11.000
PL-001451 | PS5-78-JC-9100C |  | C | M | 4:ROPE DRUM (GROOVE OF THE STEEL ROPE) OF THE HOIST IS RUSTED. | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:24:17.000 | Closed |  |  | 2025-05-13T04:16:46.750 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:16:30.000
PL-001452 | PS5-78-JC-9100C |  | C | M | 4.1:HOOK BLOCK AREA IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:24:31.000 | Closed |  |  | 2025-05-13T04:18:36.447 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:17:34.000
PL-001453 | PS5-78-JC-9100C |  | C | M | 4.2:HOISTING UNIT 2 LOCK NUTS ARE RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:24:46.000 | Closed |  |  | 2025-05-13T04:19:57.870 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:30:14.000
PL-001454 | PS5-78-JC-9100C |  | B | E | 4.3: GROUNTING / EARTHING POINT IS NOT PROVIDED FOR THE PANNEL | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:25:10.000 | Closed |  |  | 2025-05-13T04:21:07.777 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:32:16.000
PL-001455 | PS5-78-JC-9100C |  | B | E | 4.4:CABLE FERRULES NEED TO BE PROVIDED FOR ALL PANNEL BOXES | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2025-05-13T04:23:04.563 | khan, mojammil | PS5 - Milestone E
PL-001456 | PS5-78-JC-9100C |  | C | E | 4.5:TAG NUMBERS OF ALL THE PANEL BOX/JB NEED TO BE FIXED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:25:26.000 | Closed |  |  | 2025-05-13T04:24:22.643 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:33:38.000
PL-001457 | PS5-78-JC-9100C |  | C | M | 4.6:WARNING STICKER IS DAMAGE | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:25:41.000 | Closed |  |  | 2025-05-13T04:26:13.623 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:38:25.000
PL-001458 | PS5-78-JC-9100C |  | B | M | 4.7:2 BOLTS MISSING IN THE PANNEL AT TROLLEY BUMBER | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:25:57.000 | Closed |  |  | 2025-05-13T04:28:06.083 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:39:48.000
PL-001459 | PS5-78-JC-9100C |  | A | M | 4.8:TOOL MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:59:01.000 | Closed |  |  | 2025-05-13T04:29:11.630 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:40:45.000
PL-001460 | PS5-78-JC-9100C |  | B | M | 4.9:PAINT DAMAGE / PARENT METAL DAMAGE FOUND ON GIRDER | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:26:10.000 | Closed |  |  | 2025-05-13T04:30:34.343 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:46:14.000
PL-001461 | PS5-78-JC-9100C |  | A | M | 4.10:PENDANT TRACK IS BEND | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:59:15.000 | Closed |  |  | 2025-05-13T04:31:39.623 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:47:15.000
PL-001462 | PS5-78-JC-9100C |  | B | M | 4.11:3 HAND RAIL SEVERELY BEND DUE TO MISHANDLING. | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:26:28.000 | Closed |  |  | 2025-05-13T04:33:14.527 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:49:23.000
PL-001463 | PS5-78-JC-9100C |  | C | M | 4.12:HAND RAIL & PLATFORM PAINT IS DAMAGED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:26:39.000 | Closed |  |  | 2025-05-13T04:34:29.560 | khan, mojammil | PS5 - Milestone E | 2026-03-03T12:55:43.000
PL-001464 | PS5-78-JC-9100C |  | C | M | 4.13:6 HANDRAIL NUT BOLT MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:26:56.000 | Closed |  |  | 2025-05-13T04:35:58.760 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:26:51.000
PL-001465 | PS5-78-JC-9100C |  | A | M | 4.14:9 DOOR FIXING SCREWS ARE MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:59:46.000 | Closed |  |  | 2025-05-13T04:37:31.917 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:28:31.000
PL-001466 | PS5-78-JC-9100C |  | A | M | 4.15:14 C- HANGERS NOT RECEIVED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:59:58.000 | Closed |  |  | 2025-05-13T04:39:02.837 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:29:47.000
PL-001467 | PS5-78-JC-9100C |  | C | M | 4.16:CABLE TROLLEY UNIT IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:27:12.000 | Closed |  |  | 2025-05-13T04:39:29.410 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:31:14.000
PL-001468 | PS5-78-JC-9100C |  | C | M | 4.17:THE TRACK ON TOP OF THE OVER HEAD CRANE GIRDERE IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:27:26.000 | Closed |  |  | 2025-05-13T04:41:26.090 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:32:29.000
PL-001469 | PS5-78-JC-9100D |  | B | M | The Hoist fan cover/ support found damage and need to be replaced-Damage during transportation | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  | Hoist Fan & Cover need to be changed. During OH crane D testing, Hoist Fan from other unit will be used temporary. | 2025-05-13T04:59:36.240 | khan, mojammil | PS5 - Milestone E
PL-001470 | PS5-78-JC-9100D |  | B | M | The brake resistor found damage and need to be replaced-Damage during transportation | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  | The brake resistor along with VSD unit found damage and need to be replaced. OH crane D will be tested only at Speed 1 and to be re-checked after installation of new resistor. | 2025-05-13T05:00:47.230 | khan, mojammil | PS5 - Milestone E
PL-001471 | PS5-78-JC-9100D |  | C | M | 4.2:HOISTING UNIT IS NOT PROPERLY PACKED. | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:27:55.000 | Closed |  |  | 2025-05-13T05:03:45.267 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:35:11.000
PL-001472 | PS5-78-JC-9100D |  | C | M | 4.3:ROPE DRUM (GROOVE OF THE STEEL ROPE) OF THE HOIST IS RUSTED. | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:28:04.000 | Closed |  |  | 2025-05-13T05:04:35.270 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:36:45.000
PL-001473 | PS5-78-JC-9100D |  | B | M | 4.4:2 BOLTS MISSING IN THE PANNEL OF THE TROLLEY BUMBER | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:28:16.000 | Closed |  |  | 2025-05-13T05:06:44.690 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:38:00.000
PL-001474 | PS5-78-JC-9100D |  | B | E | 4.5:GROUNTING/ EARTHING POINT NOT PROVIDED FOR THE PANEL | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:28:29.000 | Closed |  |  | 2025-05-13T05:08:24.883 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:39:44.000
PL-001475 | PS5-78-JC-9100D |  | B | E | 4.6:CABLE FERRULES NEED TO BE PROVIDED FOR ALL THE PANNEL BOXES | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2025-05-13T05:10:06.553 | khan, mojammil | PS5 - Milestone E
PL-001476 | PS5-78-JC-9100D |  | C | E | 4.7:TAG NUMBERS OF ALL THE PANEL BOX/JBs NEED TO BE FIXED PROPERLY. | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:28:45.000 | Closed |  |  | 2025-05-13T05:14:45.237 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:41:08.000
PL-001477 | PS5-78-JC-9100D |  | B | M | 4.8:PAINT DAMAGE / PARENT METAL DAMAGE FOUND ON THE GIRDER | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:29:00.000 | Closed |  |  | 2025-05-13T05:37:51.150 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:44:11.000
PL-001478 | PS5-78-JC-9100D |  | A | M | 4.9:PENDANT TRACK IS DAMAGED AND BEND. | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T06:00:19.000 | Closed |  |  | 2025-05-13T05:39:04.877 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:45:21.000
PL-001479 | PS5-78-JC-9100D |  | C | M | 4.10:HAND RAIL IS SEVERELY BEND DUE TO MISHANDLING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:29:16.000 | Closed |  |  | 2025-05-13T05:40:23.940 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:46:21.000
PL-001480 | PS5-78-JC-9100D |  | C | M | 4.11:HAND RAIL AND PLATFORM PAINT IS DAMAGED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:29:29.000 | Closed |  |  | 2025-05-13T05:41:18.990 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:47:32.000
PL-001481 | PS5-78-JC-9100D |  | B | M | 4.12:DOOR LOCK HANDLE MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Completed |  | DOOR LOCK HANDLE MISSING | 2025-05-13T05:42:23.837 | khan, mojammil | PS5 - Milestone E | 2026-09-04T08:44:20.000
PL-001482 | PS5-78-JC-9100D |  | A | M | 4.13:ONE OVERAGE BOX OF CARBOLINE FIREPROOF COATING IS LEAKING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T06:00:52.000 | Closed |  |  | 2025-05-13T05:44:14.810 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:50:36.000
PL-001483 | PS5-78-JC-9100D |  | A | M | 4.14:9 DOOR FIXING SCREWS ARE MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T06:01:07.000 | Closed |  |  | 2025-05-13T05:47:49.437 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:51:33.000
PL-001484 | PS5-78-JC-9100D |  | C | M | 4.15:6 HANDRAIL NUT BOLT MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:29:45.000 | Closed |  |  | 2025-05-13T05:48:38.817 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:52:58.000
PL-001485 | PS5-78-JC-9100D |  | A | M | 4.16:14 C HANGERS NOT RECEIVED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T06:01:21.000 | Closed |  |  | 2025-05-13T05:49:41.410 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:54:01.000
PL-001486 | PS5-78-JC-9100D |  | C | M | 4.17:CABLE TROLLEYS UNIT IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:29:59.000 | Closed |  |  | 2025-05-13T05:50:03.787 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:54:53.000
PL-001487 | PS5-78-JC-9100D |  | C | M | 4.18:THE TRACK ON TOP OF THE OVER HEAD CRANE GIRDER IS RUST | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:30:12.000 | Closed |  |  | 2025-05-13T05:51:13.847 | khan, mojammil | PS5 - Milestone E | 2026-03-03T13:56:49.000
PL-001488 | PS5-60-PA-3300 |  | A | M | CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | EPS UNATRAC | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  |  | 2025-05-13T05:58:57.000 | khan, mojammil | PS5 - Milestone E
PL-001490 | PS5-05-UR-8100 |  | A | M | DUE TO THE MISALIGNMENT OF PENETRATIONS BETWEEN EDG & HYDRAULIC CABIN FIRE FIGHTING SYSTEM TUBING CANNOT BE CONNECTED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:42:51.000 | Closed |  |  | 2025-05-14T08:41:21.000 | khan, mojammil | PS5 - Milestone C
PL-001491 | PS5-05-UR-8100 |  | A | M | DUE TO THE MISALIGNMENT OF PENETRATIONS BETWEEN EDG & MIST CABIN FIRE FIGHTING SYSTEM TUBING CANNOT BE CONNECTED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:43:17.000 | Closed |  |  | 2025-05-14T08:42:43.000 | khan, mojammil | PS5 - Milestone C
PL-001547 | PS5-71-PA-3500A |  | A | M | CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | EPS VENDOR | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  |  | 2025-05-20T13:13:15.000 | khan, mojammil | PS5 - Milestone B
PL-001548 | PS5-71-PA-3500B |  | A | M | CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | EPS VENDOR | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  |  | 2025-05-20T13:15:11.000 | khan, mojammil | PS5 - Milestone B
PL-001566 | PS5-53-PA-3100A |  | A | M | USE CAT 15W40 LUBE OIL FOR PRESERVATION, FLUSH AND USE THE PROPER LUBE OIL. | EPS VENDOR | PS5-53-02 - Water Distribution Pump A/B |  | Originated |  |  | 2025-05-22T07:14:32.000 | Guan, Gang | PS5 - Milestone E
PL-001610 | PS5-60-EA-2400A |  | A | M | 4:NOZZLE/BRANCH ZAGGED DUE TO IMPROPER FABRICATION REQUIRED TO BE RECTIFIED | EPS UNATRAC | PS5-60-73 - Engine D Cooling system | 2026-07-04T11:29:06.000 | Closed |  |  | 2025-06-17T07:21:32.003 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-04T11:29:01.000
PL-001614 | PS5-60-EA-2400B |  | C | M | 4:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2025-06-17T07:47:07.520 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001615 | PS5-60-EA-2400B |  | C | M | 4.1:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2025-06-17T07:51:23.963 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001616 | PS5-60-EA-2400B |  | A | M | 4.2:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-73 - Engine D Cooling system | 2026-07-04T11:29:50.000 | Closed |  |  | 2025-06-17T07:53:15.880 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-04T11:29:46.000
PL-001617 | PS5-60-EA-2200A |  | C | M | 4:END COVER OF THE HEADDER(CLADDING) DAMAGE (MAY BE DURING TRANSPORTATION) | EPS UNATRAC | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2025-06-17T08:00:13.967 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001618 | PS5-60-EA-2200A |  | A | M | 4.1:NOZZLE/BRANCH ZAGGED DUE TO IMPROPER FABRICATION REQUIRED TO BE RECTIFIED | EPS UNATRAC | PS5-60-71 - Engine B Cooling system | 2026-07-04T11:30:11.000 | Closed |  |  | 2025-06-17T08:03:04.313 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-07-04T11:30:07.000
PL-001619 | PS5-60-EA-2200A |  | C | M | 4.2:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2025-06-17T08:05:17.257 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001620 | PS5-60-EA-2200A |  | C | M | 4.3:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2025-06-17T08:10:55.580 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001622 | PS5-60-EA-2200A |  | A | M | 4.5:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-71 - Engine B Cooling system | 2026-07-04T11:30:28.000 | Closed |  |  | 2025-06-17T08:14:46.690 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-07-04T11:30:24.000
PL-001623 | PS5-60-EA-2200B |  | C | M | 4:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2025-06-17T08:24:37.577 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001624 | PS5-60-EA-2500A |  | A | M | 4:NOZZLE/BRANCH ZAGGED DUE TO IMPROPER FABRICATION REQUIRED TO BE RECTIFIED | EPS UNATRAC | PS5-60-74 - Engine E Cooling system | 2026-07-04T11:30:46.000 | Closed |  |  | 2025-06-17T10:58:35.220 | mwigamba, john | PS5 - Milestone D | 2026-07-04T11:30:42.000
PL-001625 | PS5-60-EA-2100A |  | C | M | 4:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2025-06-20T11:52:49.453 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001626 | PS5-60-EA-2100A |  | C | M | 4.1:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2025-06-20T11:56:17.243 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001627 | PS5-60-EA-2100A |  | A | M | 4.2:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-70 - Engine A Cooling system | 2026-07-04T11:31:02.000 | Closed |  |  | 2025-06-20T11:58:17.753 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-07-04T11:30:58.000
PL-001628 | PS5-60-EA-2100B |  | C | M | 4:VALVE HANDLE COATING/COVER MISSING | EPS UNATRAC | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2025-06-20T12:04:11.657 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001629 | PS5-60-EA-2100B |  | C | M | 4.1:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2025-06-20T12:07:05.717 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001630 | PS5-60-EA-2100B |  | C | M | 4.2:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2025-06-20T12:08:33.383 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001631 | PS5-60-EA-2100B |  | A | M | 4.3:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-70 - Engine A Cooling system | 2026-07-04T11:31:18.000 | Closed |  |  | 2025-06-20T12:10:11.860 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-07-04T11:31:13.000
PL-001632 | PS5-60-EA-2400A |  | C | M | 4.1:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2025-06-20T12:15:09.803 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001633 | PS5-60-EA-2400A |  | C | M | 4.2:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2025-06-20T12:17:13.537 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001634 | PS5-60-EA-2400A |  | A | M | 4.3:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-73 - Engine D Cooling system | 2026-07-04T11:31:38.000 | Closed |  |  | 2025-06-20T12:18:43.510 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-04T11:31:34.000
PL-001641 | PS5-60-EA-2200B |  | C | M | 4.2:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2025-06-24T07:28:48.907 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001642 | PS5-60-EA-2200B |  | A | M | 4.3:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-71 - Engine B Cooling system | 2026-07-04T11:31:57.000 | Closed |  |  | 2025-06-24T07:30:23.780 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-07-04T11:31:53.000
PL-001643 | PS5-60-EA-2500A |  | C | M | 4.1:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-74 - Engine E Cooling system |  | Originated |  |  | 2025-06-24T07:39:33.820 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001645 | PS5-60-EA-2500A |  | C | M | 4.3:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-74 - Engine E Cooling system |  | Originated |  |  | 2025-06-24T07:42:10.587 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001646 | PS5-60-EA-2500A |  | A | M | 4.4:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-74 - Engine E Cooling system | 2026-07-04T11:32:13.000 | Closed |  |  | 2025-06-24T07:44:26.423 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-04T11:32:09.000
PL-001647 | PS5-60-EA-2500B |  | A | M | 4:HEADDER AND BRANCH GOT SEVERE DAMAGE (May be during transportation) AND NEED TO BE RECTIFIED | EPS UNATRAC | PS5-60-74 - Engine E Cooling system | 2026-07-04T11:32:30.000 | Closed |  |  | 2025-06-24T07:50:41.657 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-04T11:32:26.000
PL-001648 | PS5-60-EA-2500B |  | C | M | 4.1:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-74 - Engine E Cooling system |  | Originated |  |  | 2025-06-24T07:53:06.793 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001650 | PS5-60-EA-2500B |  | C | M | 4.2:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-74 - Engine E Cooling system |  | Originated |  |  | 2025-06-24T10:13:50.907 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001651 | PS5-60-EA-2500B |  | A | M | 4.3:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-74 - Engine E Cooling system | 2026-07-04T11:32:47.000 | Closed |  |  | 2025-06-24T10:17:19.597 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-04T11:32:43.000
PL-001652 | PS5-60-EA-2600A |  | A | M | 4:NOZZLE/BRANCH ZAGGED DUE TO IMPROPER FABRICATION REQUIRED TO BE RECTIFIED | EPS UNATRAC | PS5-60-75 - Engine F Cooling system | 2026-07-04T11:33:17.000 | Closed |  |  | 2025-06-24T10:21:12.453 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-04T11:33:12.000
PL-001653 | PS5-60-EA-2600A |  | C | M | 4.1:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2025-06-24T10:22:53.970 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001655 | PS5-60-EA-2600A |  | C | M | 4.3:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2025-06-24T10:25:07.167 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001656 | PS5-60-EA-2600A |  | A | M | 4.4:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-75 - Engine F Cooling system | 2026-07-04T11:33:34.000 | Closed |  |  | 2025-06-24T10:26:45.200 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-04T11:33:30.000
PL-001657 | PS5-60-EA-2600A |  | A | M | 4.5:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-75 - Engine F Cooling system | 2026-07-04T11:33:52.000 | Closed |  |  | 2025-06-24T10:29:08.727 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-04T11:33:48.000
PL-001658 | PS5-60-EA-2600B |  | C | M | 4:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2025-06-24T10:32:09.147 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001659 | PS5-60-EA-2600B |  | C | M | 4.1:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2025-06-24T10:33:51.483 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001660 | PS5-60-EA-2600B |  | A | M | 4.2:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-75 - Engine F Cooling system | 2026-07-04T11:34:06.000 | Closed |  |  | 2025-06-24T10:35:12.043 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-04T11:34:03.000
PL-001661 | PS5-60-EA-2700A |  | C | M | 4:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2025-06-24T10:39:11.757 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001662 | PS5-60-EA-2700A |  | C | M | 4.1:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2025-06-24T10:40:35.670 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001663 | PS5-60-EA-2700A |  | A | M | 4.2:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-76 - Engine G Cooling system | 2026-07-04T11:34:22.000 | Closed |  |  | 2025-06-24T10:42:09.113 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-07-04T11:34:18.000
PL-001664 | PS5-60-EA-2700B |  | C | M | 4:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2025-06-24T10:44:53.810 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001665 | PS5-60-EA-2700B |  | C | M | 4.1:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2025-06-24T10:46:27.013 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001666 | PS5-60-EA-2700B |  | A | M | 4.2:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-76 - Engine G Cooling system | 2026-07-04T11:34:37.000 | Closed |  |  | 2025-06-24T10:47:46.850 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-07-04T11:34:33.000
PL-001668 | PS5-74-UB-5100 |  | B | M | 4.1:All carbon steel (CS) bolts on the skid are rusted | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:28:39.037 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001669 | PS5-74-UB-5100 |  | B | M | 4.2:Equipment PS5-74-VF-1300B one name plate missing | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:30:10.703 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001670 | PS5-74-UB-5100 |  | C | M | 4.3:Color change observed on galvanizing of equipment and tubing supports. | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:31:38.277 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001671 | PS5-74-UB-5100 |  | C | M | 4.4:Skid base frame was found dirty and not properly cleaned prior to tansportation | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:32:57.240 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001672 | PS5-74-UB-5100 |  | B | M | 4.5:The outlet pressure gauge (PS5-74-PG-5103) needle is not functioning properly (Showing positive pressure ) | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  | Need to varify during precommissioning | 2025-06-28T10:34:08.253 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001673 | PS5-74-UB-5100 |  | B | M | 4.6:Pressure gauge needle pointing below zero, may need to replace | EPS VENDOR | PS5-74-01 - N2 Generation Skid | 2026-07-04T11:36:18.000 | Closed |  | Need to verify during precommissioning | 2025-06-28T10:35:27.423 | THANGARATHINAM, ajikumar | PS5 - Milestone F | 2026-07-04T11:36:13.000
PL-001674 | PS5-74-UB-5100 |  | C | M | 4.7:All stud bolts installed at the flange connections are over length | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:36:36.217 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001675 | PS5-74-UB-5100 |  | C | M | 4.8:Found rust of the SS earthing leg | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:37:48.837 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001676 | PS5-74-UB-5100 |  | C | M | 4.9:Welded area was not properly painted at all earthing boss. | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:39:32.330 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001677 | PS5-74-UB-5100 |  | C | M | 4.10:piping and branch connections were not properly painted | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:40:48.693 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001678 | PS5-74-UB-5100 |  | A | M | 4.11:Pipe to elbow weld joint found ruptured, Need to replace the elbow | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:41:54.310 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001690 | PS5-61-IU-3100A |  | A | M | Oil leakage found from the transformer body nozzle weld area prior to installation | EPS VENDOR | PS5-25-02 - Crude Oil Export Pump A | 2026-07-04T11:37:28.000 | Closed |  | Vender need to be rectified | 2025-07-09T11:26:57.000 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-07-04T11:37:24.000
PL-001691 | PS5-28-UO-8200 |  | C | M | 4:Minor damage found during inspection, suspected to be caused during transportation | EPS VENDOR | PS5-28-11 - Open Drain Interceptor |  | Originated |  |  | 2025-07-11T05:46:26.573 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-001692 | PS5-28-UO-8200 |  | C | M | 4.1:Detials are not clear in the PL/SRN | EPS VENDOR | PS5-28-11 - Open Drain Interceptor |  | Originated |  |  | 2025-07-11T05:48:14.967 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-001693 | PS5-28-UO-8200 |  | C | M | 4.2:Detials are not clear in the PL/SRN | EPS VENDOR | PS5-28-11 - Open Drain Interceptor |  | Originated |  |  | 2025-07-11T05:49:48.353 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-001694 | PS5-28-UO-8200 |  | B | M | 4.3:Minor damage observed inside the drainage interceptor. Also not in the correct position | EPS VENDOR | PS5-28-11 - Open Drain Interceptor |  | Originated |  |  | 2025-07-11T05:51:35.723 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-001695 | PS5-60-UZ-8900B |  | C | M | 4:It was observed that the insulation is not properly sealed | EPS UNATRAC | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  |  | 2025-07-14T05:30:17.370 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001696 | PS5-60-UZ-8900B |  | B | M | 4.1:Pressure gauge (PS5-60-PG-8905B)needle pointing below zero, may need to replace | EPS UNATRAC | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  |  | 2025-07-14T05:38:53.010 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001697 | PS5-60-UZ-8900B |  | B | M | 4.2:Pressure gauge (PS5-60-PG-8901B)needle pointing below zero, may need to replace | EPS UNATRAC | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  |  | 2025-07-14T05:40:33.580 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001698 | PS5-60-UZ-8900B |  | B | M | 4.3:Pressure gauge (PS5-60-PG-8903B)needle pointing positive, may need to replace | EPS UNATRAC | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  |  | 2025-07-14T05:41:55.303 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001699 | PS5-60-UZ-8900C |  | C | M | 4:It was observed that the insulation is not properly sealed | EPS UNATRAC | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C |  | Originated |  |  | 2025-07-14T05:45:08.430 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001700 | PS5-60-UZ-8900D |  | C | M | 4:It was observed that the insulation is not properly sealed | EPS UNATRAC | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D |  | Originated |  |  | 2025-07-14T05:48:21.383 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001701 | PS5-60-UZ-8900D |  | B | M | 4.1:Pressure gauge (PS5-60-PG-8906D)needle pointing below zero, may need to replace | EPS UNATRAC | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D |  | Originated |  |  | 2025-07-14T05:49:32.193 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001703 | PS5-60-UZ-8900E |  | C | M | 4.1:It was observed that the insulation is not properly sealed | EPS UNATRAC | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E |  | Originated |  |  | 2025-07-14T05:52:49.340 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001704 | PS5-60-UZ-8900F |  | C | M | 4:Diesel leak found, but source not yet identified (May be improper cleanning after FAT | EPS UNATRAC | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Originated |  |  | 2025-07-14T05:58:34.740 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001705 | PS5-60-UZ-8900F |  | C | M | 4.1:It was observed that the insulation is not properly sealed | EPS UNATRAC | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Originated |  |  | 2025-07-14T06:00:31.750 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001706 | PS5-60-UZ-8900F |  | B | M | 4.2:Pressure gauge (PS5-60-PG-8902F)needle pointing below zero, may need to replace | EPS UNATRAC | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Originated |  |  | 2025-07-14T06:01:44.090 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001708 | PS5-60-UZ-8900F |  | B | M | 4.4:Pressure gauge (PS5-60-PG-8905F)needle pointing below zero, may need to replace | EPS UNATRAC | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Originated |  |  | 2025-07-14T06:03:30.233 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001709 | PS5-60-UZ-8900G |  | C | M | 4:It was observed that the insulation is not properly sealed | EPS UNATRAC | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G |  | Originated |  |  | 2025-07-14T06:08:53.757 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001710 | PS5-60-UZ-8900G |  | B | M | 4.1:Pressure gauge (PS5-60-PG-8905G) needle pointing positive, may need to replace | EPS UNATRAC | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G |  | Originated |  |  | 2025-07-14T06:10:15.750 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001711 | PS5-60-UZ-8900G |  | B | M | 4.2:Pressure gauge (PS5-60-PG-8902G) needle pointing below zero, may need to replace | EPS UNATRAC | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G |  | Originated |  |  | 2025-07-14T06:11:35.363 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001712 | PS5-60-UZ-8900G |  | B | M | 4.3:Pressure gauge (PS5-60-PG-8903G)needle pointing below zero, may need to replace | EPS UNATRAC | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G |  | Originated |  |  | 2025-07-14T06:13:52.117 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001713 | PS5-61-IU-0001F |  | C | M | 4:Received Material with tag no. PS5-61-BE-0006A, As per PL PS5-61-IU-0001F. | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-07-14T06:22:27.750 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001714 | PS5-61-IU-0001F |  | C | M | 4.1:Transportation packing (Between radiators) were misplaced/ fallen down resulting damage on the edges of the radiators (May be severe) | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-07-14T06:23:56.433 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001715 | PS5-61-IU-0001G |  | C | M | 4:Received Material with tag no. PS5-61-BE-0007A, As per PL PS5-61-IU-0001G. | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-14T06:28:01.390 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001716 | PS5-61-IU-0001G |  | C | M | 4.1:Transportation packing (Between radiators) were misplaced/ fallen down resulting damage on the edges of the radiators (May be severe) | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-14T06:29:42.953 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001717 | PS5-61-IU-0001G |  | C | M | 4.2:Transportation packing (Between radiators) were misplaced/ fallen down resulting damage on the edges of the radiators (May be severe) | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-14T06:30:43.077 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001722 | PS5-61-IU-0001G |  | C | M | 4.7:Transportation packing (Between radiators) were misplaced/ fallen down resulting damage on the edges of the radiators (May be severe) | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-14T06:35:19.930 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001724 | PS5-71-UZ-6400 |  | C | M | 4.1:Found insulation not properly sealed. | EPS UNATRAC | PS5-71-08 - CFO Pre-Pressure Modules |  | Originated |  |  | 2025-07-16T05:38:05.490 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001725 | PS5-71-UZ-6400 |  | B | M | 4.2:Pressure gauge (PS5-71-PG-6401) needle pointing below zero, may need to replace | EPS UNATRAC | PS5-71-08 - CFO Pre-Pressure Modules |  | Originated |  |  | 2025-07-16T05:39:45.773 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001726 | PS5-71-UZ-6400 |  | B | M | 4.3:Pressure gauge (PS5-71-PG-6417)needle pointing below zero, may need to replace | EPS UNATRAC | PS5-71-08 - CFO Pre-Pressure Modules |  | Originated |  |  | 2025-07-16T05:41:07.977 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001727 | PS5-71-UZ-6400 |  | B | M | 4.4:Pressure gauge (PS5-71-PG-6416)needle pointing below zero, may need to replace | EPS UNATRAC | PS5-71-08 - CFO Pre-Pressure Modules |  | Originated |  |  | 2025-07-16T05:43:02.690 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001728 | PS5-71-UZ-6400 |  | B | M | 4.5:Pressure gauge (PS5-71-PG-6414)needle pointing below zero, may need to replace | EPS UNATRAC | PS5-71-08 - CFO Pre-Pressure Modules |  | Originated |  |  | 2025-07-16T05:43:59.540 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001729 | PS5-71-UZ-6400 |  | C | M | 4.6:One loose flame arrester delivered (Overage) without bolts, nuts, and gaskets | EPS UNATRAC | PS5-71-08 - CFO Pre-Pressure Modules |  | Originated |  |  | 2025-07-16T05:45:14.377 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001730 | PS5-60-UR-8200A |  | B | M | 4:Pressure gauge (PS5-60-PI-8207A, PS5-60-PI-8205A, PS5-60-PI-8206A, PS5-60-PI-8208A)needle pointing positive reading, may need to replace | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-07-16T05:48:43.290 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001731 | PS5-60-UR-8200F |  | B | M | 4:Pressure gauge (PS5-60-TI-8308F, PS5-60-TI-8306F, PS5-60-PI-8208F, PS5-60-PI-8206F)needle pointing positive reading, may need to replace | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-07-16T05:51:23.540 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001732 | PS5-60-UR-8200E |  | B | M | 4:Pressure gauge (PS5-60-PI-8207E, PS5-60-PI-8208E, PS5-60-PI-8206E, PS5-60-PI-8205E) needle pointing positive reading, may need to replace | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2025-07-16T05:53:34.177 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001733 | PS5-60-UR-8200D |  | B | M | 4:Pressure gauge (PS5-60-PI-8207D, PS5-60-PI-8205D, PS5-60-PI-8208D, PS5-60-PI-8206D)needle pointing positive reading, may need to replace | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-07-16T05:56:09.177 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001734 | PS5-60-UR-8200C |  | B | M | 4:Pressure gauge (PS5-60-PI-8207C, PS5-60-TI-8306C, PS5-60-PI-8206C, PS5-60-PI-8208C)needle pointing positive reading, may need to replace | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  |  | 2025-07-16T05:58:18.803 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001735 | PS5-60-UR-8200B |  | B | M | 4:Pressure gauge (PS5-60-PI-8207B,PS5-60-PI-8205B, PS5-60-PI-8206B, PS5-60-PI-8208B) needle pointing positive reading, may need to replace | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2025-07-16T06:02:18.753 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001736 | PS5-60-UR-8300C |  | A | E | 4:"Temperature gauge found broken (PS5-60-TI-8308C)" | EPS UNATRAC | PS5-60-37 - Injector Tip Cooling Module C |  | Originated |  |  | 2025-07-16T06:05:29.730 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001737 | PS5-60-UR-8300C |  | B | E | 4.1:Tube support found missing during inspection | EPS UNATRAC | PS5-60-37 - Injector Tip Cooling Module C |  | Originated |  |  | 2025-07-16T06:06:40.950 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001738 | PS5-60-UR-8300C |  | A | M | 4.2:Found plate removed due to not proper welding. | EPS UNATRAC | PS5-60-37 - Injector Tip Cooling Module C | 2026-07-04T11:38:05.000 | Closed |  |  | 2025-07-16T06:08:09.620 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-04T11:38:01.000
PL-001739 | PS5-60-UR-8300F |  | B | M | 4:Found top plate is damaged | EPS UNATRAC | PS5-60-40 - Injector Tip Cooling Module F | 2026-07-09T12:28:57.000 | Closed |  |  | 2025-07-16T06:11:19.610 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-09T12:28:54.000
PL-001740 | PS5-60-UR-8300D |  | A | M | 4:Found plate removed due to not proper welding. | EPS UNATRAC | PS5-60-38 - Injector Tip Cooling Module D | 2026-07-04T11:38:26.000 | Closed |  |  | 2025-07-16T06:13:38.347 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-04T11:38:23.000
PL-001741 | PS5-60-UR-8300D |  | A | M | 4.1:Cracks found on end plate welding. One of the end plate dittached and fallen down. | EPS UNATRAC | PS5-60-38 - Injector Tip Cooling Module D | 2026-07-04T11:38:49.000 | Closed |  |  | 2025-07-16T06:14:40.080 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-04T11:38:46.000
PL-001742 | PS5-60-UR-8300D |  | B | M | 4.2:Found damage on top plate damaged | EPS UNATRAC | PS5-60-38 - Injector Tip Cooling Module D | 2026-07-09T12:29:22.000 | Closed |  |  | 2025-07-16T06:15:49.750 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-09T12:29:17.000
PL-001743 | PS5-60-UR-8300D |  | C | M | 4.3:"Detials not available so not checked " | EPS UNATRAC | PS5-60-38 - Injector Tip Cooling Module D |  | Originated |  |  | 2025-07-16T06:16:43.457 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001744 | PS5-60-LA-0002A |  | B | M | 4:Found panel base damage VMS system cabinet 1 | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-07-16T06:18:57.170 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001746 | PS5-60-EA-2300A |  | A | M | 4.1:Found rust on fan supports due to improper painting | EPS UNATRAC | PS5-60-72 - Engine C Cooling system | 2026-07-04T11:39:55.000 | Closed |  |  | 2025-07-17T13:31:20.050 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-04T11:39:50.000
PL-001747 | PS5-60-EA-2300A |  | C | M | 4.2:"Rust found on outside angle of Luve remote radiator PS5-60-EA-2300A" | EPS UNATRAC | PS5-60-72 - Engine C Cooling system |  | Originated |  |  | 2025-07-17T13:32:36.507 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001748 | PS5-60-EA-2300B |  | A | M | 4:Found rust on fan supports due to improper painting | EPS UNATRAC | PS5-60-72 - Engine C Cooling system | 2026-07-04T11:40:14.000 | Closed |  |  | 2025-07-17T13:35:11.533 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-04T11:40:09.000
PL-001749 | PS5-60-EA-2300B |  | C | M | 4.1:"Rust found on outside angle of Luve remote radiator PS5-60-EA-2300B" | EPS UNATRAC | PS5-60-72 - Engine C Cooling system |  | Originated |  |  | 2025-07-17T13:36:16.247 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001750 | PS5-60-SEA-0001 |  | C | M | 4:Gas Detection Panel PS5-60-SEA-001 arrived as per the packing list, while PS-60-GB-0003 arrived without packing list/SRN and is missing the battery. | EPS VENDOR | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room |  | Originated |  |  | 2025-07-17T13:39:00.383 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001751 | PS5-60-UR-8300G |  | A | M | 4:Tube got severe bend due to the damage of top plate touching (PS5-60-EA-21200G) | EPS UNATRAC | PS5-60-41 - Injector Tip Cooling Module G | 2026-07-04T11:40:53.000 | Closed |  |  | 2025-07-17T13:41:54.393 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-07-04T11:40:48.000
PL-001752 | PS5-60-UR-8300G |  | A | M | 4.1:Tube got severe bend due to the damage of top plate touching (PS 5-60-EA-21100G) | EPS UNATRAC | PS5-60-41 - Injector Tip Cooling Module G | 2026-07-04T11:41:26.000 | Closed |  |  | 2025-07-17T13:42:58.570 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-07-04T11:41:22.000
PL-001753 | PS5-60-UR-8300G |  | A | M | 4.2:Stitch / tack welding broken and end plate displaced from it's location PS5-60-EA-21200G | EPS UNATRAC | PS5-60-41 - Injector Tip Cooling Module G | 2026-07-04T11:41:51.000 | Closed |  |  | 2025-07-17T13:44:18.687 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-07-04T11:41:47.000
PL-001754 | PS5-60-UR-8300G |  | B | M | 4.3:As per packing list, quantity of seal O-rings is 900, but received only 895 | EPS UNATRAC | PS5-60-41 - Injector Tip Cooling Module G |  | Originated |  |  | 2025-07-17T13:45:45.857 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001755 | PS5-60-UR-8200G |  | A | M | 4:As per packing list, 7 Senior Flexonics but received only 5 nos. | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-17T13:51:46.210 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001756 | PS5-60-UR-8200G |  | C | M | 4.1:"No details mentioned in the packing list SO NOT CHECKED (CAT Special tools)""No details mentioned in the packing list SO NOT CHECKED (CAT Special tools)" | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-17T13:54:51.810 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001757 | PS5-60-UR-8200G |  | C | M | 4.2:Paint damage found on oil breather line pipe during inspection | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-17T13:56:39.070 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001758 | PS5-60-UR-8200G |  | C | M | 4.3:Proper details not available for the materials in Colli no:33 | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-17T13:58:13.040 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001759 | PS5-60-UR-8200G |  | B | M | 4.4:During inspection, a leakage of glycerin was found at the pressure gauge. | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  | Need to check while precommissioning | 2025-07-17T13:59:48.240 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001760 | PS5-61-IU-0001D |  | B | M | 4:Signs of leakage were observed in three different locations | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-07-17T14:24:21.180 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001877 | PS5-71-IE-0002 |  | A | E | SFU bar neutral to be tighten | EITS | PS5-71-01 - CFO Storage Tank Feed Heater |  | Completed |  | Tightening of Neutral bar | 2025-08-25T04:58:01.000 | Thao-my, Alexandre | PS5 - Milestone H | 2026-08-16T18:10:16.000
PL-001915 | PS5-61-IU-0001B |  | B | M | 4:Base plate of the transformer found damage on two foots after opening the wooden packing box. This might have happened due to the improper packing of the equipmentfromfactory | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2025-09-08T08:04:01.633 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001919 | PS5-83-EHO-0001A |  | B | M | 4:BOLTS AND NUTS FOR LIGHTING SUPPORT ARE MISING | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-09-09T12:55:40.873 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001920 | PS5-83-EHO-0001A |  | B | M | 4.1:BOLT FOR HAND RAIL BASE PLATE ARE MISSING | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-09-09T12:58:17.260 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001921 | PS5-83-EHO-0001A |  | B | M | 4.2: MINOR DAMAGE OBSERVED ON HVAC COMPRESSOR FINS | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-09-09T13:00:06.060 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001922 | PS5-83-EHO-0001A |  | A | M | 4.3:MAJOR DAMAGE (Might happened during transportation) ON THE MAINTENANCE DOOR AND THE CORNER STRUCTURE OF THE CONTAINER. Door could't open due to this. Need to replace these.Also lot of paint damages on the container. | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Need vendor to repair | 2025-09-09T13:01:20.027 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001923 | PS5-83-EHO-0001A |  | B | M | 4.4: BOLTS DAMAGED IN THE SIDE BOTTOM PORTION OF THE CONTAINER (Transportation damage) | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-09-09T13:02:24.773 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001924 | PS5-83-EHO-0001A |  | C | M | 4.5:E-HOUSE CONTAINER OUT SIDE PAINT DAMAGE | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-09-09T13:04:01.700 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001925 | PS5-83-EHO-0001A |  | B | M | 4.6:LADDER CONNECTING PLATE BOLTS AND NUTS MISING | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-09-09T13:05:33.560 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001926 | PS5-83-EHO-0001A |  | B | M | 4.7:DOOR CAN NOT BE OPEN FROM OUTSIDE DUE TO THE IMPROPER FIXING OF THE HANDLE. NEED TO RECTIFY OR REPLACE BY VENDOR | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-09-09T13:06:52.537 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001927 | PS5-83-EHO-0001B |  | B | M | 4:L CLAMP BOLT (HAND RAIL CONNECTION) MISSING | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-09-09T13:33:59.223 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001944 | PS5-83-EHO-0001B |  | B | M | 4.1: BOLTS DAMAGED IN THE SIDE BOTTOM PORTION OF THE CONTAINER (Transportation damage) | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-09-12T12:58:46.700 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001945 | PS5-83-EHO-0001B |  | A | M | 4.2:WALLMAX PIPE INLET MISSING | EPS VENDOR | PS5-25-03 - Crude Oil Export Pump B | 2026-07-04T11:46:14.000 | Closed |  |  | 2025-09-12T13:02:27.813 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-07-04T11:46:09.000
PL-001946 | PS5-83-EHO-0001B |  | A | M | 4.3:WALLMAX PIPE CABLE ENTRY MISSING | EPS VENDOR | PS5-25-03 - Crude Oil Export Pump B | 2026-07-04T11:46:37.000 | Closed |  |  | 2025-09-12T13:04:45.137 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-07-04T11:46:33.000
PL-001947 | PS5-83-EHO-0001B |  | C | M | 4.4:DOOR CAN NOT BE OPEN FROM OUTSIDE DUE TO THE IMPROPER FIXING OF THE HANDLE. NEED TO RECTIFY OR REPLACE BY VENDOR | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-09-12T13:07:46.543 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001948 | PS5-83-EHO-0001B |  | B | M | 4.5:E-HOUSE CONTAINER OUT SIDE PAINT DAMAGE | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-09-12T13:10:24.867 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001949 | PS5-83-EHO-0001B |  | A | M | 4.6:LADDER CONNECTING PLATE BOLTS NUTS MISING | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Completed |  | 4.6:LADDER CONNECTING PLATE BOLTS NUTS MISING | 2025-09-12T13:13:37.000 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-07-14T13:10:18.000
PL-001950 | PS5-83-EHO-0001C |  | A | M | 4:BOLT FOR HAND RAIL BASE PLATE ARE MISSING | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Completed |  | 4:BOLT FOR HAND RAIL BASE PLATE ARE MISSING | 2025-09-12T13:17:59.000 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-07-14T13:11:31.000
PL-001951 | PS5-83-EHO-0001C |  | A | M | 4.1:TOE GUARD CONNECTING BOLTS ARE MISSING | EPS VENDOR | PS5-25-04 - Crude Oil Export Pump C | 2026-07-04T11:48:08.000 | Closed |  |  | 2025-09-12T13:21:29.380 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-07-04T11:48:04.000
PL-001952 | PS5-83-EHO-0001C |  | A | M | 4.2:L CLAMP (HAND RAIL CONNECTION) MISSING | CPP AGI | PS5-25-04 - Crude Oil Export Pump C | 2026-07-04T11:48:28.000 | Closed |  |  | 2025-09-12T13:23:28.763 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-07-04T11:48:24.000
PL-001953 | PS5-83-EHO-0001C |  | B | M | 4.3:L CLAMP BOLT (HAND RAIL CONNECTION) MISSING | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-09-12T13:25:18.717 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001954 | PS5-83-EHO-0001C |  | B | M | 4.4: BOLTS DAMAGED IN THE SIDE BOTTOM PORTION OF THE CONTAINER (Transportation damage) | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-09-12T13:27:10.227 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001956 | PS5-83-EHO-0001C |  | B | M | 4.6:E HOUSE CONTAINER DAMAGE AND PAINT DAMAGE | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-09-12T13:28:58.410 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001957 | PS5-83-EHO-0001C |  | B | M | 4.7:LADDER CONNECTING PLATE BOLTS NUTS MISING | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-09-12T13:30:09.447 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001959 | PS5-71-PA-3300B |  | C | M | 4:The accumulator’s support was found on the floor during inspection. | EPS VENDOR | PS5-71-05 - CFO Transfer Pump A/B |  | Originated |  |  | 2025-09-22T10:37:15.367 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001960 | PS5-71-PA-3300B |  | C | M | 4.1:The tube support was found on the floor during inspection. | EPS VENDOR | PS5-71-05 - CFO Transfer Pump A/B |  | Originated |  |  | 2025-09-22T10:43:22.050 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001962 | PS5-71-PA-3400B |  | A | M | 4: Signs of leakage were observed in one location. | EPS VENDOR | PS5-71-13 - CFO Service Pump A/B |  | Originated |  |  | 2025-09-22T11:02:01.957 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001963 | PS5-61-IU-0001D |  | B | E | Once opened the box, found the plastic cover containing bolts was not sealed. Only 3(out of 62) bolts were there inside the plastic cover-59nos (M10 X 38 stainless steel) bolts/nuts/ washersaremissing | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-09-23T08:06:40.000 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-002335 | PS5-74-VA-1100 |  | C | M | 4:Found paint damaged at ladder,davit and platform angle | EPS VENDOR | PS5-74-03 - Nitrogen Receiver |  | Originated |  |  | 2025-10-28T12:19:55.440 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002336 | PS5-61-IK-0001 |  | B | E | PS005-E&I-ALL-PL-2439 - ALL CABLE COMPARTMENTS: LABELS FROM OUTGOING FEEDERS SHALL BE BLACK/BROWN/GREY COLOURS | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) | 2026-09-02T13:18:59.000 | Closed | PS005-E&I-ALL-PL-2439 | Refer to Job Card BUILD-COW-0009 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone A | 2026-08-16T18:11:57.000
PL-002340 | PS5-61-IJ-0010 |  | B | E | PS005-E&I-ALL-PL-2451 - ALL CUBICLES: FINAL PROTECTION SETTINGS ARE NOT SET. | EITS | PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010) |  | Originated | PS005-E&I-ALL-PL-2451 | Refer to Job Card BUILD-COW-0011 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone G
PL-002341 | PS5-61-IJ-0011 |  | B | E | PS005-E&I-ALL-PL-2452 - ALL CUBICLES: FINAL PROTECTION SETTINGS ARE NOT SET. | EITS | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated | PS005-E&I-ALL-PL-2452 | Refer to Job Card BUILD-COW-0011 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone G
PL-002344 | PS5-61-IK-0001 |  | B | E | PS005-E&I-ALL-PL-2440 - ALL DRAWERS: FINAL PROTECTION SETTINGS NOT SET COMPLETELY IN DRAWERS | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated | PS005-E&I-ALL-PL-2440 | Refer to Job Card BUILD-COW-0017 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone A
PL-002347 | PS5-61-IJ-0001 |  | B | E | PS005-E&I-ALL-PL-2448 - B04 Cell : Missing 1 set of Mechanical Key Lock = 2 CAMLOCK + 1 Key + 2 Spacer with serial number PH3212 (diameter rear side 10mm) was damage | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) | 2026-08-05T06:07:43.000 | Closed | PS005-E&I-ALL-PL-2448 | Refer to Job Card BUILD-COW-0019 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone D | 2026-08-05T05:43:22.000
PL-002349 | PS5-08-15CB-1001 |  | A | T | PS005-E&I-M4-PL-2586 - Flood light to be tested in tanzania and to be included in the ISMS SAT. | EITS | PS5-08-15 - Security Data Network (SII SP3 SEC) |  | Originated | PS005-E&I-M4-PL-2586 | Will be part of SAT procedure UT-MID-60-SSF1-178660 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone C
PL-002350 | PS5-08-85DC-1007 |  | A | T | PS005-E&I-ETC-PL-2340 - Battery room door contact TBC if Atex required | EITS | PS5-08-85 - Access Control, POB & e-Mustering | 2026-08-04T04:33:43.000 | Closed | PS005-E&I-ETC-PL-2340 | Refer to Job Card BUILD-COW-0021 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone F | 2026-08-03T19:57:51.000
PL-002361 | PS5-09-ACU-0007A-CD01 |  | A | E | PS005-E&I-M4-PL-2366 - Cable One Side Termination (COW) | EITS | PS5-09-05 - HVAC for EITS Building | 2026-07-24T11:55:01.000 | Closed | PS005-E&I-M4-PL-2366 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-24T01:03:25.000
PL-002365 | PS5-06-GB-0001A-CS01 |  | A | E | PS005-E&I-ALL-PL-1584 - Cable one side termination due to battery not install here (COW) | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-16T13:05:23.000 | Closed | PS005-E&I-ALL-PL-1584 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-28T04:03:20.000
PL-002366 | PS5-06-GB-0001A-CS03 |  | A | E | PS005-E&I-ALL-PL-1587 - Cable one side termination due to battery not install here (COW) | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-16T13:06:03.000 | Closed | PS005-E&I-ALL-PL-1587 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-28T04:04:49.000
PL-002367 | PS5-06-GB-0001A-CS02 |  | A | E | PS005-E&I-ALL-PL-1590 - Cable one side termination due to battery not install here (COW) | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-16T13:06:17.000 | Closed | PS005-E&I-ALL-PL-1590 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-28T04:05:55.000
PL-002368 | PS5-06-GB-0001A-CS04 |  | A | E | PS005-E&I-ALL-PL-1593 - Cable one side termination due to battery not install here (COW) | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-16T13:06:32.000 | Closed | PS005-E&I-ALL-PL-1593 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-28T04:06:48.000
PL-002369 | PS5-06-GB-0001B-CS01 |  | A | E | PS005-E&I-ALL-PL-1895 - Cable one side termination due to battery not install here (COW) | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-16T13:06:53.000 | Closed | PS005-E&I-ALL-PL-1895 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-28T04:07:34.000
PL-002370 | PS5-06-GB-0001B-CS03 |  | A | E | PS005-E&I-ALL-PL-1898 - Cable one side termination due to battery not install here (COW) | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-16T13:07:08.000 | Closed | PS005-E&I-ALL-PL-1898 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-28T04:08:17.000
PL-002371 | PS5-06-GB-0001B-CS02 |  | A | E | PS005-E&I-ALL-PL-1901 - Cable one side termination due to battery not install here (COW) | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-16T13:07:21.000 | Closed | PS005-E&I-ALL-PL-1901 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-28T04:09:14.000
PL-002372 | PS5-06-GB-0001B-CS04 |  | A | E | PS005-E&I-ALL-PL-1904 - Cable one side termination due to battery not install here (COW) | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-16T13:07:35.000 | Closed | PS005-E&I-ALL-PL-1904 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-28T04:10:16.000
PL-002373 | PS5-61-IE-0101-CA01 |  | A | T | PS005-E&I-M3-PL-2353 - Cable one side termination due to ECS Work station n/a (cow) | EITS | PS5-61-08 - Electrical Control System |  | Originated | PS005-E&I-M3-PL-2353 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002374 | PS5-61-IE-0101-CA02 |  | A | T | PS005-E&I-M3-PL-2354 - Cable one side termination due to ECS Work station n/a (cow) | EITS | PS5-61-08 - Electrical Control System |  | Originated | PS005-E&I-M3-PL-2354 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002375 | PS5-61-IE-0101-CA03 |  | A | T | PS005-E&I-M3-PL-2355 - Cable one side termination due to ECS Work station n/a (cow) | EITS | PS5-61-08 - Electrical Control System |  | Originated | PS005-E&I-M3-PL-2355 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002378 | PS5-83-OB-0001 |  | A | B | PS005-E&I-M3-PL-2494 - Cable Still Coiled o top ECS Panel and 15CB Panel | EITS | PS5-83-01 - EITS Building | 2026-08-01T13:05:23.000 | Closed | PS005-E&I-M3-PL-2494 | Refer to Job Card BUILD-COW-0308 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A | 2026-08-01T12:33:50.000
PL-002388 | PS5-08-23LA-1001-CV01 |  | A | T | PS005-E&I-ALL-PL-2558 - Coaxial cable to be tested | EITS | PS5-08-23 - VHF Trunk Radio System |  | Originated | PS005-E&I-ALL-PL-2558 | Refer to Job Card BUILD-COW-0105 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone F
PL-002389 | PS5-61-IJ-0001 |  | A | E | PS005-E&I-ALL-PL-2449 - CT Box Not installed and not inspected. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) | 2026-07-30T04:27:20.000 | Closed | PS005-E&I-ALL-PL-2449 | Follow Building Installation Procedures at SITE TZ-MID-63-SSF1-230003 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone D | 2026-05-08T16:59:54.000
PL-002408 | PS5-06-IER-0001A |  | A | E | PS005-E&I-ALL-PL-2587 - Ex stoper plug to be installed for spare hole MCCB Box A | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-27T04:40:53.000 | Closed | PS005-E&I-ALL-PL-2587 | Refer to Job Card BUILD-COW-0134 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-26T12:20:34.000
PL-002410 | PS5-06-IER-0001B |  | A | E | PS005-E&I-ALL-PL-2588 - Ex stoper plug to be installed for spare hole MCCB Box B | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-27T04:41:08.000 | Closed | PS005-E&I-ALL-PL-2588 | Refer to Job Card BUILD-COW-0134 | 2025-11-07T06:30:22.000 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-26T12:21:09.000
PL-002413 | PS5-61-IK-0001 |  | B | E | PS005-E&I-ALL-PL-2441 - INCOMERS: INCOMER A, B AND C MCT CONFIGURATION DOES NOT FIT THE FIELD CABLE SCHEDULE PROVIDED BY EPS IN DESIGN DOSSIER | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated | PS005-E&I-ALL-PL-2441 | Refer to Job Card BUILD-COW-0148 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002414 | PS5-61-JY-0001 |  | C | E | PS005-E&I-ALL-PL-2454 - Maintenance trolley for BlokSet Air Circuit Breakers is missing | EITS | PS5-78-01 - Lifting and handling equipment | 2026-01-19T16:23:38.000 | Closed | PS005-E&I-ALL-PL-2454 | Delivery of the trolley | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone E
PL-002422 | PS5-04-PSC-0001 |  | A | I | PS005-E&I-M4-PL-0357 - Missing component BP3-68FD-03, BP468FD-04 | EITS | PS5-04-04 - 33kV PCS System | 2026-08-31T10:22:41.000 | Closed | PS005-E&I-M4-PL-0357 | Refer to Job Card BUILD-COW-0026 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A | 2026-08-28T05:00:01.000
PL-002423 | PS5-09-IES-0001 |  | C | E | PS005-HVA-ETC-PL-2254 - No access to operate Emergency stop | EITS | PS5-09-05 - HVAC for EITS Building | 2026-04-23T13:39:23.000 | Closed | PS005-HVA-ETC-PL-2254 | Punch to be closed as per TQR - SSF1-TQR-000136 which is accepted by CPY, so punch no more applicable | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A | 2026-04-23T13:39:18.000
PL-002430 | PS5-09-ACU-0007A |  | A | H | PS005-E&I-M6-PL-2308 - One side cable coil /cow | EITS | PS5-09-05 - HVAC for EITS Building | 2026-03-25T16:03:27.000 | Closed | PS005-E&I-M6-PL-2308 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A | 2026-03-25T16:03:24.000
PL-002431 | PS5-09-ACU-0007B |  | A | H | PS005-E&I-M6-PL-2309 - One side cable coil /cow | EITS | PS5-09-05 - HVAC for EITS Building | 2026-03-25T16:03:45.000 | Closed | PS005-E&I-M6-PL-2309 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A | 2026-03-25T16:03:42.000
PL-002448 | PS5-01-LA-0001-CL01 |  | A | E | PS005-E&I-ALL-PL-2589 - Power cable HIPPS Cabinet in General Batch 2 Should be replaced by Fire resistance (Orange cable) | EITS | PS5-0H-01 - HIPPS |  | Originated | PS005-E&I-ALL-PL-2589 | Refer to Job Card BUILD-COW-0083 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone H
PL-002449 | PS5-01-LA-0001-CL02 |  | A | E | PS005-E&I-ALL-PL-2589 - Power cable HIPPS Cabinet in General Batch 2 Should be replaced by Fire resistance (Orange cable) | EITS | PS5-0H-01 - HIPPS |  | Originated | PS005-E&I-ALL-PL-2589 | Refer to Job Card BUILD-COW-0083 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone H
PL-002476 | PS5-61-IK-0001 |  | B | E | PS005-E&I-ALL-PL-2442 - Ring Ethernet cat6 Cables that are extended with coupler to be replaced by longer ones, and should pass through suitable cable opening. | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated | PS005-E&I-ALL-PL-2442 | Refer to Job Card BUILD-COW-0200 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002477 | PS5-02-SGF-0010 |  | C | S | PS005-E&I-ALL-PL-2453 - Safety Kit that are supplied and installed in the substaion have some missing contents, to be check to match Doc. No. UT-MID-60-SSF1-120001 | EITS | PS5-02-01 - Miscellaneous Safety equipment | 2025-12-05T10:21:02.000 | Closed | PS005-E&I-ALL-PL-2453 | Refer to Job Card BUILD-COW-0143 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone H
PL-002484 | PS5-01-LA-0001-CC04 |  | A | I | PS005-E&I-M6-PL-1501 - Termination need to completed in drawing not mention for terminal block AN terminal number in panel ( PS5-01-LA-0001) | EITS | PS5-0H-01 - HIPPS |  | Completed | PS005-E&I-M6-PL-1501 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone H | 2026-08-16T18:15:49.000
PL-002490 | PS5-61-IE-0002-CA07 |  | A | T | PS005-E&I-M2-PL-1347 - Update cable schedule and termination drawing to be confirm by enginnering | EITS | PS5-61-08 - Electrical Control System | 2026-05-19T15:39:49.000 | Closed | PS005-E&I-M2-PL-1347 | Document update | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C | 2026-05-19T15:39:42.000
PL-002491 | PS5-61-IE-0002-CA08 |  | A | T | PS005-E&I-M2-PL-1349 - Update cable schedule and termination drawing to be confirm by enginnering | EITS | PS5-61-08 - Electrical Control System | 2026-05-19T15:40:09.000 | Closed | PS005-E&I-M2-PL-1349 | Document update | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C | 2026-05-19T15:40:05.000
PL-002492 | PS5-61-IE-0002-CA09 |  | A | T | PS005-E&I-M2-PL-1351 - Update cable schedule and termination drawing to be confirm by enginnering | EITS | PS5-61-08 - Electrical Control System | 2026-05-19T15:40:29.000 | Closed | PS005-E&I-M2-PL-1351 | Document update | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C | 2026-05-19T15:40:26.000
PL-002493 | PS5-61-IE-0002-CA10 |  | A | T | PS005-E&I-M2-PL-1353 - Update cable schedule and termination drawing to be confirm by enginnering | EITS | PS5-61-08 - Electrical Control System | 2026-05-19T15:40:48.000 | Closed | PS005-E&I-M2-PL-1353 | Document update | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C | 2026-05-19T15:40:45.000
PL-002494 | PS5-61-IE-0002-CA11 |  | A | T | PS005-E&I-M2-PL-1355 - Update cable schedule and termination drawing to be confirm by enginnering | EITS | PS5-61-08 - Electrical Control System | 2026-05-19T15:41:05.000 | Closed | PS005-E&I-M2-PL-1355 | Document update | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C | 2026-05-19T15:41:02.000
PL-002495 | PS5-61-IE-0002-CA12 |  | A | T | PS005-E&I-M2-PL-1357 - Update cable schedule and termination drawing to be confirm by enginnering | EITS | PS5-61-08 - Electrical Control System | 2026-05-19T15:41:25.000 | Closed | PS005-E&I-M2-PL-1357 | Document update | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C | 2026-05-19T15:41:21.000
PL-002496 | PS5-08-13CB-1001 |  | A | T | PS005-E&I-M1-PL-2325 - Utilities power not tested, to be tested in tanzania | EITS | PS5-08-13 - Safety Data Network (SII SP3 SAF) |  | Originated | PS005-E&I-M1-PL-2325 | Refer to Job Card BUILD-COW-0242 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002497 | PS5-08-11CB-1001 |  | A | T | PS005-E&I-M1-PL-2326 - Utilities power not tested, to be tested in tanzania | EITS | PS5-08-11 - Corporate LAN (SIE) |  | Originated | PS005-E&I-M1-PL-2326 | Refer to Job Card BUILD-COW-0242 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002498 | PS5-08-35CB-1001 |  | A | T | PS005-E&I-M1-PL-2327 - Utilities power not tested, to be tested in tanzania | EITS | PS5-08-35 - Optical Transport Network |  | Originated | PS005-E&I-M1-PL-2327 | Refer to Job Card BUILD-COW-0242 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002499 | PS5-08-15CB-1001 |  | A | T | PS005-E&I-M1-PL-2328 - Utilities power not tested, to be tested in tanzania | EITS | PS5-08-15 - Security Data Network (SII SP3 SEC) |  | Originated | PS005-E&I-M1-PL-2328 | Refer to Job Card BUILD-COW-0242 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002505 | PS5-25-MOV-0012 |  | A | P | Valve damaged by the CPP contractor, It shall be repaired or replaced. | CPP AGI | PS5-25-07 - Export Pipeline Pig Launcher |  | Originated |  | CPP contractor shall repair or Replace the MOV. | 2025-11-07T11:56:36.000 | peela, raja | PS5 - Milestone H
PL-002580 | PS5-74-VA-1100 |  | C | M | 4.1:Handrail bend due to mishandling | EPS VENDOR | PS5-74-03 - Nitrogen Receiver |  | Originated |  |  | 2025-11-21T13:49:52.377 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002581 | PS5-74-VA-1100 |  | B | M | 4.2:As per packing list materials are ok. As per drawing we need more bolts. Which is not appearing in the packing list and didn't receive. (Bolt M16x45 w/nut & washer =20 nos and Bolt M12x45 w/nut & washer = 20 nos) | EPS VENDOR | PS5-74-03 - Nitrogen Receiver | 2026-07-09T12:31:41.000 | Closed |  |  | 2025-11-21T13:54:03.290 | THANGARATHINAM, ajikumar | PS5 - Milestone F | 2026-07-09T12:31:36.000
PL-002589 | PS5-60-TR-4400 |  | B | M | 4.1:The vertical ladder top cage hoop farication is not correct. Required mirror emage of the present fabricated cage hoop | EPS UNATRAC | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump | 2026-07-09T12:32:26.000 | Closed |  |  | 2025-11-25T05:15:54.090 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-07-09T12:32:22.000
PL-002590 | PS5-01-TR-4300 |  | A | M | 4:During inspection, we found the 2" pipe weld at the bottom of the tank (Branch weld joint) is totally broken | EPS VENDOR | PS5-01-05 - Foam Skid | 2026-07-04T11:49:58.000 | Closed |  |  | 2025-11-25T05:27:35.930 | THANGARATHINAM, ajikumar | PS5 - Milestone F | 2026-07-04T11:49:53.000
PL-002591 | PS5-01-TR-4300 |  | A | M | 4.1:The PS4-01-UV-8700 skid was received here instead of the PS5 skid to be replaced with correct one | EPS VENDOR | PS5-01-05 - Foam Skid | 2025-11-27T10:54:13.000 | Closed |  |  | 2025-11-25T05:28:35.337 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002592 | PS5-01-TR-4300 |  | A | M | 4.2:Four flange connections with tag number PS4 have been identified and verified during inspection | EPS VENDOR | PS5-01-05 - Foam Skid | 2025-11-27T11:13:46.000 | Closed |  |  | 2025-11-25T05:30:57.257 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002593 | PS5-28-PR-3900A |  | C | M | 4:During the inspection, it was found that the flange face area had been painted | EPS VENDOR | PS5-28-17 - Reinjection Pump |  | Originated |  |  | 2025-11-25T05:54:41.977 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-002594 | PS5-28-PR-3900A |  | A | M | 4.1:During the inspection, a significant oil leakage was detected on the pump body(Joint) | EPS VENDOR | PS5-28-17 - Reinjection Pump |  | Originated |  |  | 2025-11-25T05:56:03.593 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-002595 | PS5-28-PR-3900A |  | C | M | 4.2:It was observed that the stud installed was shorter than the required length. | EPS VENDOR | PS5-28-17 - Reinjection Pump |  | Originated |  |  | 2025-11-25T06:00:31.907 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-002596 | PS5-28-PR-3900A |  | A | M | 4.3:During the inspection, a significant oil leakage was detected on the boll vave(Joint) | EPS VENDOR | PS5-28-17 - Reinjection Pump |  | Completed |  | 4.3:During the inspection, a significant oil leakage was detected on the boll vave(Joint) | 2025-11-25T06:02:11.630 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-07-14T12:50:30.000
PL-002597 | PS5-28-PR-3900A |  | C | M | 4.4:Found paint damage at pump area | EPS VENDOR | PS5-28-17 - Reinjection Pump |  | Originated |  |  | 2025-11-25T06:03:17.877 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-002598 | PS5-28-PR-3900B |  | A | M | 4:During inspection, a noticeable oil leakage was detected at the discharge valve area of PS5-28-APO-3901B | EPS VENDOR | PS5-28-17 - Reinjection Pump |  | Completed |  | 4:During inspection, a noticeable oil leakage was detected at the discharge valve area of PS5-28-APO-3901B | 2025-11-25T06:07:44.413 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-07-14T12:51:49.000
PL-002599 | PS5-28-PR-3900B |  | C | M | 4.1It was observed that the stud installed was shorter than the required length. | EPS VENDOR | PS5-28-17 - Reinjection Pump |  | Originated |  |  | 2025-11-25T06:09:34.090 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-002600 | PS5-01-UV-8700 |  | C | M | 4:Paint damage and U clamp support missing | EPS VENDOR | PS5-01-05 - Foam Skid |  | Originated |  |  | 2025-11-25T06:57:35.910 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002601 | PS5-01-UV-8700 |  | C | M | 4.1:Found paint damage | EPS VENDOR | PS5-01-05 - Foam Skid |  | Originated |  |  | 2025-11-25T06:58:56.350 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002602 | PS5-01-UV-8700 |  | A | M | 4.2:Hilti hit-HY-200-A was expired | EPS VENDOR | PS5-01-05 - Foam Skid | 2026-07-04T11:50:28.000 | Closed |  |  | 2025-11-25T06:59:52.303 | THANGARATHINAM, ajikumar | PS5 - Milestone F | 2026-07-04T11:50:24.000
PL-002603 | PS5-01-UV-8700 |  | B | M | 4.3:PS5-01-IE-0001A support clamp bolt missing and support clamp was broken-01-IE-0001A support clamp bolt missing and support clamp was broken | EPS VENDOR | PS5-01-05 - Foam Skid |  | Originated |  |  | 2025-11-25T07:01:21.670 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002604 | PS5-01-UV-8700 |  | B | M | 4.4:Junction box stand 2 bolts are missing | EPS VENDOR | PS5-01-05 - Foam Skid |  | Originated |  |  | 2025-11-25T07:02:39.960 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002605 | PS5-01-UV-8700 |  | A | M | 4.5:1" recirculating line piping flange connection bolts 8 nos and spool 2" flange connection bolts 8 nos are not available with spool or skid | EPS VENDOR | PS5-01-05 - Foam Skid |  | Originated |  |  | 2025-11-25T07:04:45.720 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002607 | PS5-71-VSV-1200 |  | B | M | 4.1:During the inspection, it was found that the flange face area had Found bend on the nozzle(N5) - Might have happened due to external impact. Also observed paint damage in the location.(No paint damage on the flange or damageonthebolts)been painted | EPS VENDOR | PS5-71-20 - Diesel Fuel Day Tank | 2026-09-04T08:11:28.000 | Closed |  | During the inspection, it was found that the flange face area had Found bend on the nozzle(N5) - Might have happened due to external impact. Also observed paint damage in the location.(No paint damage on the flange or damageonthebolts)been painted | 2025-11-25T10:55:55.027 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-04-28T08:20:40.000
PL-002608 | PS5-01-PA-3200A |  | B | M | 4:During the inspection, it was found that the gasket (331ID × 348OD × 1.5T) was damaged | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:26:42.997 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002609 | PS5-01-PA-3200A |  | B | M | 4.1:As per the packing list (Equipment No. 12286.347), 12 pieces of 1/2" BSP female elbows were listed; they were not received. | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:28:02.823 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002610 | PS5-01-PA-3200A |  | B | M | 4.2:As per the packing list, 4 units of Stud Coupling A-Lok 8MSC8N-316 were scheduled for delivery; only 2 units were received.. | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:29:13.433 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002611 | PS5-01-PA-3200A |  | A | M | 4.3:Hole diameter for the anchor bolts are is lesser than anchor bolt diameter. Need to enlarge the hole diameter to fit withanchorbolt | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Completed |  |  | 2025-11-25T11:30:22.280 | THANGARATHINAM, ajikumar | PS5 - Milestone C | 2026-04-27T14:18:53.000
PL-002612 | PS5-01-PA-3200A |  | C | M | 4.4:Oil observed at the pump base frame floor area (Oil indicator glass not fixed properly). | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:31:22.463 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002613 | PS5-01-PA-3200A |  | B | M | 4.5:As per the packing list (Equipment No. 13472-711-076-7), 1/2" OD × 16SWG W/T Tubes (4000 mm ) but not received. | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:33:23.817 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002614 | PS5-01-PA-3200B |  | B | M | 4:During the inspection, it was found that the gasket (331ID × 348OD × 1.5T) was damaged | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:37:49.560 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002615 | PS5-01-PA-3200B |  | B | M | 4.1:As per the packing list (Equipment No. 12286.347), 12 pieces of 1/2" BSP female elbows were listed; they were not received. | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:39:01.310 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002616 | PS5-01-PA-3200B |  | B | M | 4.2:As per the packing list, 4 units of Stud Coupling A-Lok 8MSC8N-316 were scheduled for delivery; only 2 units were received.. | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:40:36.643 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002617 | PS5-01-PA-3200B |  | A | M | 4.3:Hole diameter for the anchor bolts are is lesser than anchor bolt diameter. Need to enlarge the hole diameter to fit withanchorbolt | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Completed |  |  | 2025-11-25T11:41:54.210 | THANGARATHINAM, ajikumar | PS5 - Milestone C | 2026-04-27T14:21:19.000
PL-002618 | PS5-01-PA-3200B |  | C | M | 4.4:Oil observed at the pump base frame floor area (Oil indicator glass not fixed properly). | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:42:53.467 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002619 | PS5-01-PA-3200B |  | B | M | 4.5:As per the packing list (Equipment No. 13472-711-076-7), 1/2" OD × 16SWG W/T Tubes (4000 mm ) but not received. | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:44:27.457 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002621 | PS5-01-PA-3100B |  | B | M | 4.1:Plug missing on the 2 nos valves (with pressure gauge) firewaterpumpB | EPS VENDOR | PS5-01-03 - Fire Water Pump B |  | Originated |  |  | 2025-11-25T11:48:23.293 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002622 | PS5-01-PA-3100B |  | B | M | 4.2:Oil was found in this area (may be oil leakage) | EPS VENDOR | PS5-01-03 - Fire Water Pump B |  | Originated |  |  | 2025-11-25T11:49:56.610 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002623 | PS5-01-PA-3100B |  | B | M | 4.3:The cover plate and nuts and bolts are missing. | EPS VENDOR | PS5-01-03 - Fire Water Pump B |  | Originated |  |  | 2025-11-25T11:50:52.343 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002624 | PS5-01-PA-3100B |  | C | M | 4.4:Observed paint damage on the hose | EPS VENDOR | PS5-01-03 - Fire Water Pump B |  | Originated |  |  | 2025-11-25T11:51:58.940 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002625 | PS5-01-PA-3100B |  | A | M | 4.5:Damage observed on pressure gauge | EPS VENDOR | PS5-01-03 - Fire Water Pump B |  | Originated |  |  | 2025-11-25T11:52:52.937 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002626 | PS5-01-PA-3100B |  | B | M | 4.6:Rubber bush / shock absorber found damage. | EPS VENDOR | PS5-01-03 - Fire Water Pump B |  | Originated |  |  | 2025-11-25T11:53:53.100 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002627 | PS5-01-UZ-6900 |  | B | M | 4:During the inspection, some nuts of the overhead pipe supports were found on the floor to be reinstated | EPS VENDOR | PS5-01-10 - Water Mist Package |  | Originated |  |  | 2025-11-25T11:58:55.437 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-002634 | PS5-83-OB-0001 |  | A | M | 4.1:As per the packing list 2 units of EDS-C1-106-002 were scheduled for delivery; only 1 unit was received. | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:17:52.980 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002635 | PS5-83-OB-0001 |  | B | M | 4.2:"As per the packing list PS5-3BC-FP-01 Coverplate on deckplate 1Qty listed; that was not received" | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:21:59.973 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002636 | PS5-83-OB-0001 |  | B | M | 4.3:As per the packing list -PS5-A34-03 Dripping Nose 1Qty listed;that was not received | EPS VENDOR | PS5-83-01 - EITS Building |  | Completed |  |  | 2025-11-27T07:22:59.257 | THANGARATHINAM, ajikumar | PS5 - Milestone A | 2026-07-09T12:34:46.000
PL-002637 | PS5-83-OB-0001 |  | B | M | 4.4:As per the packing list 6 units of EDS-C1-106-002 were scheduled for delivery; only 2 unit were received. | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:24:12.710 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002638 | PS5-83-OB-0001 |  | A | M | 4.5:As per the packing list -BOLT M10*40HDG 40Qty listed;they were not received | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:25:27.557 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002639 | PS5-83-OB-0001 |  | A | M | 4.6:As per the packing list -CLAMP LADDER 40 Qty listed;they were not received | EPS VENDOR | PS5-83-01 - EITS Building | 2026-07-09T12:11:18.000 | Closed |  |  | 2025-11-27T07:27:19.100 | THANGARATHINAM, ajikumar | PS5 - Milestone A | 2026-07-09T12:11:13.000
PL-002640 | PS5-83-OB-0001 |  | B | M | 4.7:As per the packing list 57 units of shroud were scheduled for delivery; only 50 unit were received. | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:28:21.293 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002641 | PS5-83-OB-0001 |  | B | M | 4.8:As per the packing list 414 units of shroud were scheduled for delivery; only 337 unit were received. | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:29:43.673 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002642 | PS5-83-OB-0001 |  | B | M | 4.9:Flashing column (inside the module )PS5-FLS-RF10 is shorter in lenghth and it can not be fix | EPS VENDOR | PS5-83-01 - EITS Building | 2026-07-09T12:35:25.000 | Closed |  |  | 2025-11-27T07:30:54.133 | THANGARATHINAM, ajikumar | PS5 - Milestone A | 2026-07-09T12:35:21.000
PL-002643 | PS5-83-OB-0001 |  | B | M | 4.10: item cut on one side due to deep scratch | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:32:05.380 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002644 | PS5-83-OB-0001 |  | A | E | 4.11:NOT COMPLETE ONE PART IS MISSING | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:33:12.800 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002645 | PS5-83-OB-0001 |  | B | M | 4.12:External holes (for the alignment of bolt ) are missalinged /need to modify the hole, Rust found near the joint between module 2&3 | EPS VENDOR | PS5-83-01 - EITS Building | 2026-07-09T12:36:07.000 | Closed |  |  | 2025-11-27T07:34:35.710 | THANGARATHINAM, ajikumar | PS5 - Milestone A | 2026-07-09T12:36:03.000
PL-002646 | PS5-83-OB-0001 |  | B | M | 4.13:Holes not provided/drilled/tap for installing deck cover plate Between Module 5/6, 6/3, 5/2, 3/2 | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:36:08.033 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002647 | PS5-83-OB-0001 |  | B | M | 4.14:Duct support ,light support,cable tray misplaced/ collapsed from the location | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:37:44.010 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002648 | PS5-83-OB-0001 |  | B | M | 4.15:Flashing column (inside the module 5/6) PS5-FLS-RF10 is shorter in lenghth and it can not be fix. | EPS VENDOR | PS5-83-01 - EITS Building | 2026-07-09T12:36:37.000 | Closed |  |  | 2025-11-27T07:38:48.593 | THANGARATHINAM, ajikumar | PS5 - Milestone A | 2026-07-09T12:36:33.000
PL-002649 | PS5-83-OB-0001 |  | B | M | 4.16:EITS - IT room door not fixed properly and water coming inside during the rain (manufacturing issue) | EITS | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:39:41.313 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002653 | PS5-61-ISO-9005-05-CS01 |  | A | E | PS005-E&I-ALL-PL-1625 - Cable one side termination due to panel not install yet COW - TAG change to be done | EITS | PS5-61-08 - Electrical Control System |  | Completed |  | Refer to Job Card BUILD-COW-0309 | 2025-11-27T11:07:46.000 | Thao-my, Alexandre | PS5 - Milestone C | 2026-08-16T18:23:20.000
PL-002655 | PS5-09-IES-0002 |  | C | E | PS005-HVA-ETC-PL-2254 - No access to operate Emergency stop | EITS | PS5-09-05 - HVAC for EITS Building | 2025-11-27T15:25:23.000 | Closed |  | Punch to be closed as per TQR - SSF1-TQR-000136 which is accepted by CPY, so punch no more applicable | 2025-11-27T11:10:14.000 | Thao-my, Alexandre | PS5 - Milestone A
PL-002656 | PS5-01-LA-0001-CL03 |  | A | I | PS005-E&I-ALL-PL-2589 - Power cable HIPPS Cabinet in General Batch 2 Should be replaced by Fire resistance (Orange cable) | EITS | PS5-0H-01 - HIPPS |  | Originated |  | Refer to Job Card BUILD-COW-0083 | 2025-11-27T11:11:04.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-002662 | PS5-01-UB-6100 |  | C | I | PS005-E&I-ALL-PL-2426 - Special tool to reset Fire suppression solenoid valve to be provided. One by substation | EITS | PS5-01-09 - Inergen for EITS Building | 2025-12-22T09:44:12.000 | Closed |  | Delivery of the tool | 2025-11-27T11:19:00.000 | Thao-my, Alexandre | PS5 - Milestone A
PL-002663 | PS5-61-ISR-0101 |  | B | E | 4:IP washers are damaged | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2025-11-27T12:55:36.213 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-002664 | PS5-61-ISR-0101 |  | B | E | 4.1:Some cable entries are installed without IPwashers | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2025-11-27T12:57:45.720 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-002665 | PS5-61-ISR-0102 |  | A | M | 4:Pressure gauge glass was dislodged, and the gauge found in a bent position | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2025-11-27T13:00:55.240 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-002666 | PS5-61-ISR-0102 |  | C | M | 4.1:Oil barrel leakage (Since bottom side of the barrel was leaking turnedupsidedown) | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2025-11-27T13:02:05.123 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-002667 | PS5-09-PA-84500A |  | C | M | 4:There is no mention of the tag number on the name plate. | EPS VENDOR | PS5-09-03 - HVAC for Generator Building |  | Originated |  |  | 2025-11-27T13:45:07.387 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-002668 | PS5-09-PA-84500B |  | C | M | 4:There is no mention of the tag number on the name plate. | EPS VENDOR | PS5-09-03 - HVAC for Generator Building |  | Originated |  |  | 2025-11-27T13:48:22.603 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-002669 | PS5-09-PA-84500B |  | A | M | 4.1:Rust was found on the coupling / coupling hub during the inspection. | EPS VENDOR | PS5-09-03 - HVAC for Generator Building | 2026-07-09T12:14:04.000 | Closed |  |  | 2025-11-27T13:49:31.867 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-07-09T12:14:00.000
PL-002670 | PS5-60-TR-4300 |  | C | M | 4:As per the packing list, 2 numbers of compressed non-asbestos fibre gaskets; Received 4 numbers were received, resulting in an overage of 2 numbers. | EPS UNATRAC | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  |  | 2025-11-28T10:52:20.203 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-002672 | PS5-01-PA-3100B |  | A | M | Pressure gauges removed from the equipment by CPP preservation/ material team to be reistated after piping installation | CPP AGI | PS5-01-03 - Fire Water Pump B |  | Originated |  | CPP to reistate the pressure gauges | 2025-12-01T06:25:53.000 | kuttan, kuttan | PS5 - Milestone C
PL-002868 | PS5-61-IE-0002 |  | B | E | ECS-iVT - 2024-05-29-007 SFP (100Mb or 1Gb) to provide for Ethernet switches, SW02A/SW02B | EITS | PS5-61-08 - Electrical Control System |  | Originated |  | refer to job card ECS-COW-0001 | 2025-12-12T06:03:42.917 | Thao-my, Alexandre | PS5 - Milestone C
PL-002874 | PS5-25-SDV-0054B |  | B | I | 4:The panel board was found to have fallen from its bolt support during transportation. The bolt locations were cracked and torn due to excessive load. | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-12-12T11:18:11.210 | arun, jabesteen | PS5 - Milestone H
PL-002875 | PS5-25-SDV-0054C |  | B | I | 4:The panel board was found to have fallen from its bolt support during transportation. The bolt locations were cracked and torn due to excessive load. | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-12-12T11:30:41.543 | arun, jabesteen | PS5 - Milestone H
PL-003051 | PS5-61-JY-0001 |  | C | M | PS005-E&I-COW-1004 - Maintenance trolley for BlokSet : oil filling required | EITS | PS5-78-01 - Lifting and handling equipment | 2026-08-08T11:05:33.000 | Closed |  | Refer to Job Card BUILD-COW-0006 | 2026-01-06T05:42:47.707 | Thao-my, Alexandre | PS5 - Milestone E | 2026-08-08T11:05:14.000
PL-003059 | PS5-61-IK-0001 |  | B | E | PS005-E&I-COW-1014 - ATS PLC SOFTWARE (I/O MAPPING) TO BE UPDATED AND TESTED | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0018 | 2026-01-06T05:42:47.707 | Thao-my, Alexandre | PS5 - Milestone A
PL-003063 | PS5-06-IG-0002 |  | C | E | PS005-E&I-COW-1018 - Missing Terminal ID X05 and Terminal numbers 1 to 8 | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-27T05:45:38.000 | Closed |  | Refer to Job Card BUILD-COW-0176 | 2026-01-06T05:42:47.707 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-06T18:20:52.000
PL-003068 | PS5-06-IG-0002 |  | B | E | PS005-E&I-COW-1023 - STS SETTINGS TO BE SET | EITS | PS5-06-01 - AC UPS - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0210 | 2026-01-06T05:42:47.707 | Thao-my, Alexandre | PS5 - Milestone A
PL-003077 | PS5-61-IG-0015 |  | A | E | Vendor TB minimum termination capacity is 25 sqmm. Vendor to provide terminals suitable 16 sqmm and to be installed by Construction CTR. | CPP AGI | PS5-62-10 - CRO Generator Building Normal L&SP DB - PS5-61-IG-0015 |  | Originated |  |  | 2026-01-08T06:52:44.320 | Thao-my, Alexandre | PS5 - Milestone B
PL-003078 | PS5-05-IG-0026 |  | A | E | Vendor TB minimum termination capacity is 25 sqmm. Vendor to provide terminals suitable 6 sqmm and to be installed by Construction CTR. | CPP AGI | PS5-62-07 - CRO Generator Electrical Building Emergency Lighting DB - PS5-05-IG-0026 |  | Originated |  |  | 2026-01-08T06:52:44.320 | Thao-my, Alexandre | PS5 - Milestone B
PL-003254 | PS5-25-PIT-0001 |  | A | I | Range calibration to be done | EACOP | PS5-25-01 - Export Pipeline Pig Receiver |  | Originated |  |  | 2026-01-14T12:40:17.767 | Thao-my, Alexandre | PS5 - Milestone H
PL-003259 | PS5-28-PIT-0041 |  | A | I | Range calibration to be done | EACOP | PS5-28-17 - Reinjection Pump |  | Originated |  |  | 2026-01-14T12:40:17.767 | Thao-my, Alexandre | PS5 - Milestone H
PL-003294 | PS5-03-SFSC-0001 |  | A | I | Cyber-FAT-120 Moxa switch for SIS PS2-03-SW-0001 was tested in Vitrolles, the remaining moxa sw are in Batam or they have been already sent to site. | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to INS-COW-0002 | 2026-01-21T05:09:52.963 | Thao-my, Alexandre | PS5 - Milestone A
PL-003415 | PS5-01-PAL-6101 |  | A | I | PS005-E&I-ALL-PL-2608 - PAL Cable that currently installed Flame Retardant (E253359) shall be replace with Fire Resistan cable IEC60331 (Orange). | EITS | PS5-01-09 - Inergen for EITS Building | 2026-07-24T11:52:02.000 | Closed |  | Refer to Job Card BUILD-COW-0405 | 2026-02-10T05:18:20.410 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-07T08:42:23.000
PL-003416 | PS5-01-PAL-6102 |  | A | I | PS005-E&I-ALL-PL-2608 - PAL Cable that currently installed Flame Retardant (E253359) shall be replace with Fire Resistan cable IEC60331 (Orange). | EITS | PS5-01-09 - Inergen for EITS Building | 2026-07-24T11:52:14.000 | Closed |  | Refer to Job Card BUILD-COW-0405 | 2026-02-10T05:18:20.410 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-07T08:43:12.000
PL-003417 | PS5-01-PAL-6103 |  | A | I | PS005-E&I-ALL-PL-2608 - PAL Cable that currently installed Flame Retardant (E253359) shall be replace with Fire Resistan cable IEC60331 (Orange). | EITS | PS5-01-09 - Inergen for EITS Building | 2026-07-24T11:52:40.000 | Closed |  | Refer to Job Card BUILD-COW-0405 | 2026-02-10T05:18:20.410 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-07T08:44:38.000
PL-003473 | PS5-61-IV-0001A-CH01 |  | A | E | 7: | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Repulling of cable, mantain good bending radius. | 2026-02-12T12:15:25.157 | peela, raja | PS5 - Milestone A
PL-003579 | PS5-60-UR-8100A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHALL BE COMPLETED (DISCIPILINE - PIPING) | CPP AGI | PS5-60-01 - Power Generation Package A | 2026-09-04T12:00:15.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT SHALL BE COMPLETED AFTER HT | 2026-02-13T13:21:05.920 | arun, jabesteen | PS5 - Milestone B | 2026-08-13T08:15:15.000
PL-003580 | PS5-60-UR-8100A |  | B | M | 10.1:FINAL ALIGNMENT SHULD BE DONE | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  | FINAL ALIGNMENT SHULD BE carried out by vendor | 2026-02-13T13:31:26.833 | arun, jabesteen | PS5 - Milestone B
PL-003581 | PS5-60-UR-8100B |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | CPP AGI | PS5-60-04 - Power Generation Package B | 2026-09-04T12:03:49.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED AFTER HT | 2026-02-13T13:46:21.160 | arun, jabesteen | PS5 - Milestone B | 2026-08-13T08:15:33.000
PL-003582 | PS5-60-UR-8100B |  | B | M | 10.1:FINAL ALIGNMENT SHOULD BE DONE | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  | FINAL ALIGNMENT SHOULD BE carried out by vendor | 2026-02-13T13:52:08.660 | arun, jabesteen | PS5 - Milestone B
PL-003583 | PS5-60-UR-8100C |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | CPP AGI | PS5-60-07 - Power Generation Package C | 2026-09-04T12:04:26.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED AFTER HT | 2026-02-13T13:55:54.823 | arun, jabesteen | PS5 - Milestone D | 2026-08-13T08:15:53.000
PL-003584 | PS5-60-UR-8100C |  | B | M | 10.1:FINAL ALIGNMENT SHULD BE DONE | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | FINAL ALIGNMENT SHULD BE carried out by vendor | 2026-02-13T13:58:06.040 | arun, jabesteen | PS5 - Milestone D
PL-003585 | PS5-60-UR-8100D |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | CPP AGI | PS5-60-10 - Power Generation Package D | 2026-09-05T05:59:59.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED AFTER HT | 2026-02-13T14:05:42.683 | arun, jabesteen | PS5 - Milestone D | 2026-08-13T08:16:23.000
PL-003586 | PS5-60-UR-8100D |  | B | M | 10.1:FINAL ALIGNMENT SHULD BE DONE | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  | FINAL ALIGNMENT SHULD BE carried out by vendor | 2026-02-13T14:08:00.040 | arun, jabesteen | PS5 - Milestone D
PL-003587 | PS5-60-UR-8100E |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | CPP AGI | PS5-60-13 - Power Generation Package E | 2026-09-05T05:59:26.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED AFTER HT | 2026-02-13T14:13:02.357 | arun, jabesteen | PS5 - Milestone D | 2026-08-13T08:16:43.000
PL-003588 | PS5-60-UR-8100E |  | B | M | 10.1:FINAL ALIGNMENT SHULD BE DONE | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | FINAL ALIGNMENT SHULD BE carried out by vendor | 2026-02-13T14:15:01.700 | arun, jabesteen | PS5 - Milestone D
PL-003589 | PS5-60-UR-8100F |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | CPP AGI | PS5-60-16 - Power Generation Package F | 2026-09-05T06:00:31.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED AFTER HT | 2026-02-13T14:19:06.617 | arun, jabesteen | PS5 - Milestone D | 2026-08-13T08:17:03.000
PL-003590 | PS5-60-UR-8100F |  | B | M | 10.1:FINAL ALIGNMENT SHOULD BE DONE | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  | FINAL ALIGNMENT SHOULD BE carried out by vendor | 2026-02-13T14:20:49.163 | arun, jabesteen | PS5 - Milestone D
PL-003591 | PS5-60-UR-8100G |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | CPP AGI | PS5-60-19 - Power Generation Package G | 2026-09-05T06:00:55.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED AFTER HT | 2026-02-13T14:23:25.577 | arun, jabesteen | PS5 - Milestone E | 2026-08-13T08:17:23.000
PL-003592 | PS5-60-UR-8100G |  | B | M | 10.1:FINAL ALIGNMENT SHOULD BE DONE | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  | FINAL ALIGNMENT SHOULD BE carried out by vendor | 2026-02-13T14:24:31.330 | arun, jabesteen | PS5 - Milestone E
PL-003593 | PS5-83-OB-0001_Installation |  | A | M | Structural bolts shall be properly secured & tightened all over the EITS Building area | CPP AGI | PS5-83-01 - EITS Building | 2026-02-24T14:00:42.000 | Closed |  | Structural bolts shall be properly secured & tightened all over the EITS Building area | 2026-02-14T06:59:23.000 | arun, jabesteen | PS5 - Milestone A | 2026-02-24T14:00:32.000
PL-003594 | PS5-83-OB-0001_Installation |  | B | B | Proper Leveling, compaction, gravel fill required for the whole EITS building area. | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | Proper Leveling, compaction, gravel fill required for the whole EITS building area. | 2026-02-14T07:10:07.000 | arun, jabesteen | PS5 - Milestone A
PL-003595 | PS5-83-OB-0001_Installation |  | A | M | Grating Clips shall be properly fastened and tightened | CPP AGI | PS5-83-01 - EITS Building | 2026-02-24T14:01:03.000 | Closed |  | Grating Clips shall be properly fastened and tightened | 2026-02-14T07:15:33.000 | arun, jabesteen | PS5 - Milestone A | 2026-02-24T14:00:59.000
PL-003596 | PS5-83-OB-0001_Installation |  | B | M | External covers outside the EITS building found gaps, screw damages & holes mismatch. | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | External covers outside the EITS building found gaps, screw damages & holes mismatch should be rectified | 2026-02-14T07:19:22.000 | arun, jabesteen | PS5 - Milestone A
PL-003597 | PS5-83-OB-0001_Installation |  | B | B | Proper finishing required for the EITS building foundations. | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | Proper finishing required for the EITS building foundations. | 2026-02-14T07:23:29.000 | arun, jabesteen | PS5 - Milestone A
PL-003600 | PS5-83-OB-0001_Installation |  | B | E | Sprinkler to be installed after GALT. | EITS | PS5-83-01 - EITS Building |  | Originated |  | Sprinkler to be installed after GALT. | 2026-02-14T07:34:31.000 | arun, jabesteen | PS5 - Milestone A
PL-003601 | PS5-09-ACU-0007_OUTDOOR_INSTALLATION |  | A | M | Anchor bolts need to be tightened for HVAC ACU units. | CPP AGI | PS5-09-05 - HVAC for EITS Building |  | Originated |  | Anchor bolts need to be tightened for HVAC ACU units. | 2026-02-14T07:38:50.000 | arun, jabesteen | PS5 - Milestone A
PL-003602 | PS5-83-OB-0001_Installation |  | B | M | Handrail Splice needs to be Welded and Painted at East side area | CPP AGI | PS5-83-01 - EITS Building | 2026-02-24T14:01:21.000 | Closed |  | Handrail Splice needs to be Welded and Painted at East side area | 2026-02-14T07:42:24.000 | arun, jabesteen | PS5 - Milestone A | 2026-02-24T14:01:18.000
PL-003605 | PS5-83-OB-0001_Installation |  | A | H | All HVAC ducts were misaligned with the ACU units. | EITS | PS5-83-01 - EITS Building |  | Originated |  | All HVAC ducts were misaligned with the ACU units. | 2026-02-14T07:46:41.000 | arun, jabesteen | PS5 - Milestone A
PL-003606 | PS5-83-OB-0001_Installation |  | A | E | Earthing bonders need to be installed all over structural connection. | EITS | PS5-83-01 - EITS Building |  | Originated |  | Earthing bonders need to be installed all over structural connection | 2026-02-14T07:52:09.000 | arun, jabesteen | PS5 - Milestone A
PL-003608 | PS5-83-OB-0001_Installation |  | A | E | For all Inergen lines U-bolts tightening & Torquing shall be done before GALT | EITS | PS5-83-01 - EITS Building |  | Originated |  | For all Inergen lines U-bolts tightening & Torquing shall be done before GALT | 2026-02-14T07:57:00.000 | arun, jabesteen | PS5 - Milestone A
PL-003609 | PS5-83-OB-0001_Installation |  | A | M | Shutoff Dampers were not installed above the HVAC ACU units (4 Dampers) | CPP AGI | PS5-83-01 - EITS Building | 2026-02-24T14:01:39.000 | Closed |  | Shutoff Dampers were above the HVAC ACU units (4 Dampers)-should be installed | 2026-02-14T08:02:05.000 | arun, jabesteen | PS5 - Milestone A | 2026-02-24T14:01:35.000
PL-003610 | PS5-83-OB-0001_Installation |  | A | H | HVAC Ducts leak test shall be performed after finishing the whole installations | EITS | PS5-83-01 - EITS Building |  | Originated |  | HVAC Ducts leak test shall be performed after finishing the whole installations | 2026-02-14T08:05:57.000 | arun, jabesteen | PS5 - Milestone A
PL-003611 | PS5-83-OB-0001_Installation |  | A | B | Missing two elbows (3019F and 3019G) | EITS | PS5-83-01 - EITS Building |  | Originated |  | Missing two elbows (3019F and 3019G) should be installed | 2026-02-14T08:09:26.000 | arun, jabesteen | PS5 - Milestone A
PL-003612 | PS5-83-OB-0001_Installation |  | A | P | MCT not provided for the Inergen pipes which are entering into the Inergen Package | EITS | PS5-83-01 - EITS Building | 2026-05-12T11:53:39.000 | Closed |  | MCT not provided for the Inergen pipes which are entering into the Inergen Package | 2026-02-14T08:15:00.000 | arun, jabesteen | PS5 - Milestone A | 2026-05-12T11:48:31.000
PL-003615 | PS5-83-OB-0001_Installation |  | B | E | All EIT cable tray, Ladder, tray supports shall be installed | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | All EIT cable tray, Ladder, tray supports shall be installed. | 2026-02-14T08:18:38.000 | arun, jabesteen | PS5 - Milestone A
PL-003616 | PS5-83-OB-0001_Installation |  | A | E | Electrical earthing around the building shall be completed. | CPP AGI | PS5-83-01 - EITS Building | 2026-02-24T14:03:19.000 | Closed |  | Electrical earthing around the building shall be completed. | 2026-02-14T08:21:38.000 | arun, jabesteen | PS5 - Milestone A | 2026-02-24T14:03:15.000
PL-003617 | PS5-61-IU-0011 |  | A | E | 4:During inspection, the junction box fell down due to improper fixing. The item was dispatched without being securely installed. | EPS VENDOR | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  |  | 2026-02-14T11:31:27.620 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-003618 | PS5-61-IU-0011 |  | B | E | 4.1:No cable glands are installed in the DECT MDU PANEL | EPS VENDOR | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  |  | 2026-02-14T11:33:24.200 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-003619 | PS5-61-IU-0011 |  | B | E | 4.2:All installed cables are directly fixed to the transformer without cable trays and/or rigid conduit pipes. | EPS VENDOR | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  |  | 2026-02-14T11:34:50.800 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-003620 | PS5-61-IU-0011 |  | B | E | 4.3:"At the commissioning stage, it is necessary to verify the functionality of the equipment and confirm the absence of any hidden defects. Because panel was unfixed." | EPS VENDOR | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  |  | 2026-02-14T11:36:23.003 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-003621 | BF_PS5-61-IU-0010 |  | B | E | 4:No cable glands are installed in the DECT MDU PANEL | EPS VENDOR | PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010) |  | Originated |  |  | 2026-02-14T11:41:59.533 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-003622 | PS5-61-IU-0010 |  | B | E | 4.1:All installed cables are directly fixed to the transformer without cable trays and/or rigid conduit pipes. | EPS VENDOR | PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010) |  | Originated |  |  | 2026-02-14T11:43:37.660 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-003623 | PS5-01-PA-3100A |  | B | M | 4:All the jack bolts are missing on the base frame of the pump | EPS VENDOR | PS5-01-02 - Fire Water Pump A |  | Originated |  |  | 2026-02-14T11:49:01.793 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-003624 | PS5-01-PA-3100A |  | A | M | 4.1:22 batteries had a voltage below 1V, 6 batteries had a voltage below 1.2V | EPS VENDOR | PS5-01-02 - Fire Water Pump A |  | Originated |  |  | 2026-02-14T11:51:08.820 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-003625 | PS5-01-PA-3100A |  | A | M | 4.2:Silencer not received along with the pump | EPS VENDOR | PS5-01-02 - Fire Water Pump A |  | Completed |  |  | 2026-02-14T11:52:42.530 | THANGARATHINAM, ajikumar | PS5 - Milestone C | 2026-04-27T14:23:24.000
PL-003648 | PS5-01-UZ-610 |  | A | M | 4:As per the packing list, a 0.18-liter Nitrogen (N₂) cylinder is specified with a filling pressure of 200 bar. However, upon receipt at PS5-01-UZ-610, two cylinders were found with pressures of 1300 psi (89.6 Bar), which are below the specified 200 bar requirement. | EPS VENDOR | PS5-01-11 - Inergen for Power Gen Building |  | Originated |  |  | 2026-02-19T11:49:56.420 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-003649 | PS5-71-UN-7200 |  | B | M | 4:"Spare parts have arrived; but no details are mentioned in the packing list. ( gaskets-2 pcs 3/4"" 150# 4 pcs 1"" 150# 4 pcs 1 1/2"" 150# 5 pcs 2"" 150"" 3 pcs 4"" 150# 2 set lamps fuses and connectors (SIBA FUSE 5X20 T 125MA DS10) 1 PCS DIGITAL BARRIER dek-oe-24dc/100k. 1 pcs repeater power supply (Analog barrier) MACX MCR-SL-RPSSI-2I. )" | EPS VENDOR | PS5-71-02 - CFO Allocation Metering Package |  | Originated |  |  | 2026-02-19T13:30:18.920 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003654 | PS5-28-PA-3700A |  | B | M | Coupling hub inside dia is not matching with the shaft dia of pump and motor | EPS VENDOR | PS5-28-04 - Closed Drain Drum and Pump 02 | 2026-07-09T12:37:57.000 | Closed |  | vendor to rectify | 2026-02-20T07:17:37.000 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-07-09T12:37:52.000
PL-003655 | PS5-28-PA-3700B |  | A | M | Coupling hub inside dia is not matching with the shaft dia of pump and motor | EPS VENDOR | PS5-28-04 - Closed Drain Drum and Pump 02 | 2026-07-04T11:52:39.000 | Closed |  | vendor to rectify | 2026-02-20T07:21:04.000 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-07-04T11:52:36.000
PL-003692 | PS5-75-UI-6100 |  | B | I | Level Gauge FAT not conducted as the Specific gravity of the water does not allow the instrument float to float. | EACOP | PS5-75-02 - Biocide Injection Package |  | Originated |  | To be verified along with commissioning test | 2026-02-23T12:49:22.000 | Thao-my, Alexandre | PS5 - Milestone G
PL-003701 | PS5-61-IE-0001 |  | B | E | ECS-iFAT-2024-07-02-011 Keyboard and mouse lose connection after power recycle from MCB on ECS Server A & B | EITS | PS5-61-08 - Electrical Control System |  | Originated |  | refer to job card ECS-COW-007 | 2026-02-24T05:20:03.557 | Thao-my, Alexandre | PS5 - Milestone C
PL-003706 | PS5-61-IE-0001 |  | B | E | ECS-ECS - 20255-08-12-003 Configure the static route for ALL ECS/PCS connection | EITS | PS5-61-08 - Electrical Control System |  | Originated |  | refer to job card ECS-COW-0006 | 2026-02-24T05:20:03.557 | Thao-my, Alexandre | PS5 - Milestone C
PL-003714 | PS5-71-TR-4100 |  | A | M | 4:As per the drawing, the deluge piping should be galvanized Carbon steel, but it was received without a galvanized coating. | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-07-04T11:53:23.000 | Closed |  |  | 2026-02-24T13:10:06.950 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-07-04T11:53:19.000
PL-003715 | PS5-71-TR-4100 |  | A | M | 4.1:SL NO-11, M10 'U' BOLT - 2" PIPE + 4NUTS (STD) NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:26:42.000 | Closed |  | SL NO-11, M10 'U' BOLT - 2" PIPE + 4NUTS (STD) RECEIVED IN THE NEXT PACKAGE | 2026-02-24T13:12:04.870 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:18:15.000
PL-003716 | PS5-71-TR-4100 |  | A | M | 4.2:SL NO - 14 , GASKET 3MM NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:26:08.000 | Closed |  | SL NO - 14 , GASKET 3MM NOT RECEIVED | 2026-02-24T13:13:05.400 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:20:17.000
PL-003717 | PS5-71-TR-4100 |  | A | M | 4.3: SL NO - 17, WASHER NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:27:02.000 | Closed |  | SL NO - 17, WASHER NOT RECEIVED | 2026-02-24T13:14:15.343 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:21:13.000
PL-003718 | PS5-71-TR-4100 |  | A | M | 4.4:SL NO - 20 , GASKET 762O.D.x600I.D.x1.5THK NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:28:18.000 | Closed |  | SL NO - 20 , GASKET 762O.D.x600I.D.x1.5THK NOT RECEIVED | 2026-02-24T13:15:26.817 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:22:19.000
PL-003719 | PS5-71-TR-4100 |  | A | M | 4.5:SL NO - 24 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:28:34.000 | Closed |  | SL NO - 24 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | 2026-02-24T13:16:38.200 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:26:46.000
PL-003720 | PS5-71-TR-4100 |  | A | M | 4.6:SL NO - 26 , GASKET 1.5 THK., 6"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:28:53.000 | Closed |  | SL NO - 26 , GASKET 1.5 THK., 6"-150# RF NOT RECEIVED | 2026-02-24T13:18:02.313 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:27:44.000
PL-003721 | PS5-71-TR-4100 |  | A | M | 4.7:SL NO - 29 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:29:09.000 | Closed |  | 4.7:SL NO - 29 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | 2026-02-24T13:18:57.017 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:32:50.000
PL-003722 | PS5-71-TR-4100 |  | A | M | 4.8:SL NO - 32 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:29:28.000 | Closed |  | SL NO - 32 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | 2026-02-24T13:20:06.950 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:35:36.000
PL-003723 | PS5-71-TR-4100 |  | A | M | 4.9:SL NO - 37 , GASKET 4.5 THK., 3"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:29:46.000 | Closed |  | SL NO - 37 , GASKET 4.5 THK., 3"-150# RF NOT RECEIVED | 2026-02-24T13:21:08.703 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:37:29.000
PL-003724 | PS5-71-TR-4100 |  | A | M | 4.10:SL NO - 38 , STUD+2NUTS-5/8" UNC NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:30:03.000 | Closed |  | SL NO - 38 , STUD+2NUTS-5/8" UNC NOT RECEIVED | 2026-02-24T13:22:18.360 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:39:00.000
PL-003725 | PS5-71-TR-4100 |  | A | M | 4.11:SL NO - 54 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:30:21.000 | Closed |  | SL NO - 54 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | 2026-02-24T13:23:25.320 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:40:05.000
PL-003726 | PS5-71-TR-4100 |  | A | M | 4.12:SL NO - 58 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:30:44.000 | Closed |  | L NO - 58 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | 2026-02-24T13:24:34.683 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:41:27.000
PL-003727 | PS5-71-TR-4200 |  | A | M | 4:As per the drawing, the deluge piping should be galvanized carbon steel, but it was received without a galvanized coating. | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-07-04T11:53:56.000 | Closed |  |  | 2026-02-24T13:29:28.133 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-07-04T11:53:52.000
PL-003728 | PS5-71-TR-4200 |  | A | M | 4.1:SL NO - 61 , GASKET 762 ,O.D.x600,I.D.x1.5THK NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:32:11.000 | Closed |  | SL NO - 61 , GASKET 762 ,O.D.x600,I.D.x1.5THK NOT RECEIVED | 2026-02-24T13:31:02.293 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-02T13:17:36.000
PL-003729 | PS5-71-TR-4200 |  | A | M | 4.2:SL NO - 67 , GASKET 3MM NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:33:01.000 | Closed |  | SL NO - 67 , GASKET 3MM NOT RECEIVED | 2026-02-24T13:32:15.527 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-02T13:23:10.000
PL-003731 | PS5-71-TR-4200 |  | A | M | 4.4:SL NO - 70 , WASHER NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:33:15.000 | Closed |  | SL NO - 70 , WASHER NOT RECEIVED | 2026-02-24T13:33:24.057 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-02T13:25:03.000
PL-003732 | PS5-71-TR-4200 |  | A | M | 4.5:SL SL NO - 71 , HEX. NUTS M20 NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:33:33.000 | Closed |  | SL NO - 71 , HEX. NUTS M20 NOT RECEIVED | 2026-02-24T13:34:18.187 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-02T13:26:22.000
PL-003733 | PS5-71-TR-4200 |  | A | M | 4.6:SL NO - 75 , WASHER O.D. 40 x I.D. 18 NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:34:54.000 | Closed |  | SL NO - 75 , WASHER O.D. 40 x I.D. 18 NOT RECEIVED | 2026-02-24T13:36:16.690 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-02T13:30:14.000
PL-003734 | PS5-71-TR-4200 |  | A | M | 4.7:SL NO - 76 , SPLIT PIN-5Ø NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:35:15.000 | Closed |  | SL NO - 76 , SPLIT PIN-5Ø NOT RECEIVED | 2026-02-24T13:37:18.260 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-02T13:34:23.000
PL-003735 | PS5-71-TR-4200 |  | A | M | 4.8:SL NO -77 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:35:41.000 | Closed |  | SL NO -77 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | 2026-02-24T13:39:10.940 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-02T13:41:19.000
PL-003736 | PS5-71-TR-4200 |  | A | M | 4.9:SL NO - 79 , GASKET 1.5 THK., 3"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:36:16.000 | Closed |  | SL NO - 79 , GASKET 1.5 THK., 3"-150# RF NOT RECEIVED | 2026-02-24T13:40:12.990 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-02T14:19:30.000
PL-003737 | PS5-71-TR-4200 |  | A | M | 4.10:SL NO - 82 , GASKET 4.5 THK., 10"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:36:33.000 | Closed |  | SL NO - 82 , GASKET 4.5 THK., 10"-150# RF NOT RECEIVED | 2026-02-24T13:41:16.850 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:08:08.000
PL-003738 | PS5-71-TR-4200 |  | A | M | 4.11:SL NO - 85 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:36:47.000 | Closed |  | SL NO - 85 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | 2026-02-24T13:42:52.970 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:09:34.000
PL-003739 | PS5-71-TR-4200 |  | A | M | 4.12:SL NO - 90 , GASKET 4.5 THK., 3"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:37:03.000 | Closed |  | SL NO - 90 , GASKET 4.5 THK., 3"-150# RF NOT RECEIVED | 2026-02-24T13:44:19.240 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:10:33.000
PL-003740 | PS5-71-TR-4200 |  | A | M | 4.13:SL NO - 90 , GASKET 4.5 THK., 3"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:37:16.000 | Closed |  | SL NO - 90 , GASKET 4.5 THK., 3"-150# RF NOT RECEIVED | 2026-02-24T13:45:09.410 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:11:55.000
PL-003741 | PS5-71-TR-4200 |  | A | M | 4.14:SL NO - 106 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:37:29.000 | Closed |  | SL NO - 106 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | 2026-02-24T13:46:46.080 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:13:25.000
PL-003742 | PS5-71-TR-4200 |  | A | M | 4.15:SL NO - 111 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:37:47.000 | Closed |  | SL NO - 111 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | 2026-02-24T13:48:00.817 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-05-07T13:14:30.000
PL-003743 | PS5-71-TR-4400 |  | B | M | As per the packing list, 3 Nos. of 1/4" nipple are mentioned, but they have not been received. | EPS VENDOR | PS5-71-15 - Diesel Fuel Storage Tank |  | Originated |  | Vendor to rectify | 2026-02-24T14:06:04.000 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-003744 | PS5-53-TR-4100 |  | B | M | As per the packing list, 3 Nos. of vortex breakers are mentioned, but they have not been received. | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank |  | Completed |  | Vendor to rectify | 2026-02-24T14:09:14.000 | THANGARATHINAM, ajikumar | PS5 - Milestone C | 2026-08-11T12:34:50.000
PL-004311 | PS5-60-VS-9100A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A | 2026-09-05T06:01:15.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-02T10:42:45.157 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T08:17:45.000
PL-004312 | PS5-60-VS-9100B |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B | 2026-09-05T06:01:36.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-02T10:54:14.483 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T08:18:29.000
PL-004313 | PS5-60-VS-9100C |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C | 2026-09-05T06:01:57.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-02T11:00:09.387 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T08:18:49.000
PL-004314 | PS5-60-VS-9100D |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D | 2026-09-05T06:02:28.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-02T11:04:21.727 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T08:19:15.000
PL-004315 | PS5-60-VS-9100F |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping | CPP AGI | PS5-60-47 - Oil Mist Separator Skid PS5-60-VS-9100F | 2026-09-05T06:02:46.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping | 2026-03-02T11:09:05.243 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T08:19:36.000
PL-004316 | PS5-60-VA-5100C |  | A | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-30 - Air Receiver C & Air Regulator C | 2026-09-04T06:10:35.000 | Closed | - The Reinstatement Closed based on Task ID - T-00216-0270 |  | 2026-03-02T12:45:37.510 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T08:19:57.000
PL-004333 | PS5-60-YF-1700A |  | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A | 2026-09-05T06:03:37.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-03T06:31:39.983 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T08:20:19.000
PL-004334 | PS5-60-YF-1700A |  | C | E | 16.1:EARTHING TO BE DONE | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | ARTHING TO BE DONE | 2026-03-03T06:32:22.740 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004335 | PS5-60-YF-1700B |  | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-03T06:38:00.760 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004336 | PS5-60-YF-1700B |  | C | E | 16.1:EARTHING TO BE DONE | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | EARTHING TO BE DONE | 2026-03-03T06:38:35.387 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004340 | PS5-78-JC-9100A |  | C | M | 25:ouch up paint will be carried out | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2026-03-04T04:38:53.837 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004341 | PS5-78-JC-9100B |  | C | M | 25:Touch-up painting will be carried out | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2026-03-04T04:43:17.320 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004342 | PS5-78-JC-9100C |  | C | M | 25:Touch-up painting will be carried out | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2026-03-04T04:44:53.743 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004343 | PS5-78-JC-9100D |  | C | M | 25:Touch-up painting will be carried out | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2026-03-04T04:46:36.597 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004344 | PS5-05-UR-8100 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-09-05T06:04:29.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-04T10:06:16.263 | THANGARATHINAM, ajikumar | PS5 - Milestone C | 2026-08-13T08:20:56.000
PL-004345 | PS5-05-UR-8100 |  | A | M | 10.1: Flame arrester to be installed | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-07-04T11:55:50.000 | Closed |  |  | 2026-03-04T10:35:48.293 | THANGARATHINAM, ajikumar | PS5 - Milestone C | 2026-07-04T11:55:47.000
PL-004346 | PS5-05-UR-8100 |  | B | M | 10.2:Final alignment to be verified | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  | To be verified by vendor | 2026-03-04T10:36:23.793 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-004347 | PS5-60-VA-5100A |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-28 - Air Receiver A & Air Regulator A | 2026-09-05T07:22:37.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(discipline-piping) | 2026-03-04T12:33:23.000 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T08:21:20.000
PL-004348 | PS5-60-VA-5100A |  | B | E | 23.1:EARTHING TO BE DONE | CPP AGI | PS5-60-28 - Air Receiver A & Air Regulator A |  | Originated |  |  | 2026-03-04T12:34:01.427 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004349 | PS5-60-VA-5100B |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(discipline-piping) | CPP AGI | PS5-60-29 - Air Receiver B & Air Regulator B | 2026-09-05T07:23:13.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(discipline-piping) | 2026-03-04T12:46:11.933 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T08:21:45.000
PL-004350 | PS5-60-VA-5100B |  | B | E | 23.1:EARTHING TO BE DONE | CPP AGI | PS5-60-29 - Air Receiver B & Air Regulator B |  | Originated |  |  | 2026-03-04T12:46:56.717 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004351 | PS5-60-VS-9100E |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(discipline-piping) | CPP AGI | PS5-60-46 - Oil Mist Separator Skid PS5-60-VS-9100E | 2026-09-05T07:25:30.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(discipline-piping) | 2026-03-04T12:59:34.597 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T08:22:18.000
PL-004352 | PS5-60-VS-9100G |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-48 - Oil Mist Separator Skid PS5-60-VS-9100G | 2026-09-05T07:27:18.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(discipline-piping) | 2026-03-04T13:09:59.443 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-08-13T08:22:40.000
PL-004353 | PS5-60-UZ-8900A |  | A | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A | 2026-09-05T07:27:42.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(discipline-piping) | 2026-03-04T13:17:49.207 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T08:23:05.000
PL-004354 | PS5-60-VA-5100D |  | A | E | 23:EARTHING TO BE DONE | CPP AGI | PS5-60-31 - Air Receiver D & Air Regulator D |  | Completed |  |  | 2026-03-04T14:05:39.233 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T08:13:06.000
PL-004355 | PS5-60-VA-5100D |  | B | P | 23.1:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-31 - Air Receiver D & Air Regulator D | 2026-09-05T07:28:31.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-04T14:06:54.250 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T06:42:25.000
PL-004356 | PS5-60-VA-5100E |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-32 - Air Receiver E & Air Regulator E | 2026-09-05T07:28:47.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-04T14:11:23.857 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T06:46:50.000
PL-004357 | PS5-60-VA-5100E |  | B | E | 23.1:EARTHING TO BE DONE | CPP AGI | PS5-60-32 - Air Receiver E & Air Regulator E |  | Originated |  |  | 2026-03-04T14:11:44.880 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004358 | PS5-60-VA-5100F |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-33 - Air Receiver F & Air Regulator F | 2026-09-05T07:29:01.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-04T14:18:39.830 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T06:48:27.000
PL-004359 | PS5-60-VA-5100F |  | B | E | 23.1: EARTHING TO BE DONE | CPP AGI | PS5-60-33 - Air Receiver F & Air Regulator F |  | Originated |  |  | 2026-03-04T14:18:59.577 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004360 | PS5-60-VA-5100G |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-34 - Air Receiver G & Air Regulator G | 2026-09-05T07:29:12.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-04T14:25:37.763 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-08-13T06:49:09.000
PL-004361 | PS5-60-VA-5100G |  | B | E | 23.1: EARTHING TO BE DONE | CPP AGI | PS5-60-34 - Air Receiver G & Air Regulator G |  | Originated |  |  | 2026-03-04T14:26:00.973 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004362 | PS5-60-YF-1700G |  | B | M | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-04T14:39:49.190 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-08-13T06:50:05.000
PL-004363 | PS5-60-YF-1700G |  | B | E | 16.1: EARTHING TO BE DONE | CPP AGI | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G |  | Originated |  |  | 2026-03-04T14:40:26.563 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004364 | PS5-60-YF-1700F |  | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F | 2026-09-05T07:29:26.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T12:51:07.483 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T06:52:27.000
PL-004365 | PS5-60-YF-1700F |  | B | E | 16.1:EARTHING TO BE DONE | CPP AGI | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Originated |  |  | 2026-03-05T12:51:34.050 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004366 | PS5-60-YF-1700E |  | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E | 2026-09-05T07:30:15.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T12:55:48.527 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T06:53:53.000
PL-004367 | PS5-60-YF-1700E |  | B | E | 16.1:EARTHING TO BE DONE | CPP AGI | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E |  | Originated |  |  | 2026-03-05T12:56:15.463 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004368 | PS5-60-YF-1700D |  | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D | 2026-09-05T08:19:09.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T12:59:29.633 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T06:57:20.000
PL-004369 | PS5-60-YF-1700D |  | B | E | 16.1:EATRHING TO BE DONE | CPP AGI | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D |  | Originated |  |  | 2026-03-05T12:59:50.947 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004370 | PS5-60-YF-1700C |  | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C | 2026-09-05T11:42:25.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T13:06:48.617 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T06:58:07.000
PL-004371 | PS5-60-YF-1700C |  | B | E | 16.1:EARTHING TO BE DONE | CPP AGI | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C |  | Originated |  |  | 2026-03-05T13:07:26.887 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004372 | PS5-60-UR-8200A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-01 - Power Generation Package A | 2026-09-05T11:42:55.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T13:23:10.510 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T06:58:40.000
PL-004373 | PS5-60-UR-8200B |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-04 - Power Generation Package B | 2026-09-05T11:44:29.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T13:26:04.377 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T06:59:04.000
PL-004374 | PS5-60-UR-8200C |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-07 - Power Generation Package C | 2026-09-05T11:44:43.000 | Closed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T13:28:26.753 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T06:59:42.000
PL-004375 | PS5-60-UR-8200D |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-10 - Power Generation Package D |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T13:32:38.910 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T07:00:05.000
PL-004376 | PS5-60-UR-8200E |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-13 - Power Generation Package E |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T13:42:43.950 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T07:00:25.000
PL-004377 | PS5-60-UR-8200F |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-16 - Power Generation Package F |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T13:54:33.130 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T07:00:49.000
PL-004378 | PS5-60-UR-8200G |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-19 - Power Generation Package G |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T13:58:04.690 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-08-13T07:01:11.000
PL-004379 | PS5-78-JC-9100A |  | B | B | ROOF-final installation need to be done In PG area | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | ROOF-final installation need to be done In PG area | 2026-03-06T05:27:24.000 | arun, jabesteen | PS5 - Milestone E
PL-004380 | PS5-78-JC-9100B |  | B | B | ROOF-final installation need to be done In PG area | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | ROOF-final installation need to be done In PG area | 2026-03-06T07:01:12.000 | arun, jabesteen | PS5 - Milestone E
PL-004381 | PS5-78-JC-9100C |  | B | B | ROOF-final installation need to be done In PG area-9100 C | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | ROOF-final installation need to be done In PG area | 2026-03-06T07:05:29.000 | arun, jabesteen | PS5 - Milestone E
PL-004382 | PS5-78-JC-9100D |  | B | B | ROOF-final installation need to be done In PG area | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | ROOF-final installation need to be done In PG area-9100 D | 2026-03-06T07:08:26.000 | arun, jabesteen | PS5 - Milestone E
PL-004384 | PS5-60-IJ-0001A-CH04 |  | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | 2026-03-07T11:12:27.703 | arun, jabesteen | PS5 - Milestone B
PL-004385 | PS5-60-IJ-0001B-CH04 |  | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | 2026-03-07T11:34:01.367 | arun, jabesteen | PS5 - Milestone B
PL-004386 | PS5-60-IJ-0001C-CH04 |  | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | 2026-03-07T11:37:51.250 | arun, jabesteen | PS5 - Milestone D
PL-004387 | PS5-60-IJ-0001D-CH04 |  | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | 2026-03-07T11:40:47.027 | arun, jabesteen | PS5 - Milestone D
PL-004388 | PS5-60-IJ-0001E-CH04 |  | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | CPP AGI | PS5-60-13 - Power Generation Package E |  | Originated |  | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | 2026-03-07T11:44:20.037 | arun, jabesteen | PS5 - Milestone D
PL-004389 | PS5-60-IJ-0001F-CH04 |  | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | CPP AGI | PS5-60-16 - Power Generation Package F |  | Originated |  | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | 2026-03-07T11:47:40.440 | arun, jabesteen | PS5 - Milestone D
PL-004390 | PS5-60-IJ-0001G-CH04 |  | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | 2026-03-07T11:50:00.550 | arun, jabesteen | PS5 - Milestone E
PL-004411 | PS5-78-JC-9100A |  | B | M | Chain to be correctly installed (still hooked on the rail). | CPP AGI | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:45:33.000 | Closed |  | Chain to be correctly installed (still hooked on the rail). | 2026-03-10T07:32:16.000 | arun, jabesteen | PS5 - Milestone E | 2026-05-02T05:45:20.000
PL-004412 | PS5-78-JC-9100B |  | B | M | Chain to be installed | CPP AGI | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:46:31.000 | Closed |  | Chain to be installed | 2026-03-10T07:41:42.000 | arun, jabesteen | PS5 - Milestone E | 2026-05-02T05:46:27.000
PL-004413 | PS5-78-JC-9100B |  | B | M | Guide rail anti-derailment to be installed | CPP AGI | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:46:51.000 | Closed |  | Guide rail anti-derailment to be installed | 2026-03-10T07:47:12.000 | arun, jabesteen | PS5 - Milestone E | 2026-05-02T05:46:48.000
PL-004414 | PS5-78-JC-9100B |  | B | E | 3 pin connectors damaged for motor fan and need to be replaced --> Damage during installation | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | 3 pin connectors damaged for motor fan and need to be replaced --> Damage during installation | 2026-03-10T07:54:11.000 | arun, jabesteen | PS5 - Milestone E
PL-004415 | PS5-78-JC-9100B |  | B | M | Control pendant height to be properly secured within the crane | CPP AGI | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:47:26.000 | Closed |  | Control pendant height to be properly secured within the crane | 2026-03-10T07:56:36.000 | arun, jabesteen | PS5 - Milestone E | 2026-05-02T05:47:23.000
PL-004416 | PS5-78-JC-9100B |  | B | E | Rectify the GAP between the C/T power supply and the pendant power supply to avoid any blockage | CPP AGI | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:49:32.000 | Closed |  | Rectify the GAP between the C/T power supply and the pendant power supply to avoid any blockage | 2026-03-10T07:58:23.000 | arun, jabesteen | PS5 - Milestone E | 2026-05-02T05:49:27.000
PL-004417 | PS5-78-JC-9100C |  | B | M | Guide rail anti-derailment to be installed | CPP AGI | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:49:50.000 | Closed |  | Guide rail anti-derailment to be installed | 2026-03-10T08:00:43.000 | arun, jabesteen | PS5 - Milestone E | 2026-05-02T05:49:47.000
PL-004418 | PS5-78-JC-9100C |  | B | M | Control pendant height to be properly secured within the crane | CPP AGI | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:50:23.000 | Closed |  | Control pendant height to be properly secured within the crane | 2026-03-10T08:02:37.000 | arun, jabesteen | PS5 - Milestone E | 2026-05-02T05:50:19.000
PL-004419 | PS5-78-JC-9100D |  | B | E | VSD failure during testing and need to be changed by vendor (Equipment failure) | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  | VSD failure during testing and need to be changed by vendor (Equipment failure) | 2026-03-10T08:09:08.000 | arun, jabesteen | PS5 - Milestone E
PL-004420 | PS5-78-JC-9100D |  | B | M | Damaged current collector (swapped to Crane C) to be changed | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | Damaged current collector (swapped to Crane C) to be changed | 2026-03-10T08:12:57.000 | arun, jabesteen | PS5 - Milestone E
PL-004423 | PS5-78-JC-9100A |  | C | E | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | 2026-03-10T08:26:08.000 | arun, jabesteen | PS5 - Milestone E
PL-004424 | PS5-78-JC-9100B |  | C | E | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | 2026-03-10T08:26:51.000 | arun, jabesteen | PS5 - Milestone E
PL-004425 | PS5-78-JC-9100C |  | C | E | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | 2026-03-10T08:27:09.000 | arun, jabesteen | PS5 - Milestone E
PL-004426 | PS5-78-JC-9100D |  | C | E | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | 2026-03-10T08:27:19.000 | arun, jabesteen | PS5 - Milestone E
PL-004427 | PS5-71-UZ-6500 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-10T12:36:04.680 | THANGARATHINAM, ajikumar | PS5 - Milestone F | 2026-08-13T07:03:24.000
PL-004429 | PS5-71-UZ-6700 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-10T12:44:16.187 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T07:04:28.000
PL-004433 | PS5-71-UZ-6400 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-08 - CFO Pre-Pressure Modules |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-10T12:52:50.320 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-08-13T07:08:08.000
PL-004436 | PS5-71-UZ-6800A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-06 - Crude Fuel Separation Module |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-10T12:55:36.283 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-08-13T07:09:13.000
PL-004439 | PS5-71-UZ-6800B |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-06 - Crude Fuel Separation Module |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-10T12:58:41.397 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-08-13T07:09:51.000
PL-004454 | PS5-09-ACU-0007B-CG01 |  | A | E | PS005-E&I-M6-PL-2234 - Cable 1 side termination | EITS | PS5-63-04 - Electrical Earthing - EITS Building | 2026-07-24T13:54:20.000 | Closed |  | Refer to Job Card BUILD-COW-0082 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-24T13:37:58.000
PL-004455 | PS5-09-ACU-0007A-CG01 |  | A | E | PS005-E&I-M6-PL-2236 - Cable 1 side termination | EITS | PS5-63-04 - Electrical Earthing - EITS Building | 2026-07-24T13:54:29.000 | Closed |  | Refer to Job Card BUILD-COW-0082 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-24T13:38:25.000
PL-004456 | PS5-04-PNC-0002-CG02 |  | A | E | PS005-E&I-M4-PL-2238 - Cable 1 side termination | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0308 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A
PL-004457 | PS5-04-PNC-0001-CA64 |  | A | T | PS005-E&I-M4-PL-2350 - Port number (Terminal no.) N/A at interconnection drawing | EITS | PS5-04-03 - 33kV ICSS System | 2026-03-26T09:26:38.000 | Closed |  | Refer to Job Card BUILD-COW-0194 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A | 2026-03-26T09:26:33.000
PL-004458 | PS5-08-23AN-0004-CV01 |  | A | T | PS005-E&I-ALL-PL-2559 - Coaxial cable to be tested | EITS | PS5-08-23 - VHF Trunk Radio System |  | Originated |  | Refer to Job Card BUILD-COW-0105 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone F
PL-004459 | PS5-08-23AN-1001-CV01 |  | A | T | PS005-E&I-ALL-PL-2560 - Coaxial cable to be tested | EITS | PS5-08-23 - VHF Trunk Radio System |  | Originated |  | Refer to Job Card BUILD-COW-0105 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone F
PL-004460 | PS5-08-23AN-1002-CV01 |  | A | T | PS005-E&I-ALL-PL-2561 - Coaxial cable to be tested | EITS | PS5-08-23 - VHF Trunk Radio System |  | Originated |  | Refer to Job Card BUILD-COW-0105 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone F
PL-004546 | PS5-06-GB-0001A-CU01 |  | A | I | PS005-E&I-M1-PL-2592 - Cable gland for temperature cable sensor in battery room oversize ( General punch for all the buildings) | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-16T13:07:59.000 | Closed |  | Refer to Job Card BUILD-COW-0403 | 2026-03-12T10:52:23.000 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-28T04:21:26.000
PL-004547 | PS5-06-GB-0001B-CU01 |  | A | I | PS005-E&I-M1-PL-2592 - Cable gland for temperature cable sensor in battery room oversize ( General punch for all the buildings) | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-16T13:08:12.000 | Closed |  | Refer to Job Card BUILD-COW-0403 | 2026-03-12T10:52:23.000 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-28T04:24:37.000
PL-004548 | PS5-83-OB-0001 |  | A | B | PS005-E&I-M1-PL-2605 - The MCT installed in the battery room must be replaced with an Ex-rated MCT. | EITS | PS5-83-01 - EITS Building | 2026-07-28T15:12:00.000 | Closed |  | Refer to Job Card BUILD-COW-0404 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-28T13:22:39.000
PL-004549 | PS5-83-OB-0001 |  | A | B | PS005-E&I-M1-PL-2605 - The MCT installed in the battery room must be replaced with an Ex-rated MCT. | EITS | PS5-83-01 - EITS Building | 2026-07-28T15:13:22.000 | Closed |  | Refer to Job Card BUILD-COW-0404 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-28T13:23:09.000
PL-004550 | PS5-83-OB-0001 |  | A | B | PS005-E&I-M1-PL-2605 - The MCT installed in the battery room must be replaced with an Ex-rated MCT. | EITS | PS5-83-01 - EITS Building | 2026-07-28T15:13:49.000 | Closed |  | Refer to Job Card BUILD-COW-0404 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-28T13:23:48.000
PL-004551 | PS5-83-OB-0001 |  | A | B | PS005-E&I-M1-PL-2605 - The MCT installed in the battery room must be replaced with an Ex-rated MCT. | EITS | PS5-83-01 - EITS Building | 2026-07-28T15:15:24.000 | Closed |  | Refer to Job Card BUILD-COW-0404 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-28T13:24:18.000
PL-004552 | PS5-01-UB-6100 |  | C | M | PS005-MEC-ALL-PL-2606 - The name tag is messy, the letters are not straight line | EITS | PS5-01-09 - Inergen for EITS Building | 2026-07-24T11:52:53.000 | Closed |  | Refer to Job Card BUILD-COW-0401 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-07T08:50:47.000
PL-004596 | PS5-83-OB-0001 |  | C | B | PS005-ARC-ALL-PL-2612 - Poor quality of rubber gasket installed on the doors (easy to detaches and some contamined by water) to be replaced with the proper rubber gasket for industrial grade. | EITS | PS5-83-01 - EITS Building | 2026-09-02T13:22:24.000 | Closed |  | Refer to BUILD-COW-0409 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A | 2026-08-16T18:24:37.000
PL-004605 | PS5-83-OB-0001 |  | B | B | PS005-E&I-ALL-PL-2609 - Earthing bonding jumpers drawing mark up to be provided. The shorted material to be provided such as earthing boss, bonding jumper 1core 70 mm2, bonding plate inclued holes and Bolt. | EITS | PS5-83-01 - EITS Building | 2026-05-06T07:01:47.000 | Closed |  | Refer to BUILD-COW-0402 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-06T07:01:44.000
PL-004654 | PS5-09-PDT-0004 |  | B | I | PS005-E&I-COW-1827 - Pressure Differential Transmitters (PDTs) installed for the battery exhaust fans to be replaced with fit to purpose PDTs ( new complete product code 3051CD1A22A1KKSY2L4M5Q4Q8T1D0 / 7th digit = "1" for Differential Pressure Range type = –25 to +25 in H2O / (–62.16 to +62.16 mbar) | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0430 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A
PL-004655 | PS5-09-PDT-0005 |  | B | I | PS005-E&I-COW-1828 - Pressure Differential Transmitters (PDTs) installed for the battery exhaust fans to be replaced with fit to purpose PDTs ( new complete product code 3051CD1A22A1KKSY2L4M5Q4Q8T1D0 / 7th digit = "1" for Differential Pressure Range type = –25 to +25 in H2O / (–62.16 to +62.16 mbar) | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0430 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A
PL-004837 | PS5-60-UA-5100 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-28T08:02:01.077 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T07:10:31.000
PL-004838 | PS5-60-UA-5200 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-26 - Instrument Air Compressor Skid |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-28T08:05:51.737 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T07:11:16.000
PL-004839 | PS5-71-UN-7200 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-02 - CFO Allocation Metering Package |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-28T08:30:49.017 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-08-13T07:11:47.000
PL-004840 | PS5-01-UV-8700 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-01-05 - Foam Skid |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-28T08:37:30.830 | THANGARATHINAM, ajikumar | PS5 - Milestone F | 2026-08-13T07:12:26.000
PL-004841 | PS5-71-UZ-6200 |  | A | M | 10:OSD PUNCH POINTS TO BE CLOSED | CPP AGI | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Completed |  | OSD PUNCH POINTS TO BE CLOSED | 2026-03-28T08:40:06.517 | THANGARATHINAM, ajikumar | PS5 - Milestone F | 2026-07-04T11:56:45.000
PL-004842 | PS5-01-UZ-6900 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-01-10 - Water Mist Package |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-28T08:43:14.887 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-08-13T07:12:56.000
PL-004843 | PS5-01-UK-6100 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100) |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-28T14:03:11.827 | THANGARATHINAM, ajikumar | PS5 - Milestone F | 2026-08-13T07:13:34.000
PL-004844 | PS5-71-TR-4200 |  | B | M | During verification of loose materials received from Velath, I have found some issues which is related to materials. Some spools received from the vendor for the Deluge system are not fabricated as per drawing. N9 The spool received is not as per the drawing(3x2 reducer and 3” flange was not welded with the spool and 2” flange welded.). | EPS VENDOR | PS5-71-12 - CFO Service Tank |  | Originated |  | Vendor to rectify | 2026-03-30T10:34:23.000 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-004905 | PS5-04-PMC-0005-CJ01 |  | A | I | PS005-E&I-COW-1974 - New cable to be added | EITS | PS5-04-04 - 33kV PCS System | 2026-07-30T04:34:11.000 | Closed |  | Refer to Job Card BUILD-COW-0304 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-29T11:21:08.000
PL-004906 | PS5-04-PMC-0008-CC59 |  | A | I | PS005-E&I-COW-1975 - New cable to be added | EITS | PS5-04-04 - 33kV PCS System | 2026-08-01T13:05:48.000 | Closed |  | Refer to Job Card BUILD-COW-0304 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A | 2026-08-01T12:35:20.000
PL-004909 | PS5-08-13CB-1001-CA24 |  | A | T | PS005-E&I-COW-1978 - New cable to be added | EITS | PS5-08-13 - Safety Data Network (SII SP3 SAF) | 2026-07-30T04:39:03.000 | Closed |  | Refer to Job Card BUILD-COW-0304 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C | 2026-07-29T11:21:52.000
PL-004910 | PS5-09-AS-0001A-CD01 |  | A | E | PS005-E&I-COW-1979 - Cable to be removed | EITS | PS5-09-05 - HVAC for EITS Building | 2026-07-23T08:08:16.000 | Closed |  | Refer to Job Card BUILD-COW-0308 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-28T05:38:42.000
PL-004911 | PS5-09-AS-0001B-CD01 |  | A | E | PS005-E&I-COW-1980 - Cable to be removed | EITS | PS5-09-05 - HVAC for EITS Building | 2026-07-23T08:08:35.000 | Closed |  | Refer to Job Card BUILD-COW-0308 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-28T05:39:22.000
PL-004912 | PS5-09-AS-0002A-CD01 |  | A | E | PS005-E&I-COW-1981 - Cable to be removed | EITS | PS5-09-05 - HVAC for EITS Building | 2026-07-23T08:08:47.000 | Closed |  | Refer to Job Card BUILD-COW-0308 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-28T05:39:38.000
PL-004913 | PS5-09-AS-0002B-CD01 |  | A | E | PS005-E&I-COW-1982 - Cable to be removed | EITS | PS5-09-05 - HVAC for EITS Building | 2026-07-23T08:08:57.000 | Closed |  | Refer to Job Card BUILD-COW-0308 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-28T05:39:54.000
PL-004914 | PS5-61-IJ-0011-CA03 |  | A | T | PS005-E&I-COW-1983 - New cable to be added | EITS | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) | 2026-08-01T13:06:10.000 | Closed |  | Refer to Job Card BUILD-COW-0304 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone G | 2026-08-01T12:35:56.000
PL-004915 | PS5-61-IE-0003-CS03 |  | A | E | PS005-E&I-COW-1984 - Cable to be removed | EITS | PS5-61-08 - Electrical Control System | 2026-08-01T13:06:30.000 | Closed |  | Refer to Job Card BUILD-COW-0308 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C | 2026-08-01T12:36:32.000
PL-005182 | PS5-01-UV-8700 |  | B | M | Internal piping within the skid to be completed & reinstated | CPP AGI | PS5-01-05 - Foam Skid |  | Originated |  | Internal piping within the skid to be completed & reinstated | 2026-04-13T07:20:30.000 | arun, jabesteen | PS5 - Milestone F
PL-005183 | PS5-01-UV-8700 |  | B | M | OSD points to be cleared and closed | EPS VENDOR | PS5-01-05 - Foam Skid |  | Originated |  | OSD points to be cleared and closed | 2026-04-13T07:22:16.000 | arun, jabesteen | PS5 - Milestone F
PL-005184 | PS5-01-UV-8700 |  | C | M | Touch up painting to be completed | CPP AGI | PS5-01-05 - Foam Skid |  | Originated |  | Touch up painting to be completed | 2026-04-13T07:24:33.000 | arun, jabesteen | PS5 - Milestone F
PL-005252 | PS5-53-TR-4100 |  | A | M | Opening of cage ladder fabricated in the wrong direction. To be corrected as per drawing (requirement) | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank | 2026-07-04T11:58:16.000 | Closed |  | VENDOR TO RECTIFY | 2026-04-14T06:05:04.000 | THANGARATHINAM, ajikumar | PS5 - Milestone C | 2026-07-04T11:58:12.000
PL-005263 | PS5-60-UR-8300A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-35 - Injector Tip Cooling Module A |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-04-17T12:19:51.787 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T07:14:38.000
PL-005265 | PS5-60-UR-8300B |  | B | P | 10.1:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-36 - Injector Tip Cooling Module B |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-04-17T12:22:27.747 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T07:14:59.000
PL-005266 | PS5-60-UR-8300C |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-37 - Injector Tip Cooling Module C |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-04-17T12:25:51.313 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T07:15:29.000
PL-005267 | PS5-60-UR-8300D |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-38 - Injector Tip Cooling Module D |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-04-17T12:27:21.450 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T07:16:08.000
PL-005268 | PS5-60-UR-8300E |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-39 - Injector Tip Cooling Module E |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-04-17T12:28:55.007 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T07:16:31.000
PL-005269 | PS5-60-UR-8300F |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-40 - Injector Tip Cooling Module F |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-04-17T12:30:30.900 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T07:17:07.000
PL-005270 | PS5-60-UR-8300G |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-41 - Injector Tip Cooling Module G |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-04-17T12:32:08.740 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-08-13T07:18:10.000
PL-005299 | PS5-60-VA-5100C |  | B | E | 23.1: EARTHING TO BE DONE | CPP AGI | PS5-60-30 - Air Receiver C & Air Regulator C |  | Originated |  | EARTHING TO BE DONE | 2026-04-21T07:58:44.537 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-005300 | PS5 - CFO AREA_Earthing |  | B | E | 7 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install all earth bosses as per the drawing and proceed with the termination of the earthing cables at the bosses and equipment | 2026-04-21T11:23:42.880 | Mohamed, Amira | PS5 - Milestone A
PL-005308 | PS5-61-IJ-0001-CH01 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-01 - Power Generation Package A |  | Completed |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-21T12:38:25.000 | Mohamed, Amira | PS5 - Milestone B | 2026-08-27T08:51:03.000
PL-005309 | PS5-61-IJ-0001-CH02 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-01 - Power Generation Package A |  | Completed |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-21T14:21:05.427 | Mohamed, Amira | PS5 - Milestone B | 2026-08-27T08:52:06.000
PL-005310 | PS5-61-IJ-0001-CH03 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-01 - Power Generation Package A |  | Completed |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-21T14:23:54.797 | Mohamed, Amira | PS5 - Milestone B | 2026-08-27T08:52:44.000
PL-005311 | PS5-61-IJ-0001-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-04 - Power Generation Package B |  | Completed |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-21T14:25:28.087 | Mohamed, Amira | PS5 - Milestone B | 2026-08-22T07:18:58.000
PL-005312 | PS5-61-IJ-0001-CH05 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-04 - Power Generation Package B |  | Completed |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-21T14:28:49.000 | Mohamed, Amira | PS5 - Milestone B | 2026-08-22T07:20:31.000
PL-005313 | PS5-61-IJ-0001-CH06 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-04 - Power Generation Package B |  | Completed |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-21T14:32:16.990 | Mohamed, Amira | PS5 - Milestone B | 2026-08-22T07:18:23.000
PL-005314 | PS5-61-IJ-0001-CH07 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-22T06:19:24.473 | Mohamed, Amira | PS5 - Milestone D
PL-005315 | PS5-61-IJ-0001-CH08 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-22T06:22:02.900 | Mohamed, Amira | PS5 - Milestone D
PL-005318 | PS5-61-IJ-0001-CH09 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-22T08:07:20.090 | Mohamed, Amira | PS5 - Milestone D
PL-005415 | PS5-61-IJ-0001 |  | A | E | PS005-E&I-COW-2194 - CTs and secondary wiring are not installed in side CT Box | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Completed |  | Refer to Job Card BUILD-COW-0470 | 2026-04-22T09:53:13.457 | Thao-my, Alexandre | PS5 - Milestone D | 2026-08-16T18:27:58.000
PL-005428 | PS5-06-GU-0001-CC03 |  | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-06-GU-0001-CC03 INSTRUMENTATION CABLE | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-28T06:56:57.000 | Closed |  | Refer to BUILD-COW-0082 | 2026-04-22T09:53:13.457 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-27T14:06:22.000
PL-005429 | PS5-06-GU-0001-CC04 |  | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-06-GU-0001-CC04 INSTRUMENTATION CABLE | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-28T06:57:06.000 | Closed |  | Refer to BUILD-COW-0082 | 2026-04-22T09:53:13.457 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-27T14:06:52.000
PL-005430 | PS5-06-GU-0001-CJ01 |  | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-06-GU-0001-CJ01 INSTRUMENTATION CABLE | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-28T06:57:15.000 | Closed |  | Refer to BUILD-COW-0082 | 2026-04-22T09:53:13.457 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-27T14:07:32.000
PL-005431 | PS5-06-GU-0001-CJ02 |  | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-06-GU-0001-CJ02 INSTRUMENTATION CABLE | EITS | PS5-06-01 - AC UPS - EITS Building | 2026-07-28T06:57:23.000 | Closed |  | Refer to BUILD-COW-0082 | 2026-04-22T09:53:13.457 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-27T14:07:59.000
PL-005432 | PS5-08-01IO-1004-CJ01 |  | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-08-01IO-1004-CJ01 (HOLD) INSTRUMENTATION CABLE | EITS | PS5-08-13 - Safety Data Network (SII SP3 SAF) | 2026-08-05T06:08:00.000 | Closed |  | Refer to BUILD-COW-0082 | 2026-04-22T09:53:13.457 | Thao-my, Alexandre | PS5 - Milestone C | 2026-08-05T05:44:37.000
PL-005479 | PS5-61-IJ-0001-CH10 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-22T10:24:15.897 | Mohamed, Amira | PS5 - Milestone D
PL-005480 | PS5-61-IJ-0001-CH11 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-22T10:26:59.297 | Mohamed, Amira | PS5 - Milestone D
PL-005481 | PS5-61-IJ-0001-CH12 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-22T10:33:23.213 | Mohamed, Amira | PS5 - Milestone D
PL-005484 | PS5-74-UB-5100 |  | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-74-01 - N2 Generation Skid |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-04-23T08:50:52.790 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-005485 | PS5-61-IJ-0001-CH13 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-13 - Power Generation Package E |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-23T10:26:55.773 | Mohamed, Amira | PS5 - Milestone D
PL-005487 | PS5-74-UB-5100 |  | A | M | 10.1: BROKEN SPOOL TO BE REPLACED | CPP AGI | PS5-74-01 - N2 Generation Skid | 2026-07-04T11:59:14.000 | Closed |  | BROKEN SPOOL TO BE REPLACED | 2026-04-23T10:38:29.827 | THANGARATHINAM, ajikumar | PS5 - Milestone F | 2026-07-04T11:59:08.000
PL-005488 | PS5-61-IJ-0001-CH14 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-13 - Power Generation Package E |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-23T10:38:51.317 | Mohamed, Amira | PS5 - Milestone D
PL-005489 | PS5-61-IJ-0001-CH15 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-13 - Power Generation Package E |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-23T10:41:24.167 | Mohamed, Amira | PS5 - Milestone D
PL-005490 | PS5-61-IJ-0001-CH16 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-16 - Power Generation Package F |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-23T10:42:50.107 | Mohamed, Amira | PS5 - Milestone D
PL-005491 | PS5-61-IJ-0001-CH17 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-16 - Power Generation Package F |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-23T10:48:28.460 | Mohamed, Amira | PS5 - Milestone D
PL-005492 | PS5-61-IJ-0001-CH18 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-16 - Power Generation Package F |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-23T10:51:32.810 | Mohamed, Amira | PS5 - Milestone D
PL-005493 | PS5-61-IJ-0001-CH19 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-23T10:53:00.127 | Mohamed, Amira | PS5 - Milestone E
PL-005494 | PS5-61-IJ-0001-CH20 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-23T10:54:23.153 | Mohamed, Amira | PS5 - Milestone E
PL-005495 | PS5-61-IJ-0001-CH21 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-23T10:55:43.433 | Mohamed, Amira | PS5 - Milestone E
PL-005535 | PS5-25-DM-3100A-CH01 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T11:01:19.523 | Mohamed, Amira | PS5 - Milestone H
PL-005536 | PS5-25-DM-3100A-CH02 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T11:02:52.650 | Mohamed, Amira | PS5 - Milestone H
PL-005537 | PS5-25-DM-3100A-CH03 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T11:04:52.903 | Mohamed, Amira | PS5 - Milestone H
PL-005538 | PS5-25-DM-3100A-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T11:06:16.940 | Mohamed, Amira | PS5 - Milestone H
PL-005539 | PS5-25-DM-3100A-CH05 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T11:07:36.717 | Mohamed, Amira | PS5 - Milestone H
PL-005540 | PS5-25-DM-3100A-CH06 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T11:08:45.220 | Mohamed, Amira | PS5 - Milestone H
PL-005541 | PS5-25-DM-3100B-CH01 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T11:56:44.023 | Mohamed, Amira | PS5 - Milestone H
PL-005542 | PS5-25-DM-3100B-CH02 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T11:58:31.710 | Mohamed, Amira | PS5 - Milestone H
PL-005543 | PS5-25-DM-3100B-CH03 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T12:00:15.990 | Mohamed, Amira | PS5 - Milestone H
PL-005545 | PS5-28-PA-3600A |  | A | M | CPP USE 15W40 FOR BEARING LUBRICATION INSTEAD OF vg32 | EACOP | PS5-28-08 - Open Drain Sump and Pumps |  | Originated |  | THE OIL MUST BE FLUSHED BEFORE COMMISSIONING | 2026-04-24T13:43:05.000 | arun, jabesteen | PS5 - Milestone G
PL-005546 | PS5-28-PA-3600B |  | A | M | CPP USE 15W40 FOR BEARING LUBRICATION INSTEAD OF vg32 | EACOP | PS5-28-08 - Open Drain Sump and Pumps |  | Originated |  | THE OIL MUST BE FLUSHED BEFORE COMMISSIONING | 2026-04-24T13:45:20.000 | arun, jabesteen | PS5 - Milestone G
PL-005547 | PS5-28-PA-3500 |  | A | M | CPP USE 15W40 FOR BEARING LUBRICATION INSTEAD OF vg32 | EACOP | PS5-28-08 - Open Drain Sump and Pumps |  | Originated |  | THE OIL MUST BE FLUSHED BEFORE COMMISSIONING | 2026-04-24T13:47:09.000 | arun, jabesteen | PS5 - Milestone G
PL-005558 | PS5-25-DM-3100B-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-25T11:14:03.777 | Mohamed, Amira | PS5 - Milestone H
PL-005559 | PS5-25-DM-3100B-CH05 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-25T11:15:46.913 | Mohamed, Amira | PS5 - Milestone H
PL-005560 | PS5-25-DM-3100B-CH06 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-25T11:17:03.910 | Mohamed, Amira | PS5 - Milestone H
PL-005561 | PS5-25-DM-3100C-CH01 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-25T11:18:20.940 | Mohamed, Amira | PS5 - Milestone H
PL-005562 | PS5-25-DM-3100C-CH02 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-25T11:19:42.323 | Mohamed, Amira | PS5 - Milestone H
PL-005563 | PS5-25-DM-3100C-CH03 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-25T11:21:30.170 | Mohamed, Amira | PS5 - Milestone H
PL-005564 | PS5-25-DM-3100C-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-25T11:23:38.707 | Mohamed, Amira | PS5 - Milestone H
PL-005565 | PS5-25-DM-3100C-CH05 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-25T11:26:43.300 | Mohamed, Amira | PS5 - Milestone H
PL-005566 | PS5-25-DM-3100C-CH06 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-25T11:28:02.603 | Mohamed, Amira | PS5 - Milestone H
PL-005571 | PS5-83-OB-0001_Installation |  | A | E | Leveling and cleaning of the floor and cable trays/ladders | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | Level and clean the floor surface beneath the cable trays to ensure a stable and even installation, with no contact between the supports and the ground. | 2026-04-27T07:03:10.967 | Mohamed, Amira | PS5 - Milestone A
PL-005572 | PS5-83-OB-0001_Installation |  | B | E | Corrosion need to be removed | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | Remove all corrosion from cable trays and ladders and treat the affected areas with appropriate anti-corrosion protection | 2026-04-27T07:06:51.970 | Mohamed, Amira | PS5 - Milestone A
PL-005574 | PS5-83-OB-0001_Installation |  | A | E | Hold down Clamp not Installed yet | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | Install the hold-down clamps once they become available on site, in accordance with the approved drawings. | 2026-04-27T07:10:03.210 | Mohamed, Amira | PS5 - Milestone A
PL-005575 | PS5-83-OB-0001_Installation |  | B | E | Earth jumper not installed completely | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | Complete the installation of all earth jumpers in accordance with the approved drawings and ensure proper earthing continuity | 2026-04-27T07:13:07.333 | Mohamed, Amira | PS5 - Milestone A
PL-005751 | PS5-09-LB-0001 |  | B | H | PS005-E&I-ALL-PL-2596 - HVAC UCP is unable to read PDT-0004/0005 value correctly dut to oversized scale 0-300psi. (current value: High: 62210 Pa, Low:-62210Pa, Low alarm: 50 Pa) | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | PLC/HMI program updated, refer to BUILD-COW-0451 for new PLC/HMI program upload | 2026-04-28T05:08:51.687 | Thao-my, Alexandre | PS5 - Milestone A
PL-005752 | PS5-09-LB-0001 |  | B | H | PS005-HVA-ALL-PL-2595 - Temporary banner for "Force run time" to be deleted | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | PLC/HMI program updated, refer to BUILD-COW-0451 for new PLC/HMI program upload | 2026-04-28T05:08:51.687 | Thao-my, Alexandre | PS5 - Milestone A
PL-005753 | PS5-09-LB-0001 |  | B | H | PS005-HVA-ALL-PL-2597 - The latested PLC program to be implemented and to be performed demonstration on site | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | PLC/HMI program updated, refer to BUILD-COW-0451 for new PLC/HMI program upload | 2026-04-28T05:08:51.687 | Thao-my, Alexandre | PS5 - Milestone A
PL-005754 | PS5-09-LB-0001 |  | B | H | PS005-HVA-ALL-PL-2599 - TSH alarm tag to be provided | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | PLC/HMI program updated, refer to BUILD-COW-0451 for new PLC/HMI program upload | 2026-04-28T05:08:51.687 | Thao-my, Alexandre | PS5 - Milestone A
PL-005755 | PS5-09-LB-0001 |  | B | H | PS005-HVA-ALL-PL-2600 - Extract Fan PDT-0003/0004 High / Low Set point to be validated and set accordingly | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | PLC/HMI program updated, refer to BUILD-COW-0451 for new PLC/HMI program upload | 2026-04-28T05:08:51.687 | Thao-my, Alexandre | PS5 - Milestone A
PL-005756 | PS5-09-LB-0001 |  | B | H | PS005-HVA-ALL-PL-2602 - HVAC UCP Heater function to be demonstrated (2.3 Pre iFAT Power up tests and checks) | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | Part of HVAC System SAT Procedure, the punch must be closed after the demonstration during the SAT | 2026-04-28T05:08:51.687 | Thao-my, Alexandre | PS5 - Milestone A
PL-005769 | PS5-28-VK-1200 |  | B | M | 4:The relief drum tag number is not correct to be rectified(Required PS5-28-VK-1200 but received as PS4-28-VK-1200) | EPS VENDOR | PS5-28-06 - Relief Drum and Pump | 2026-07-09T12:39:46.000 | Closed |  |  | 2026-04-28T07:53:04.237 | THANGARATHINAM, ajikumar | PS5 - Milestone G | 2026-07-09T12:39:42.000
PL-006055 | PS5-61-IK-0003-CG07 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-07T05:35:47.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-07T12:55:32.933 | Mohamed, Amira | PS5 - Milestone C | 2026-05-07T13:02:53.000
PL-006056 | PS5-25-ESDV-0021-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-01 - Export Pipeline Pig Receiver | 2026-06-14T08:34:46.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-07T13:41:30.610 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:34:39.000
PL-006058 | PS5-25-ESDV-0023-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-07 - Export Pipeline Pig Launcher | 2026-06-14T08:35:37.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-07T14:24:50.787 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:35:33.000
PL-006061 | PS5-25-FCV-0003A-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-02 - Crude Oil Export Pump A | 2026-06-14T08:36:11.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-08T08:18:17.823 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:36:06.000
PL-006062 | PS5-25-FCV-0003B-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-03 - Crude Oil Export Pump B | 2026-06-14T08:36:53.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-08T08:37:27.640 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:36:49.000
PL-006063 | PS5-25-FCV-0003C-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-04 - Crude Oil Export Pump C | 2026-06-14T08:39:04.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-08T09:20:11.503 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:39:00.000
PL-006064 | PS5-25-SDV-0054A-CL01 |  | A | E | Cable to be connected . | CPP AGI | PS5-25-02 - Crude Oil Export Pump A | 2026-06-14T08:40:15.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-08T09:28:01.973 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:40:10.000
PL-006065 | PS5-25-SDV-0054B-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-03 - Crude Oil Export Pump B | 2026-06-14T08:41:45.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-08T09:33:27.343 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:41:42.000
PL-006066 | PS5-25-SDV-0054C-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-04 - Crude Oil Export Pump C | 2026-06-08T10:13:09.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-08T10:58:40.997 | Mohamed, Amira | PS5 - Milestone H | 2026-06-08T10:12:45.000
PL-006067 | PS5-28-SDV-0053A-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-28-13 - Seal Oil Drain Drum & Pump A | 2026-06-14T08:42:32.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-08T11:02:25.860 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:42:26.000
PL-006068 | PS5-61-IK-0006-CL19 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:43:08.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-08T11:10:54.700 | Mohamed, Amira | PS5 - Milestone D | 2026-06-14T08:43:02.000
PL-006069 | PS5-61-IK-0006-CL20 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:45:54.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-08T11:22:54.237 | Mohamed, Amira | PS5 - Milestone D | 2026-06-14T08:45:51.000
PL-006070 | PS5-61-IK-0006-CL21 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:46:07.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-08T11:33:22.627 | Mohamed, Amira | PS5 - Milestone D | 2026-06-14T08:46:04.000
PL-006071 | PS5-61-IK-0006-CL22 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:46:21.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-08T11:40:03.963 | Mohamed, Amira | PS5 - Milestone D | 2026-06-14T08:46:18.000
PL-006072 | PS5-62-IE-0001-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-62-01 - Lighting Control Panel - PS5-62-IE-0001 | 2026-06-14T08:46:33.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-08T11:45:56.457 | Mohamed, Amira | PS5 - Milestone G | 2026-06-14T08:46:30.000
PL-006073 | PS5-71-HE-2400A-CL01 |  | A | E | Cable to be connected . | CPP AGI | PS5-71-01 - CFO Storage Tank Feed Heater | 2026-06-14T08:46:46.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-08T11:59:15.173 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:46:42.000
PL-006074 | PS5-71-HE-2400A-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-71-01 - CFO Storage Tank Feed Heater | 2026-06-14T08:46:57.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-08T12:04:47.010 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:46:54.000
PL-006090 | PS5-25-DM-3100A-CD01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-02 - Crude Oil Export Pump A | 2026-06-14T08:47:26.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-09T08:46:31.927 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:47:23.000
PL-006091 | PS5-25-DM-3100B-CD01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-03 - Crude Oil Export Pump B | 2026-06-14T08:47:43.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-09T10:15:46.883 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:47:39.000
PL-006092 | PS5-25-DM-3100C-CD01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-04 - Crude Oil Export Pump C | 2026-06-14T08:47:56.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-09T10:23:16.057 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:47:52.000
PL-006093 | PS5-62-IE-0001-CD01 |  | A | E | Cable to be connected | CPP AGI | PS5-62-01 - Lighting Control Panel - PS5-62-IE-0001 | 2026-06-14T08:48:09.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-09T10:34:03.573 | Mohamed, Amira | PS5 - Milestone G | 2026-06-14T08:48:06.000
PL-006094 | PS5-61-IDH-3100A-CD03 |  | A | E | Cable to be connected | CPP AGI | PS5-25-02 - Crude Oil Export Pump A | 2026-06-14T08:48:22.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-09T10:47:12.270 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:48:19.000
PL-006097 | PS5-61-IDH-3100B-CD03 |  | A | E | Cable to be connected | CPP AGI | PS5-25-03 - Crude Oil Export Pump B | 2026-06-14T08:48:35.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-09T10:55:04.610 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:48:32.000
PL-006100 | PS5-61-IDH-3100C-CD03 |  | A | E | Cable to be connected | CPP AGI | PS5-25-04 - Crude Oil Export Pump C | 2026-06-14T08:49:01.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-09T11:00:37.977 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:48:57.000
PL-006142 | PS5-71-TR-4200 |  | A | M | Platform structure middle member of cfo service tank is not matching with gratings and connected drawing. To be modified | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-07-04T11:59:50.000 | Closed |  | vendor to rectify | 2026-05-11T10:00:52.000 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-07-04T11:59:46.000
PL-006193 | PS5-25-DM-3100B-CG01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-03 - Crude Oil Export Pump B | 2026-06-14T08:49:13.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-12T07:03:32.610 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:49:10.000
PL-006215 | PS5-61-IJ-0001 |  | B | E | PS005-E&I-COW-1126 - ALL CUBICLES: FINAL PROTECTION SETTINGS ARE NOT SET. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0011 | 2026-05-12T09:31:34.577 | Thao-my, Alexandre | PS5 - Milestone D
PL-006253 | PS5-61-IK-0001 |  | B | E | PS005-E&I-COW-1172 - INCOMERS: FINAL PROTECTION SETTINGS ARE NOT SET. | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0146 | 2026-05-12T09:31:34.577 | Thao-my, Alexandre | PS5 - Milestone A
PL-006281 | PS5-25-DM-3100B-CG02 |  | A | E | cable to be connected | CPP AGI | PS5-25-03 - Crude Oil Export Pump B | 2026-06-14T08:49:39.000 | Closed |  | cable must be connected glanded and terminated | 2026-05-14T06:49:11.467 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:49:36.000
PL-006282 | PS5-25-DM-3100C-CG01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-04 - Crude Oil Export Pump C | 2026-06-14T08:49:51.000 | Closed |  | Cable must be connected, and terminated. | 2026-05-14T07:11:01.577 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:49:47.000
PL-006283 | PS5-60-TCV-0001A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  |  | 2026-05-14T07:55:31.963 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T08:34:00.000
PL-006284 | PS5-60-TCV-0001A |  | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2026-05-14T07:56:39.673 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-006285 | PS5-60-TCV-0001B |  | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2026-05-14T07:59:41.020 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-006286 | PS5-60-TCV-0001B |  | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2026-05-14T08:00:18.030 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-006287 | PS5-60-TCV-0001D |  | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2026-05-14T08:02:18.983 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006288 | PS5-60-TCV-0001D |  | C | M | 10.1: TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2026-05-14T08:02:52.650 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006289 | PS5-60-TCV-0001F |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Completed |  |  | 2026-05-14T08:04:51.790 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T08:37:51.000
PL-006290 | PS5-60-TCV-0001F |  | C | M | 10.1: TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2026-05-14T08:05:48.017 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006291 | PS5-60-TCV-0001G |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-76 - Engine G Cooling system |  | Completed |  |  | 2026-05-14T08:07:50.040 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-08-13T08:39:11.000
PL-006292 | PS5-60-TCV-0001G |  | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2026-05-14T08:08:22.723 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-006293 | PS5-60-TCV-0002A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  |  | 2026-05-14T08:11:22.737 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T08:40:16.000
PL-006294 | PS5-60-TCV-0002A |  | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2026-05-14T08:11:53.697 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-006295 | PS5-60-TCV-0002B |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  |  | 2026-05-14T08:14:06.440 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T08:41:39.000
PL-006296 | PS5-60-TCV-0002B |  | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  |  | 2026-05-14T08:14:45.553 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T08:42:23.000
PL-006297 | PS5-60-TCV-0002C |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  |  | 2026-05-14T08:16:27.783 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T08:42:58.000
PL-006298 | PS5-60-TCV-0002C |  | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  |  | 2026-05-14T08:17:07.970 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006299 | PS5-60-TCV-0002D |  | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2026-05-14T08:20:05.270 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006300 | PS5-60-TCV-0002D |  | C | M | 10.1:touch up painting to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2026-05-14T08:20:36.130 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006301 | PS5-60-TCV-0002E |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Completed |  |  | 2026-05-14T08:22:22.650 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T08:44:30.000
PL-006302 | PS5-60-TCV-0002E |  | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  |  | 2026-05-14T08:22:59.843 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006303 | PS5-60-TCV-0002F |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Completed |  |  | 2026-05-14T08:25:41.170 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T08:45:11.000
PL-006304 | PS5-60-TCV-0002F |  | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2026-05-14T08:26:15.573 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006305 | PS5-60-TCV-0002G |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-76 - Engine G Cooling system |  | Completed |  |  | 2026-05-14T08:28:13.333 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-08-13T08:46:29.000
PL-006306 | PS5-60-TCV-0002G |  | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2026-05-14T08:28:45.423 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-006313 | PS5-25-DM-3100C-CG02 |  | A | E | Cable to be connected | CPP AGI | PS5-25-04 - Crude Oil Export Pump C | 2026-06-14T08:50:23.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-14T10:54:37.353 | Mohamed, Amira | PS5 - Milestone H | 2026-06-14T08:50:20.000
PL-006314 | PS5-79-BH-0002-CH01 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-05-14T11:13:36.770 | Mohamed, Amira | PS5 - Milestone G
PL-006315 | PS5-79-BH-0002-CH02 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-05-14T11:42:45.970 | Mohamed, Amira | PS5 - Milestone G
PL-006316 | PS5-79-BH-0002-CH03 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-05-14T11:59:34.407 | Mohamed, Amira | PS5 - Milestone G
PL-006317 | PS5-04-PMC-0001 |  | A | B | PS005-E&I-M4-PL-1286 - Terminal to be update on termination drawing by enginnering (mark up drawing) (PS5-04-PMC-0001-CS01) | EITS | PS5-04-04 - 33kV PCS System | 2026-05-19T15:37:29.000 | Closed |  | Document update | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A | 2026-05-19T15:37:24.000
PL-006318 | PS5-09-ACU-0007B-CD02 |  | A | E | PS005-E&I-M4-PL-2369 - Cable One Side Termination (COW) | EITS | PS5-09-05 - HVAC for EITS Building | 2026-07-24T11:55:29.000 | Closed |  | Refer to Job Card BUILD-COW-0082 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-24T01:05:12.000
PL-006332 |  | PS5-06-GB-0001A | B | E | PS005-E&I-COW-1876 - Ensure that the battery connector is compatible with the cable’s rigidity and cross-sectional characteristics. Modify the battery interconnection cables so that the positive and negative terminals are routed from the left side of the rack. | EITS | PS5-06-01 - AC UPS - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0415 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A
PL-006333 |  | PS5-06-GB-0001B | B | E | PS005-E&I-COW-1877 - Ensure that the battery connector is compatible with the cable’s rigidity and cross-sectional characteristics. Modify the battery interconnection cables so that the positive and negative terminals are routed from the left side of the rack. | EITS | PS5-06-01 - AC UPS - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0415 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A
PL-006391 | PS5-61-IK-0001 |  | B | E | PS005-E&I-COW-2175 - CUBICLE : CABLE SUPPORT MISSING AND CABLE ARRANGMENT TO BE REWORKED - PS4-61-IK-0001-C01 | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0131 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A
PL-006429 | PS5-04-PMC-0003-CN01 |  | A | T | PS005-E&I-COW-2329 - New cable to be added | EITS | PS5-04-04 - 33kV PCS System | 2026-08-01T13:06:49.000 | Closed |  | Refer to Job Card BUILD-COW-0304 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A | 2026-08-01T12:37:17.000
PL-006430 | PS5-04-PMC-0003-CN02 |  | A | T | PS005-E&I-COW-2330 - New cable to be added | EITS | PS5-04-04 - 33kV PCS System | 2026-08-01T13:07:06.000 | Closed |  | Refer to Job Card BUILD-COW-0304 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A | 2026-08-01T12:38:45.000
PL-006431 | PS5-04-PSC-0001 |  | A | I | PS005-E&I-M3-PL-2591 - AGI NEW 4 SWITCHES TO BE INSTALLED AND WIRE | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0406 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A
PL-006449 | PS5-08-86IO-1002-CC01 |  | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-08-86IO-1002-CC01 (HOLD) INSTRUMENTATION CABLE | EITS | PS5-08-15 - Security Data Network (SII SP3 SEC) | 2026-08-05T07:08:54.000 | Closed |  | Refer to Job Card BUILD-COW-0082 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone C | 2026-08-05T06:25:58.000
PL-006450 | PS5-09-ACU-0007A-CP01 |  | A | E | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-09-ACU-0007A-CP01 POWER CABLE | EITS | PS5-09-05 - HVAC for EITS Building | 2026-07-25T04:43:34.000 | Closed |  | Refer to Job Card BUILD-COW-0082 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-25T02:14:30.000
PL-006451 | PS5-09-ACU-0007B-CP01 |  | A | E | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-09-ACU-0007B-CP01 POWER CABLE | EITS | PS5-09-05 - HVAC for EITS Building | 2026-07-25T04:43:54.000 | Closed |  | Refer to Job Card BUILD-COW-0082 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A | 2026-07-25T02:16:03.000
PL-006488 | PS5-61-IK-0003-CL13 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:50:38.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-16T05:53:28.157 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:50:35.000
PL-006489 | PS5-61-IK-0003-CL14 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:50:52.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-16T07:48:45.267 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:50:48.000
PL-006490 | PS5-61-IK-0003-CL15 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:51:32.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T08:02:09.513 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:51:28.000
PL-006491 | PS5-61-IK-0003-CL16 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:51:44.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T08:34:07.590 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:51:41.000
PL-006492 | PS5-61-IK-0003-CL17 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:51:58.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T10:27:26.020 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:51:55.000
PL-006493 | PS5-61-IK-0003-CL36 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:52:11.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T10:52:36.223 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:52:08.000
PL-006494 | PS5-61-IK-0003-CL18 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:52:27.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T10:54:10.883 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:52:23.000
PL-006495 | PS5-61-IK-0003-CL35 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:52:43.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:00:20.333 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:52:39.000
PL-006496 | PS5-61-IK-0003-CL34 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:52:57.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:08:23.987 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:52:52.000
PL-006497 | PS5-61-IK-0003-CL19 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:53:10.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:08:38.967 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:53:07.000
PL-006498 | PS5-61-IK-0003-CL20 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:53:23.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:14:26.040 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:53:20.000
PL-006499 | PS5-61-IK-0003-CL33 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:53:36.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:14:34.963 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:53:32.000
PL-006500 | PS5-61-IK-0003-CL32 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:53:48.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:21:05.020 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:53:44.000
PL-006501 | PS5-61-IK-0003-CL21 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:54:57.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:22:01.893 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:54:53.000
PL-006502 | PS5-61-IK-0003-CL31 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:55:12.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:28:53.467 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:55:09.000
PL-006503 | PS5-61-IK-0003-CL22 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:55:26.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:32:41.743 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:55:22.000
PL-006504 | PS5-61-IK-0003-CL30 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:55:45.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:40:18.477 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:55:41.000
PL-006505 | PS5-61-IK-0003-CL23 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:56:00.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:40:55.070 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:55:56.000
PL-006506 | PS5-61-IK-0006-CL10 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:56:16.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:46:05.713 | Mohamed, Amira | PS5 - Milestone D | 2026-06-14T08:56:12.000
PL-006507 | PS5-61-IK-0003-CL24 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:56:34.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:49:55.427 | Mohamed, Amira | PS5 - Milestone B | 2026-06-14T08:56:30.000
PL-006508 | PS5-61-IK-0006-CL11 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:57:01.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:56:25.787 | Mohamed, Amira | PS5 - Milestone D | 2026-06-14T08:56:58.000
PL-006509 | PS5-61-IK-0006-CL12 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:57:16.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T12:04:44.560 | Mohamed, Amira | PS5 - Milestone D | 2026-06-14T08:57:13.000
PL-006510 | PS5-61-IK-0006-CL13 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:57:29.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T12:06:29.503 | Mohamed, Amira | PS5 - Milestone D | 2026-06-14T08:57:25.000
PL-006512 | PS5-61-IK-0006-CL16 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:57:57.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T12:11:25.530 | Mohamed, Amira | PS5 - Milestone D | 2026-06-14T08:57:54.000
PL-006513 | PS5-61-IK-0006-CL17 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:58:09.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T12:29:50.740 | Mohamed, Amira | PS5 - Milestone D | 2026-06-14T08:58:05.000
PL-006514 | PS5-61-IK-0006-CL18 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:58:21.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T12:39:34.300 | Mohamed, Amira | PS5 - Milestone D | 2026-06-14T08:58:17.000
PL-006515 | PS5-61-IK-0006-CL14 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:58:34.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-16T13:00:24.507 | Mohamed, Amira | PS5 - Milestone D | 2026-06-14T08:58:29.000
PL-006516 | PS5-61-IK-0006-CL15 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:58:45.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T13:07:46.140 | Mohamed, Amira | PS5 - Milestone D | 2026-06-14T08:58:42.000
PL-006559 | PS5-61-IV-0002A |  | B | M | 4:Quality of welding in the transformer is not upto the standard. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T12:47:14.887 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006560 | PS5-61-IV-0002A |  | B | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T12:48:54.633 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006561 | PS5-61-IV-0002A |  | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T12:50:20.720 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006562 | PS5-61-IV-0002A |  | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T12:51:56.177 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006563 | PS5-61-IV-0002A |  | A | E | 4.4:Flexible conduit routing over the enclosure is improperly installed or broken | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T12:54:36.423 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006564 | PS5-61-IV-0002A |  | B | E | 4.5:Earthing cable not connected, poor cable management, improper stripping, and improper glanding | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T12:56:26.260 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006565 | PS5-61-IV-0002A |  | B | E | 4.6:Internal wiring and cable entry inside the enclosure are poorly installed and not properly managed, unused openings are covered by rubber plugs | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T12:57:46.530 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006566 | PS5-61-IV-0002A |  | B | E | 4.7:The opening has been temporarily sealed using plastic tape. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T12:59:12.617 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006567 | PS5-61-IV-0002A |  | A | E | 4.8:Flexible conduit not properly terminated into the cable gland. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T13:00:18.810 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006568 | PS5-61-IV-0002A |  | A | E | 4.9:All cable entries are not properly tightened and cables are not properly sealed in cable glands. Applicable for all transformers. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T13:02:15.380 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006569 | PS5-61-IV-0002A |  | A | E | 4.10:64. No heat-shrink sleeves are installed on the cable inside the main panel. Applicable for all transformers. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T13:03:03.237 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006570 | PS5-61-IV-0002A |  | A | E | 4.11:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). Applicable for all transformers. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T13:04:24.403 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006571 | PS5-61-IV-0002A |  | B | E | 4.12: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. Applicable for all transformers. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T13:05:25.943 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006572 | PS5-61-IV-0002A |  | B | E | 4.13:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc) | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T13:06:57.170 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006573 | PS5-61-IV-0002A |  | A | E | 4.14:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T13:07:45.823 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006574 | PS5-61-IV-0002A |  | B | E | 4.15:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T13:09:47.487 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006576 | PS5-61-IV-0002B |  | B | M | 4:Quality of welding in the transformer is not upto the standard. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:21:41.363 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006577 | PS5-61-IV-0002B |  | C | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:24:10.287 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006578 | PS5-61-IV-0002B |  | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:29:51.177 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006579 | PS5-61-IV-0002B |  | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:31:24.010 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006580 | PS5-61-IV-0002B |  | B | E | 4.4:Internal wiring and cable entry inside the enclosure are poorly installed and not properly managed, unused openings are covered by rubber plugs | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:34:41.410 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006581 | PS5-61-IV-0002B |  | B | E | 4.5:The opening has been temporarily sealed using plastic tape. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:35:49.003 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006582 | PS5-61-IV-0002B |  | A | E | 4.6:Cable entry is improperly installed. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:37:58.283 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006583 | PS5-61-IV-0002B |  | A | E | 4.7:All cable entries are not properly tightened and cables are not properly sealed in cable glands.. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:39:35.727 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006584 | PS5-61-IV-0002B |  | A | E | 4.8:64. No heat-shrink sleeves are installed on the cable inside the main panel. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:51:02.470 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006585 | PS5-61-IV-0002B |  | B | E | 4.9:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:51:50.320 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006586 | PS5-61-IV-0002B |  | B | E | 4.10: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. . | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:53:31.830 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006587 | PS5-61-IV-0002B |  | B | E | 4.11:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc).. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:54:21.477 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006588 | PS5-61-IV-0002B |  | A | E | 4.12:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:55:46.333 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006590 | PS5-61-IV-0002B |  | A | E | 4.13:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:56:34.757 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006591 | PS5-61-IV-0007A |  | B | M | 4:Quality of welding in the transformer is not upto the standard. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:25:57.213 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006592 | PS5-61-IV-0007A |  | C | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:28:11.897 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006593 | PS5-61-IV-0007A |  | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:29:09.663 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006594 | PS5-61-IV-0007A |  | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:30:44.923 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006595 | PS5-61-IV-0007A |  | B | E | 4.4:Improper termination of earthing conductor | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:32:11.487 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006596 | PS5-61-IV-0007A |  | A | E | 4.5:Earthing cable not connected, poor cable management, improper stripping, and improper glanding. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:42:15.790 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006597 | PS5-61-IV-0007A |  | A | E | 4.6:Improper installation of copper bonding/earthing strap | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:43:40.663 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006598 | PS5-61-IV-0007A |  | B | E | 4.7:Unused gland plate sealed with rubber instead of stopping plug. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:44:36.830 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006599 | PS5-61-IV-0007A |  | B | E | 4.8:The opening has been temporarily sealed using plastic tape | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:46:47.453 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006600 | PS5-61-IV-0007A |  | A | E | 4.9:Cable entry at the bottom of the enclosure is improperly installed. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:47:46.997 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006601 | PS5-61-IV-0007A |  | A | M | 4.10:Oil Leakage found at the oil level gauge weld area. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:49:14.923 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006602 | PS5-61-IV-0007A |  | A | E | 4.11:All cable entries are not properly tightened and cables are not properly sealed in cable glands.. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:51:20.993 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006603 | PS5-61-IV-0007A |  | A | M | 4.12:64. No heat-shrink sleeves are installed on the cable inside the main panel. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:52:09.650 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006604 | PS5-61-IV-0007A |  | B | M | 4.13:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:53:36.467 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006605 | PS5-61-IV-0007A |  | B | E | 4.14: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. . | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:54:33.773 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006606 | PS5-61-IV-0007A |  | B | E | 4.15:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc).. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:56:18.253 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006607 | PS5-61-IV-0007A |  | A | E | 4.16:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:57:00.673 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006608 | PS5-61-IV-0007A |  | A | E | 4.17:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:58:28.123 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006609 | PS5-61-IV-0007B |  | B | M | 4:Quality of welding in the transformer is not upto the standard. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:15:28.513 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006610 | PS5-61-IV-0007B |  | C | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:17:04.393 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006611 | PS5-61-IV-0007B |  | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:18:30.613 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006612 | PS5-61-IV-0007B |  | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:20:06.177 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006613 | PS5-61-IV-0007B |  | A | M | 4.4:Temperature sensor not sealed properly | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:21:00.077 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006614 | PS5-61-IV-0007B |  | B | E | 4.5:loose bolt for 1U & 1W. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:26:24.223 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006615 | PS5-61-IV-0007B |  | A | M | 4.6:Internal wiring and cable entry inside the enclosure are poorly installed and not properly managed, unused openings are covered by rubber plugs | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:27:32.567 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006616 | PS5-61-IV-0007B |  | B | E | 4.7:Unused gland plate sealed with rubber instead of stopping plug | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:29:33.423 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006617 | PS5-61-IV-0007B |  | A | E | 4.8:Cable entry is improperly installed. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:30:19.970 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006618 | PS5-61-IV-0007B |  | A | M | 4.9:Oil Leakage found at the weld area. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:32:05.480 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006619 | PS5-61-IV-0007B |  | A | E | 4.10:All cable entries are not properly tightened and cables are not properly sealed in cable glands.. | CPP AGI | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:33:28.617 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006620 | PS5-61-IV-0007B |  | A | E | 4.11:64. No heat-shrink sleeves are installed on the cable inside the main panel. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:37:40.113 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006621 | PS5-61-IV-0007B |  | B | E | 4.12:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:38:26.853 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006622 | PS5-61-IV-0007B |  | B | E | 4.13: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. . | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:39:43.767 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006623 | PS5-61-IV-0007B |  | B | M | 4.14:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc).. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:40:23.323 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006624 | PS5-61-IV-0007B |  | A | E | 4.15:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:41:30.810 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006625 | PS5-61-IV-0007B |  | A | E | 4.16:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:42:14.747 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006626 | PS5-61-IV-0001A |  | B | M | 4:Quality of welding in the transformer is not upto the standard. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T07:50:27.033 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006627 | PS5-61-IV-0001A |  | C | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T07:52:20.300 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006628 | PS5-61-IV-0001A |  | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T07:53:11.440 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006629 | PS5-61-IV-0001A |  | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T07:54:46.970 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006630 | PS5-61-IV-0001A |  | B | M | 4.4:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T07:55:43.780 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006631 | PS5-61-IV-0001A |  | A | E | 4.5:Cable entry is improperly installed. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T07:59:48.210 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006632 | PS5-61-IV-0001A |  | B | E | 4.6:Unused gland plate sealed with rubber instead of stopping plug. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:02:47.510 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006633 | PS5-61-IV-0001A |  | B | E | 4.7:loose bolt for 1W. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:03:37.340 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006634 | PS5-61-IV-0001A |  | B | E | 4.8:Poor cable management, improper stripping and glanding. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:07:01.020 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006635 | PS5-61-IV-0001A |  | A | E | 4.9:Cable glanding not properly tightened and sealed | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:08:53.287 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006636 | PS5-61-IV-0001A |  | B | E | 4.10:Cable entry temporarily sealed using plastic tape | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:11:18.603 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006637 | PS5-61-IV-0001A |  | A | E | 4.11:All cable entries are not properly tightened and cables are not properly sealed in cable glands.. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:12:37.737 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006638 | PS5-61-IV-0001A |  | A | M | 4.12:64. No heat-shrink sleeves are installed on the cable inside the main panel. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:24:49.750 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006639 | PS5-61-IV-0001A |  | B | E | 4.13:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:25:27.220 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006640 | PS5-61-IV-0001A |  | B | E | 4.14: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. . | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:26:54.213 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006641 | PS5-61-IV-0001A |  | B | E | 4.15:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc).. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:27:49.297 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006642 | PS5-61-IV-0001A |  | A | E | 4.16:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:29:12.513 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006643 | PS5-61-IV-0001A |  | A | E | 4.17:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:30:08.660 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006653 | PS5-61-IV-0001B |  | B | M | 4:Quality of welding in the transformer is not upto the standard. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:08:14.693 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006655 | PS5-61-IV-0001B |  | C | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:09:53.167 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006656 | PS5-61-IV-0001B |  | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:10:47.477 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006657 | PS5-61-IV-0001B |  | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:12:50.333 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006658 | PS5-61-IV-0001B |  | A | M | 4.4:Oil Leakage found at the oil level gauge weld area. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:13:56.710 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006659 | PS5-61-IV-0001B |  | A | M | 4.5:Oil Leakage found at the weld area. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:16:18.023 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006660 | PS5-61-IV-0001B |  | A | M | 4.6:Oil Leakage found. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:17:06.253 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006661 | PS5-61-IV-0001B |  | A | M | 4.7:Oil Leakage found at the weld area. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:18:18.720 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006662 | PS5-61-IV-0001B |  | A | M | 4.8:Oil Leakage found at the weld area. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:19:15.140 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006663 | PS5-61-IV-0001B |  | A | E | 4.9:internal wiring and cable entry inside the enclosure are poorly installed and not properly managed; unused openings are covered with rubber plugs | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:20:45.867 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006664 | PS5-61-IV-0001B |  | B | E | 4.10:poor cable management, improper stripping, and improper glanding | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:21:47.130 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006665 | PS5-61-IV-0001B |  | A | E | 4.11:flexible conduit routing over the enclosure is improperly installed. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:24:00.727 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006666 | PS5-61-IV-0001B |  | B | E | 4.12:unused gland plate is sealed with rubber instead of a stopping plug. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:24:51.633 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006667 | PS5-61-IV-0001B |  | A | E | 4.13:cable entry at the bottom of the enclosure is improperly installed. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:26:12.610 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006668 | PS5-61-IV-0001B |  | A | E | 4.14:temperature sensor is not properly sealed. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:27:14.903 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006669 | PS5-61-IV-0001B |  | A | E | 4.15:All cable entries are not properly tightened and cables are not properly sealed in cable glands.. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:31:06.080 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006670 | PS5-61-IV-0001B |  | A | E | 4.16:64. No heat-shrink sleeves are installed on the cable inside the main panel. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:31:53.783 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006671 | PS5-61-IV-0001B |  | B | E | 4.17:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:33:13.060 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006672 | PS5-61-IV-0001B |  | B | E | 4.18: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. . | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:33:57.573 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006673 | PS5-61-IV-0001B |  | B | E | 4.19:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc).. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:35:08.877 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006674 | PS5-61-IV-0001B |  | A | E | 4.20:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:36:31.693 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006675 | PS5-61-IV-0001B |  | A | E | 4.21:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:37:19.473 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006681 | PS5-61-IK-0003-CL41 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:59:18.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-20T11:59:12.357 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T08:59:15.000
PL-006683 | PS5-61-IK-0003-CL42 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:59:32.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-20T12:17:17.127 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T08:59:29.000
PL-006685 | PS5-61-IK-0006-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:59:48.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-20T12:41:37.250 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T08:59:44.000
PL-006691 | PS5-03-SFMC-0012-CD01 (Reconnection) |  | B | E | core 5,6,7,8 as spare to be terminated to PE at PS5-03-SFMC-0012 side | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-05T06:08:27.000 | Closed |  | core 5,6,7,8 as spare to be terminated to PE at PS5-03-SFMC-0012 side | 2026-05-20T13:51:49.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-05T05:45:42.000
PL-006692 | PS5-09-ACU-0007A-CP01 |  | B | E | To be installed cable tray for cable laying at PS5-09-ACU-0007A to protecting that cable from damage | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  |  | 2026-05-20T14:04:11.000 | Silaban, Junardi | PS5 - Milestone A
PL-006693 | PS5-03-SFMC-0005-CC01 |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC01/TBA08/3/PR02/WH, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T04:34:21.000 | Closed |  | to be changed ferulle | 2026-05-20T14:10:42.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T19:50:17.000
PL-006694 | PS5-61-IK-0006-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:00:21.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-20T17:19:41.150 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:00:18.000
PL-006695 | PS5-61-IK-0006-CL03 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:00:35.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T04:37:17.950 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:00:31.000
PL-006697 | PS5-61-IK-0006-CL05 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:00:48.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T05:02:49.410 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:00:45.000
PL-006698 | PS5-03-SFMC-0005-CC01 |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC02/TBA09/3/PR02/WH, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T04:34:31.000 | Closed |  | to be changed ferulle | 2026-05-21T05:18:05.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T19:51:26.000
PL-006699 | PS5-61-IK-0006-CL06 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:01:01.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T05:22:43.313 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:00:58.000
PL-006700 | PS5-03-SFMC-0005-CC03 (Reconnection) |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC03/TBA10/4/PR02/BK, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T04:34:41.000 | Closed |  | to be changed ferulle | 2026-05-21T05:25:46.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T19:52:45.000
PL-006701 | PS5-61-IK-0006-CL07 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:01:23.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T05:30:33.757 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:01:20.000
PL-006702 | PS5-03-SFMC-0005-CC05 (Reconnection) |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC05/TBA12/1/PR01/WH ; /2/PR01/WH and /3/PR02/BK, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T04:34:50.000 | Closed |  | to be changed ferulle | 2026-05-21T05:33:57.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T19:53:23.000
PL-006703 | PS5-03-SFMC-0005-CC06 (Reconnection) |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC06/TBA13/1/PR01/WH ; to be replaced wire marker PS5-03-SFMC-0005-CC06/TBA13/2/PR01/BK, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T04:34:59.000 | Closed |  | to be changed ferulle | 2026-05-21T05:37:46.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T19:54:03.000
PL-006704 | PS5-03-SFMC-0005-CC07 (Reconnection) |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC07/TBA14/1/PR01/WH, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T04:35:10.000 | Closed |  | to be changed ferulle | 2026-05-21T05:40:03.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T19:56:47.000
PL-006705 | PS5-61-IK-0006-CL08 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:01:34.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T05:40:08.650 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:01:31.000
PL-006706 | PS5-03-SFMC-0005-CC08 (Reconnection) |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC08/TBA15/1/PR01/WH, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T04:35:20.000 | Closed |  | to be changed ferulle | 2026-05-21T05:42:54.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T20:00:30.000
PL-006707 | PS5-03-SFMC-0005-CC09 (Reconnection) |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC09/TBA16/1/PR01/WH, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T04:35:29.000 | Closed |  | to be changed ferulle | 2026-05-21T05:45:17.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T20:01:22.000
PL-006708 | PS5-03-SFMC-0005-CC18 (Reconnection) |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC18/TBA01/1/PR01/WH and /3/PR02/WH, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T08:15:13.000 | Closed |  | to be changed ferulle | 2026-05-21T05:49:07.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-04T08:11:07.000
PL-006709 | PS5-03-SFMC-0005-CC19 (Reconnection) |  | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBA03 to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T08:18:22.000 | Closed |  | to be changed ferulle | 2026-05-21T05:53:39.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-04T08:11:26.000
PL-006710 | PS5-61-IK-0006-CL09 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:01:51.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T05:54:45.987 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:01:47.000
PL-006711 | PS5-03-SFMC-0005-CC20 (Reconnection) |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC20/TBA06/1/PR01/WH, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T08:18:35.000 | Closed |  | to be changed ferulle | 2026-05-21T05:57:20.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-04T08:11:47.000
PL-006741 | PS5-61-IK-0003-CL07 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:02:21.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T07:48:39.903 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T09:02:18.000
PL-006748 | PS5-61-IK-0003-CL12 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:02:34.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T07:56:35.460 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T09:02:30.000
PL-006754 | PS5-61-IK-0003-CL08 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:03:05.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T08:04:44.260 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T09:02:59.000
PL-006755 | PS5-61-IK-0003-CL11 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:03:22.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T08:04:54.373 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T09:03:18.000
PL-006759 | PS5-61-IK-0003-CL09 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:03:34.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T08:13:57.850 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T09:03:31.000
PL-006760 | PS5-61-IK-0003-CL10 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:04:45.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T08:14:53.353 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T09:04:42.000
PL-006761 | PS5-03-SFMC-0005-CC23 (Reconnection) |  | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBA02 to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T08:19:46.000 | Closed |  | to be changed ferulle | 2026-05-21T08:22:40.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-04T08:12:13.000
PL-006762 | PS5-61-IK-0003-CL37 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:04:58.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T08:26:39.973 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T09:04:54.000
PL-006764 | PS5-61-IK-0003-CL38 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:05:11.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T08:34:45.850 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T09:05:08.000
PL-006765 | PS5-61-IK-0003-CL39 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:05:24.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T08:49:48.203 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T09:05:20.000
PL-006766 | PS5-03-SFMC-0005-CC24 (Reconnection) |  | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBA05 to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T08:20:01.000 | Closed |  | to be changed ferulle | 2026-05-21T09:10:10.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-04T08:12:41.000
PL-006767 | PS5-03-SFMC-0005-CC27 (Reconnection) |  | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBD11 to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T08:20:12.000 | Closed |  | to be changed ferulle | 2026-05-21T09:16:00.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-04T08:13:10.000
PL-006772 | PS5-03-SFMC-0005-CC32 (Reconnection) |  | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBD10 to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T04:35:41.000 | Closed |  | to be changed ferulle | 2026-05-21T10:11:02.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T20:01:55.000
PL-006776 | PS5-03-SFMC-0005-CC34 (Reconnection) |  | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBD06 to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T04:35:49.000 | Closed |  | to be changed ferulle | 2026-05-21T10:13:34.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T20:02:23.000
PL-006777 | PS5-61-IK-0003-CL40 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:05:56.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T10:13:45.370 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T09:05:53.000
PL-006780 | PS5-03-SFMC-0005-CC41 (Reconnection) |  | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBA07 to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T04:36:04.000 | Closed |  | to be changed ferulle | 2026-05-21T10:16:08.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T20:02:50.000
PL-006781 | PS5-03-SFMC-0006-CC01 (Reconnection) |  | A | I | Ferulle for PS5-03-SFMC-0006-CC01/TBD09/1/PR01/WH to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T04:36:21.000 | Closed |  | to be changed ferulle | 2026-05-21T10:17:58.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T20:03:13.000
PL-006785 | PS5-03-SFMC-0006-CC02 (Reconnection) |  | A | I | Ferulle for PS5-03-SFMC-0006-CC02/TBD10/3/PR02/WH to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T04:36:36.000 | Closed |  | to be changed ferulle | 2026-05-21T10:20:03.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T20:03:37.000
PL-006787 | PS5-61-IK-0003-CL43 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:06:08.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T10:21:14.757 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:06:05.000
PL-006790 | PS5-04-PMC-0008-CC07 (Reconnection) |  | A | I | All ferulles on PS5-04-PMC-0008-CC07/TBD15 to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-05T06:08:37.000 | Closed |  | to be changed ferulle | 2026-05-21T10:22:22.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-05T05:46:12.000
PL-006791 | PS5-04-PMC-0008-CC26 (Reconnection) |  | A | I | Core marker for PS5-04-PMC-0008-CC26/TBA12/1/PR01/WH to be installed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-05T06:08:48.000 | Closed |  | to be changed ferulle | 2026-05-21T10:24:54.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-05T05:46:31.000
PL-006792 | PS5-04-PMC-0008-CC30 (Reconnection) |  | A | I | Core marker for PS5-04-PMC-0008-CC30/TBD23/4/PR01/BK to be installed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-09T12:10:11.000 | Closed |  |  | 2026-05-21T10:28:57.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-08T11:06:20.000
PL-006793 | PS5-61-IK-0003-CL45 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:06:46.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T10:29:14.950 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:06:42.000
PL-006794 | PS5-04-PMC-0008-CC39 (Reconnection) |  | B | I | Terminal Blok Name TBA16/04-PMC-0008-CC39 to be installed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  |  | 2026-05-21T10:32:31.000 | Silaban, Junardi | PS5 - Milestone A
PL-006795 | PS5-04-PMC-0008-CC40 (Reconnection) |  | A | I | All ferrules on PS5-04-PMC-0008-CC40/TBD25 to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-05T06:09:09.000 | Closed |  | to be changed ferulle | 2026-05-21T10:36:07.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-05T05:39:22.000
PL-006796 | PS5-04-PMC-0008-CC41 (Reconnection) |  | A | I | Ferulle for PS5-04-PMC-0008-CC41/TBD08/1/PR01/WH to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-05T06:09:20.000 | Closed |  | to be changed ferulle | 2026-05-21T10:42:34.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-05T05:39:48.000
PL-006797 | PS5-61-IK-0003-CL46 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:06:58.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T10:49:59.877 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:06:55.000
PL-006798 | PS5-61-IK-0003-CL47 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:07:16.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T11:00:51.480 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:07:12.000
PL-006799 | PS5-61-IK-0003-CL48 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:07:29.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T11:08:47.883 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:07:25.000
PL-006801 | PS5-61-IK-0003-CL50 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:08:07.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T11:30:20.457 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:08:00.000
PL-006809 | PS5-61-IK-0003-CL51 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:08:21.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T12:44:23.840 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:08:17.000
PL-006810 | PS5-61-IK-0001-CL01 |  | B | E | Cable dressing not completed at both ends | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Completed |  | Complete cable dressing at both ends. Ensure proper cable ties, cleats, and bending radius are maintained as per project specification | 2026-05-21T12:49:49.783 | Gawad, Mohamed | PS5 - Milestone A | 2026-05-21T14:18:20.000
PL-006811 | PS5-61-IK-0003-CL52 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:08:52.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T12:55:41.280 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:08:47.000
PL-006812 | PS5-61-IK-0001-CL01 |  | B | E | Trench backfilled at Transformer side without installation of Red Protection Tiles and Warning Tape over LV Power Cable | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Completed |  | Excavate trench at Transformer side, install Red Protection Tiles and Warning Tape at correct depth above cable as per project civil/electrical specification, then re-backfill and compact properly. | 2026-05-21T13:15:09.640 | Gawad, Mohamed | PS5 - Milestone A | 2026-05-21T14:20:55.000
PL-006813 | PS5-61-IK-0003-CL53 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:09:06.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T13:17:14.973 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:09:03.000
PL-006832 | PS5-04-PMC-0008-CC12 (Reconnection) |  | A | I | All ferulles on PS5-04-PMC-0008-CC12/TBD18 to be changed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-05T06:09:29.000 | Closed |  | to be changed ferulle | 2026-05-21T14:20:28.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-05T05:48:06.000
PL-006834 | PS5-04-PMC-0008-CC25 (Reconnection) |  | A | I | All ferulles on PS5-04-PMC-0008-CC25/TBA11 to be changed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-04T04:37:13.000 | Closed |  | to be changed ferulle | 2026-05-21T14:23:03.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T20:09:54.000
PL-006861 | PS5-04-PMC-0008-CC24 (Reconnection) |  | B | I | Ferulle for PS5-04-PMC-0008-CC24/TBA07/4/PR02/BK to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-05T06:09:39.000 | Closed |  | to be changed ferulle | 2026-05-22T04:38:58.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-05T05:40:20.000
PL-006862 | PS5-61-IK-0003-CL54 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:09:37.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T04:39:14.563 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:09:33.000
PL-006863 | PS5-04-PMC-0008-CC20 (Reconnection) |  | A | I | Ferulle for PS5-04-PMC-0008-CC20/TBD07/1/PR01/WH to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-05T06:09:51.000 | Closed |  | to be changed ferulle | 2026-05-22T04:41:22.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-05T05:40:53.000
PL-006864 | PS5-04-PMC-0008-CC28 (Reconnection) |  | A | I | Ferulle for PS5-04-PMC-0008-CC28/TBD21/1/PR01/WH and PS5-04-PMC-0008-CC28/TBD21/2/PR01/BK to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-05T06:10:05.000 | Closed |  | to be changed ferulle | 2026-05-22T04:44:00.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-05T05:41:16.000
PL-006865 | PS5-04-PMC-0008-CC31 (Reconnection) |  | A | I | Ferulle for PS5-04-PMC-0008-CC31/TBD24/1/PR01/WH and PS5-04-PMC-0008-CC31/TBD24/2/PR01/BK to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-04T04:37:25.000 | Closed |  | to be changed ferulle | 2026-05-22T04:47:22.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T20:04:27.000
PL-006866 | PS5-04-PMC-0008-CC17 (Reconnection) |  | A | I | Ferulle for PS5-04-PMC-0008-CC17/TBA09/1/PR01/WH and PS5-04-PMC-0008-CC17/TBA09/2/PR01/BK to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-04T04:37:39.000 | Closed |  | to be changed ferulle | 2026-05-22T04:49:32.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T20:05:16.000
PL-006867 | PS5-04-PMC-0008-CC13 (Reconnection) |  | B | I | Ferulle for PS5-04-PMC-0008-CC13/TBD19/4/PR02/BK to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-04T04:37:48.000 | Closed |  | to be changed ferulle | 2026-05-22T04:52:36.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T20:05:47.000
PL-006868 | PS5-04-PMC-0008-CC11 (Reconnection) |  | B | I | Ferulle for PS5-04-PMC-0008-CC11/TBD17/3/PR02/WH and PS5-04-PMC-0008-CC11/TBD17/4/PR02/BK to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-04T04:37:58.000 | Closed |  | to be changed ferulle | 2026-05-22T04:55:16.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T20:06:25.000
PL-006869 | PS5-04-PMC-0008-CC10 (Reconnection) |  | A | I | Ferulle for PS5-04-PMC-0008-CC10/TBD16/1/PR01/WH to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-04T04:38:10.000 | Closed |  | to be changed ferulle | 2026-05-22T04:57:15.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T20:06:59.000
PL-006870 | PS5-04-PMC-0008-CC09 (Reconnection) |  | A | I | Ferulle for PS5-04-PMC-0008-CC09/TBA02/1/PR01/WH to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-04T04:38:28.000 | Closed |  | to be changed ferulle | 2026-05-22T04:59:20.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T20:07:34.000
PL-006871 | PS5-04-PMC-0008-CC47 (Reconnection) |  | A | I | Ferulle for PS5-04-PMC-0008-CC47/TBA18/1/PR01/WH and PS5-04-PMC-0008-CC47/TBA18/4/PR02/BK to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-04T04:38:38.000 | Closed |  | to be changed ferulle | 2026-05-22T05:03:05.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T20:08:09.000
PL-006872 | PS5-09-PDT-0004-CJ01 (Reconnection) |  | B | I | Missing terminal block name XAI inside Panel PS5-09-LB-0001, to be provided | EITS | PS5-09-05 - HVAC for EITS Building | 2026-09-02T13:32:07.000 | Closed |  |  | 2026-05-22T05:06:13.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-16T18:30:49.000
PL-006873 | PS5-04-PMC-0002-CS03 (Reconnection) |  | A | E | Wrong core marker at Panel PS5-04-PMC-0002 side, to be replaced. PS5-04-PMC-0002-CS03,,, instead PS5-04-PMC-002-CS03,,, | EITS | PS5-04-04 - 33kV PCS System | 2026-08-05T06:10:21.000 | Closed |  | Core marker to be replaced | 2026-05-22T05:19:07.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-05T05:49:25.000
PL-006874 | PS5-04-PMC-0008-CC48 (Reconnection) |  | B | I | to be changed terminal number on the drawing No. TZ-MID-68-SSF1-160014 page 288 of 952 due to actual number inside of panel is 1,2,3,4 | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T05:28:21.000 | Silaban, Junardi | PS5 - Milestone A
PL-006875 | PS5-61-IJ-0011-CD01 (Reconnection) |  | B | E | Terminal Blok Name XDI13 at Panel PS5-61-IE-0002 is not available, to be provided | EITS | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  | Yes | 2026-05-22T05:38:33.000 | Silaban, Junardi | PS5 - Milestone G
PL-006876 | PS5-04-PMC-0008-CC35 (Reconnection) |  | A | I | to provided core marker for PS5-04-PMC-0008-CC35/TBA10/7/PR04/WH at PS5-04-PMC-0008 side | EITS | PS5-04-04 - 33kV PCS System | 2026-08-04T04:38:49.000 | Closed |  | to be changed ferulle | 2026-05-22T05:42:12.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-03T20:10:30.000
PL-006877 | PS5-03-SFMC-0005-CC33 (Reconnection) |  | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBD08 to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T08:20:32.000 | Closed |  | to be changed ferulle | 2026-05-22T05:45:03.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-04T08:13:37.000
PL-006878 | PS5-04-PMC-0008-CC57 (Reconnection) |  | B | I | Ferulle for PS5-04-PMC-0008-CC57/TBD32/3/PR02/WH and PS5-04-PMC-0008-CC57/TBD32/4/PR02/BK to be changed, wire exposed | EITS | PS5-71-01 - CFO Storage Tank Feed Heater | 2026-08-05T06:10:41.000 | Closed |  | to be changed ferulle | 2026-05-22T05:50:17.000 | Silaban, Junardi | PS5 - Milestone H | 2026-08-05T05:41:43.000
PL-006879 | PS5-06-GU-0001-CC03 (Reconnection) |  | A | I | Ferulle for PS5-06-GU-0001-CC03/TBA01/1/PR01/WH and PS5-06-GU-0001-CC03/TBA01/1/PR01/BK to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T08:20:42.000 | Closed |  | to be changed ferulle | 2026-05-22T05:52:40.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-04T08:14:01.000
PL-006880 | PS5-06-GU-0001-CC04 (Reconnection) |  | A | I | All ferulles at PS5-03-SFMC-0003/TBA01 to be changed,wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-04T08:20:51.000 | Closed |  | to be changed ferulle | 2026-05-22T05:55:17.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-04T08:14:30.000
PL-006881 | PS5-61-IJ-0001-CC01 (Reconnection) |  | A | I | All ferulles at PS5-04-PMC-0006/TBA05 to be changed, wire exposed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) | 2026-08-05T06:10:50.000 | Closed |  | Ferulle to be changed | 2026-05-22T05:57:49.000 | Silaban, Junardi | PS5 - Milestone D | 2026-08-05T05:55:25.000
PL-006882 | PS5-61-IJ-0001-CC02 (Reconnection) |  | A | I | All ferulles at PS5-04-PMC-0006/TBA06 to be changed,wire exposed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) | 2026-08-05T06:11:00.000 | Closed |  | Ferulle to be changed | 2026-05-22T06:00:14.000 | Silaban, Junardi | PS5 - Milestone D | 2026-08-05T05:55:52.000
PL-006883 | PS5-61-IJ-0001-CC03 (Reconnection) |  | A | I | All ferulles at PS5-04-PMC-0006/TBA07 to be changed, wire exposed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) | 2026-08-05T06:11:14.000 | Closed |  | Ferulle to be changed | 2026-05-22T06:02:06.000 | Silaban, Junardi | PS5 - Milestone D | 2026-08-05T05:56:20.000
PL-006884 | PS5-61-IK-0001-CC15 (Reconnection) |  | A | I | to be changed ferulle for PS5-61-IK-0001-CC15/TBA02/1/PR01/WH; /3/PR02/WH and /5/PR03/WH, wire exposed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-09T12:10:27.000 | Closed |  | Yes | 2026-05-22T06:04:28.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-08T11:07:03.000
PL-006885 | PS5-61-IK-0001-CC40 (Reconnection) |  | A | I | to be changed ferulle for PS5-61-0001-CC40/TBD01/1/PR01/WH and PS5-61-0001-CC40/TBD01/8/PR04/BK, wire exposed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-05T06:11:25.000 | Closed |  | Ferulle to be changed | 2026-05-22T06:06:13.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-05T05:56:45.000
PL-006886 | PS5-61-IK-0001-CC43 (Reconnection) |  | A | I | to be changed ferulle for PS5-61-0001-CC43/TBD03/1/PR01/WH ; /2/PR01/BK and PS5-61-0001-CC43/TBD02/3/PR02/WH; /4/PR02/BK , wire exposed | EITS | PS5-04-04 - 33kV PCS System | 2026-08-05T06:11:46.000 | Closed |  | Ferulle to be changed | 2026-05-22T06:07:44.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-05T05:57:08.000
PL-006887 | PS5-03-SFMC-0006-CC57 (Reconnection) |  | A | I | Ferulle for PS5-03-SFMC-0006-CC57/TBD07/1/PR01/WH and PS5-03-SFMC-0006-CC57/TBD07/4/PR02/BK to be changed, wire exposed | EITS | PS5-71-01 - CFO Storage Tank Feed Heater | 2026-08-05T06:11:56.000 | Closed |  | Ferulle to be changed | 2026-05-22T06:09:51.000 | Silaban, Junardi | PS5 - Milestone H | 2026-08-05T05:57:33.000
PL-006888 | PS5-03-SFMC-0006-CC45 (Reconnection) |  | A | I | Ferulle for PS5-03-SFMC-0006-CC45/TBD02/1/PR01/WH and PS5-03-SFMC-0006-CC45/TBD02/3/PR02/WH to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-05T06:12:10.000 | Closed |  | Ferulle to be changed | 2026-05-22T06:11:54.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-05T05:57:56.000
PL-006889 | PS5-03-SFMC-0006-CC38 (Reconnection) |  | B | I | Ferulle for PS5-03-SFMC-0006-CC02/TBA12/4/PR02/BK to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System | 2026-08-05T06:12:18.000 | Closed |  | Ferulle to be changed | 2026-05-22T06:13:19.000 | Silaban, Junardi | PS5 - Milestone A | 2026-08-05T05:58:20.000
PL-006894 | PS5-05-BE-0001-CG01 |  | A | E | Earth boss and Termination missing | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-08-15T13:01:44.000 | Closed |  | Install all earth bosses as per the drawing and proceed with the termination of the earthing cables at the bosses and equipment | 2026-05-22T08:39:27.993 | Gawad, Mohamed | PS5 - Milestone C | 2026-08-15T12:38:35.000
PL-006895 | PS5-05-BE-0001-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:10:07.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T10:18:15.737 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:10:03.000
PL-006896 | PS5-05-BE-0001-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:10:29.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T10:31:11.680 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:10:26.000
PL-006897 | PS5-05-BE-0001-CL03 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:10:42.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T10:39:21.130 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:10:39.000
PL-006898 | PS5-05-BE-0001-CL04 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:10:56.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T10:45:15.300 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:10:53.000
PL-006899 | PS5-05-BE-0001-CL05 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:11:10.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-22T10:52:00.140 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:11:06.000
PL-006900 | PS5-05-BE-0001-CL06 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:11:57.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T11:00:11.213 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:11:54.000
PL-006901 | PS5-61-IK-0003-CL56 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:12:10.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T11:05:50.120 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:12:06.000
PL-006903 | PS5-61-IK-0003-CL55 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:12:22.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T11:13:18.980 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:12:18.000
PL-006904 | PS5-05-BE-0001-CL08 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:12:36.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T11:16:02.703 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:12:33.000
PL-006905 | PS5-05-BE-0001-CL09 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:12:48.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-22T11:23:07.127 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:12:45.000
PL-006906 | PS5-05-BE-0001-CL11 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:13:02.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T11:24:30.343 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:12:58.000
PL-006907 | PS5-05-BE-0001-CL10 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:13:17.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T11:30:00.780 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:13:14.000
PL-006926 | PS5-87-IRF-0001-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-53-01 - Utility Water / Storage Tank | 2026-06-14T09:14:15.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T08:26:16.377 | Gawad, Mohamed | PS5 - Milestone C | 2026-06-14T09:14:12.000
PL-006927 | PS5-74-LB-5101-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-74-02 - N2 Generation Skid (UCP) | 2026-06-14T09:14:28.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T08:36:06.897 | Gawad, Mohamed | PS5 - Milestone F | 2026-06-14T09:14:24.000
PL-006928 | PS5-71-XV-0092-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank | 2026-06-14T09:14:41.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T08:44:09.940 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T09:14:38.000
PL-006929 | PS5-28-SDV-0053B-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-28-14 - Seal Oil Drain Drum & Pump B | 2026-06-14T09:14:55.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-23T09:03:17.360 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:14:52.000
PL-006930 | PS5-28-SDV-0053C-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-28-15 - Seal Oil Drain Drum & Pump C | 2026-06-14T09:18:12.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:02:48.387 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:18:08.000
PL-006931 | PS5-71-XV-0090-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-12 - CFO Service Tank | 2026-06-14T09:18:32.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:04:46.427 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:18:29.000
PL-006932 | PS5-71-XV-0089-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-04 - CFO Storage Tank | 2026-06-14T09:18:49.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:10:23.600 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:18:45.000
PL-006933 | PS5-71-SDV-0039-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-12 - CFO Service Tank | 2026-06-14T09:19:04.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:18:39.977 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:18:59.000
PL-006934 | PS5-71-SDV-0001-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank | 2026-06-14T09:19:16.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:26:37.613 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T09:19:13.000
PL-006939 | PS5-62-IE-0002-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-62-02 - Lighting Control Panel - PS5-62-IE-0002 | 2026-06-14T09:19:29.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:40:22.937 | Gawad, Mohamed | PS5 - Milestone G | 2026-06-14T09:19:25.000
PL-006940 | PS5-61-IV-0007B-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:20:05.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:40:24.420 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:20:02.000
PL-006943 | PS5-71-FCV-0019-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B | 2026-06-14T09:20:16.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:47:07.603 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T09:20:13.000
PL-006947 | PS5-61-IV-0007A-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:20:28.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:57:40.177 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:20:25.000
PL-006948 | PS5-71-FCV-0020-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-05 - CFO Transfer Pump A/B | 2026-06-14T09:20:40.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:59:33.527 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:20:36.000
PL-006949 | PS5-71-HE-2200-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-71-12 - CFO Service Tank | 2026-06-14T09:20:52.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T11:18:39.080 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:20:49.000
PL-006950 | PS5-71-LCV-4101-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-04 - CFO Storage Tank | 2026-06-14T09:21:29.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T11:23:17.423 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:21:25.000
PL-006951 | PS5-61-BI-0001-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-60-01 - Power Generation Package A | 2026-06-14T09:21:54.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T11:31:52.130 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T09:21:50.000
PL-006952 | PS5-61-BI-0002-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-60-04 - Power Generation Package B | 2026-06-14T09:22:06.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T11:35:58.607 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T09:22:02.000
PL-006953 | PS5-61-IK-0006-CL34 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:22:18.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T11:48:47.420 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:22:14.000
PL-006954 | PS5-71-HE-2200 |  | C | M | 4:During the inspection, the tag number and nameplate were not found. | EPS VENDOR | PS5-71-12 - CFO Service Tank |  | Originated |  |  | 2026-05-23T12:19:09.930 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-006955 | PS5-71-HE-2200 |  | C | M | 4.1:Two gaskets arrived without a packing list. | EPS VENDOR | PS5-71-12 - CFO Service Tank |  | Originated |  |  | 2026-05-23T12:19:57.060 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-006956 | PS5-71-HE-2200 |  | B | M | 4.2:The duplex RTD 3-wire was found improperly aligned and extending outside the heater bundle | EPS VENDOR | PS5-71-12 - CFO Service Tank |  | Originated |  |  | 2026-05-23T12:21:06.913 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-006957 | PS5-71-HE-2300 |  | C | M | 4:During the inspection, the tag number and nameplate were not found. | EPS VENDOR | PS5-71-04 - CFO Storage Tank |  | Originated |  |  | 2026-05-23T12:22:57.200 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-006958 | PS5-71-HE-2300 |  | C | M | 4.1:Two gaskets arrived without a packing list. | EPS VENDOR | PS5-71-04 - CFO Storage Tank |  | Originated |  |  | 2026-05-23T12:23:53.917 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-006959 | PS5-71-HE-2300 |  | B | M | 4.2:The duplex RTD 3-wire was found improperly aligned and extending outside the heater bundle | EPS VENDOR | PS5-71-04 - CFO Storage Tank |  | Originated |  |  | 2026-05-23T12:24:44.540 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-006960 | PS5-61-IK-0006-CL33 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:23:13.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T12:40:36.300 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:23:09.000
PL-006961 | PS5-61-IK-0006-CL28 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:23:28.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T12:51:58.850 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:23:24.000
PL-006962 | PS5-61-IK-0006-CL27 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:23:41.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T13:04:37.107 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:23:37.000
PL-006963 | PS5-61-IK-0006-CL26 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:23:52.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T13:11:22.007 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:23:49.000
PL-006964 | PS5-61-BI-0007-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-60-19 - Power Generation Package G | 2026-06-14T09:24:07.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T13:18:43.630 | Gawad, Mohamed | PS5 - Milestone E | 2026-06-14T09:24:03.000
PL-006967 | PS5-28-HE-2100-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-28-03 - Closed Drain Drum and Pump 01 | 2026-06-14T09:24:19.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T05:44:25.933 | Gawad, Mohamed | PS5 - Milestone G | 2026-06-14T09:24:16.000
PL-006968 | PS5-28-BE-0002B-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-28-17 - Reinjection Pump | 2026-06-14T09:24:31.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T05:49:29.183 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:24:28.000
PL-006969 | PS5-28-BE-0002A-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-28-17 - Reinjection Pump | 2026-06-14T09:24:44.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T05:58:48.983 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:24:40.000
PL-006970 | PS5-25-MOV-0008-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-07 - Export Pipeline Pig Launcher | 2026-06-14T09:26:45.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T06:15:33.847 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:26:40.000
PL-006971 | PS5-25-MOV-0025-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-01 - Export Pipeline Pig Receiver | 2026-06-14T09:26:58.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T06:29:11.673 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:26:54.000
PL-006972 | PS5-25-MOV-0026-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-01 - Export Pipeline Pig Receiver | 2026-06-14T09:27:11.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T06:36:27.230 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:27:07.000
PL-006973 | PS5-25-SDV-0046-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-05 - Crude Oil Export Pumps Bypass | 2026-06-14T09:27:32.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T07:15:26.360 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:27:25.000
PL-006974 | PS5-25-DM-3100A-CG01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-02 - Crude Oil Export Pump A | 2026-06-14T09:27:48.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T07:41:23.083 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:27:44.000
PL-006975 | PS5-25-DM-3100A-CG02 |  | A | E | Cable to be connected | CPP AGI | PS5-25-02 - Crude Oil Export Pump A | 2026-06-14T09:28:00.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T07:48:34.160 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:27:56.000
PL-006976 | PS5-01-BE-0001-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100) | 2026-06-14T09:28:12.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T07:59:41.013 | Gawad, Mohamed | PS5 - Milestone F | 2026-06-14T09:28:08.000
PL-007094 | PS5-01-FCV-0003A-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-01-02 - Fire Water Pump A | 2026-06-14T09:28:39.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-26T10:23:56.360 | Anwar, Zeeshan | PS5 - Milestone C | 2026-06-14T09:28:35.000
PL-007095 | PS5-61-IU-3100A-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | : Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T10:25:54.270 | Gawad, Mohamed | PS5 - Milestone H
PL-007096 | PS5-61-IU-3100C-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:19:01.280 | Gawad, Mohamed | PS5 - Milestone H
PL-007097 | PS5-61-IU-3100B-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:21:24.180 | Gawad, Mohamed | PS5 - Milestone H
PL-007099 | PS5-61-IDH-3100A-CH01 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:23:38.863 | Gawad, Mohamed | PS5 - Milestone H
PL-007100 | PS5-61-IDH-3100A-CH02 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:25:34.943 | Gawad, Mohamed | PS5 - Milestone H
PL-007101 | PS5-61-IDH-3100A-CH03 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:27:53.930 | Gawad, Mohamed | PS5 - Milestone H
PL-007102 | PS5-61-IDH-3100A-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:29:35.067 | Gawad, Mohamed | PS5 - Milestone H
PL-007103 | PS5-61-IDH-3100A-CH05 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:31:19.660 | Gawad, Mohamed | PS5 - Milestone H
PL-007104 | PS5-61-IDH-3100A-CH06 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:32:36.020 | Gawad, Mohamed | PS5 - Milestone H
PL-007105 | PS5-61-IDH-3100A-CH07 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:34:19.290 | Gawad, Mohamed | PS5 - Milestone H
PL-007106 | PS5-61-IDH-3100A-CH08 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:37:40.647 | Gawad, Mohamed | PS5 - Milestone H
PL-007107 | PS5-61-IDH-3100A-CH09 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:39:16.740 | Gawad, Mohamed | PS5 - Milestone H
PL-007108 | PS5-61-IDH-3100A-CH10 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:40:46.563 | Gawad, Mohamed | PS5 - Milestone H
PL-007109 | PS5-61-IDH-3100A-CH11 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:42:30.157 | Gawad, Mohamed | PS5 - Milestone H
PL-007110 | PS5-61-IDH-3100A-CH12 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:44:07.907 | Gawad, Mohamed | PS5 - Milestone H
PL-007111 | PS5-61-IDH-3100B-CH01 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:45:31.667 | Gawad, Mohamed | PS5 - Milestone H
PL-007112 | PS5-61-IDH-3100B-CH02 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:50:08.377 | Gawad, Mohamed | PS5 - Milestone H
PL-007113 | PS5-61-IDH-3100B-CH03 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:53:20.510 | Gawad, Mohamed | PS5 - Milestone H
PL-007114 | PS5-61-IDH-3100B-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:54:58.720 | Gawad, Mohamed | PS5 - Milestone H
PL-007115 | PS5-61-IDH-3100B-CH05 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:56:32.710 | Gawad, Mohamed | PS5 - Milestone H
PL-007117 | PS5-61-IDH-3100B-CH07 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:59:26.417 | Gawad, Mohamed | PS5 - Milestone H
PL-007118 | PS5-61-IDH-3100B-CH08 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T12:02:02.193 | Gawad, Mohamed | PS5 - Milestone H
PL-007119 | PS5-61-IDH-3100B-CH09 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T12:03:33.743 | Gawad, Mohamed | PS5 - Milestone H
PL-007120 | PS5-61-IDH-3100B-CH10 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T12:05:29.840 | Gawad, Mohamed | PS5 - Milestone H
PL-007121 | PS5-61-IDH-3100B-CH11 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T12:06:54.703 | Gawad, Mohamed | PS5 - Milestone H
PL-007122 | PS5-61-IDH-3100B-CH12 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T12:08:40.483 | Gawad, Mohamed | PS5 - Milestone H
PL-007173 | PS5-61-IK-0006-CL25 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:29:05.000 | Closed |  | Cable to be connected | 2026-05-28T08:12:17.430 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:29:02.000
PL-007176 | PS5-61-BI-0003-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-60-07 - Power Generation Package C | 2026-06-14T09:29:20.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-28T08:48:17.607 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:29:16.000
PL-007177 | PS5-61-BI-0004-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-60-10 - Power Generation Package D | 2026-06-14T09:29:43.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-28T09:13:51.000 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:29:39.000
PL-007178 | PS5-61-BI-0005-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-60-13 - Power Generation Package E | 2026-06-14T09:29:56.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-28T09:28:03.787 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:29:53.000
PL-007179 | PS5-61-BI-0006-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-60-16 - Power Generation Package F | 2026-06-14T09:30:13.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-28T09:40:06.420 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:30:07.000
PL-007180 | PS5-61-IK-0006-CL23 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:30:43.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-28T10:42:01.260 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:30:40.000
PL-007181 | PS5-61-IK-0006-CL24 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:30:57.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-28T10:52:21.093 | Gawad, Mohamed | PS5 - Milestone D | 2026-06-14T09:30:54.000
PL-007192 | PS5-06-GB-0003-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:31:28.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:03:05.363 | Anwar, Zeeshan | PS5 - Milestone B | 2026-06-14T09:31:24.000
PL-007193 | PS5-06-GB-0003-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:31:39.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:13:07.740 | Anwar, Zeeshan | PS5 - Milestone B | 2026-06-14T09:31:36.000
PL-007194 | PS5-74-LB-5101-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-74-02 - N2 Generation Skid (UCP) | 2026-06-14T09:31:52.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:16:14.453 | Gawad, Mohamed | PS5 - Milestone F | 2026-06-14T09:31:49.000
PL-007195 | PS5-06-GB-0003-CL03 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:32:06.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:17:33.417 | Anwar, Zeeshan | PS5 - Milestone B | 2026-06-14T09:32:02.000
PL-007196 | PS5-06-GB-0003-CL04 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:32:18.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:23:35.477 | Anwar, Zeeshan | PS5 - Milestone B | 2026-06-14T09:32:15.000
PL-007197 | PS5-06-GB-0003-CL05 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:32:31.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:28:34.650 | Anwar, Zeeshan | PS5 - Milestone B | 2026-06-14T09:32:27.000
PL-007198 | PS5-06-GB-0003-CL06 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:32:45.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:33:54.523 | Anwar, Zeeshan | PS5 - Milestone B | 2026-06-14T09:32:41.000
PL-007199 | PS5-06-IG-0004B-CL04 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:33:02.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:36:26.817 | Gawad, Mohamed | PS5 - Milestone B | 2026-06-14T09:32:58.000
PL-007200 | PS5-06-GU-0003A-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:33:32.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:39:03.543 | Anwar, Zeeshan | PS5 - Milestone B | 2026-06-14T09:33:29.000
PL-007201 | PS5-06-GU-0003B-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:33:43.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:45:35.833 | Anwar, Zeeshan | PS5 - Milestone B | 2026-06-14T09:33:40.000
PL-007202 | PS5-06-GU-0003C-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:33:55.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:52:59.927 | Anwar, Zeeshan | PS5 - Milestone B | 2026-06-14T09:33:52.000
PL-007203 | PS5-06-IG-0004A-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:34:07.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:55:57.857 | Anwar, Zeeshan | PS5 - Milestone B | 2026-06-14T09:34:04.000
PL-007204 | PS5-06-IG-0004A-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:34:20.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T06:02:18.770 | Anwar, Zeeshan | PS5 - Milestone B | 2026-06-14T09:34:16.000
PL-007205 | PS5-06-IG-0004A-CL03 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:34:32.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T06:07:48.803 | Anwar, Zeeshan | PS5 - Milestone B | 2026-06-14T09:34:28.000
PL-007206 | PS5-06-IG-0004A-CL04 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:34:44.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T07:01:35.143 | Anwar, Zeeshan | PS5 - Milestone B | 2026-06-14T09:34:40.000
PL-007207 | PS5-06-IG-0004B-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:34:57.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T07:23:52.217 | Anwar, Zeeshan | PS5 - Milestone B | 2026-06-14T09:34:54.000
PL-007211 | PS5-06-IG-0004B-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:35:29.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T10:58:14.283 | Anwar, Zeeshan | PS5 - Milestone B | 2026-06-14T09:35:25.000
PL-007212 | PS5-06-IG-0004B-CL03 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:35:46.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T11:03:58.807 | Anwar, Zeeshan | PS5 - Milestone B | 2026-06-14T09:35:42.000
PL-007231 | PS5-60-TCV-0001C |  | C | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-05-30T06:08:03.527 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T08:47:33.000
PL-007232 | PS5-60-TCV-0001C |  | C | M | 10.1: TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | TOUCH UP PAINTING TO BE DONE | 2026-05-30T06:09:27.880 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-007233 | PS5-60-TCV-0001E |  | C | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-05-30T06:12:31.480 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T08:47:59.000
PL-007234 | PS5-60-TCV-0001E |  | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | TOUCH UP PAINTING TO BE DONE | 2026-05-30T06:13:30.947 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-007305 | PS5-61-IDH-3100C-CH01 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T14:21:42.287 | Gawad, Mohamed | PS5 - Milestone H
PL-007306 | PS5-61-IDH-3100C-CH02 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T14:26:04.707 | Gawad, Mohamed | PS5 - Milestone H
PL-007307 | PS5-61-IDH-3100C-CH03 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T14:27:53.310 | Gawad, Mohamed | PS5 - Milestone H
PL-007308 | PS5-61-IDH-3100C-CH04 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T14:29:29.227 | Gawad, Mohamed | PS5 - Milestone H
PL-007309 | PS5-61-IDH-3100C-CH05 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T14:30:57.493 | Gawad, Mohamed | PS5 - Milestone H
PL-007310 | PS5-61-IDH-3100C-CH06 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T14:32:31.760 | Gawad, Mohamed | PS5 - Milestone H
PL-007311 | PS5-61-IDH-3100C-CH07 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T15:40:13.450 | Gawad, Mohamed | PS5 - Milestone H
PL-007312 | PS5-61-IDH-3100C-CH08 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T15:55:48.937 | Gawad, Mohamed | PS5 - Milestone H
PL-007313 | PS5-61-IDH-3100C-CH09 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T15:57:22.227 | Gawad, Mohamed | PS5 - Milestone H
PL-007314 | PS5-61-IDH-3100C-CH10 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T15:58:49.440 | Gawad, Mohamed | PS5 - Milestone H
PL-007315 | PS5-61-IDH-3100C-CH11 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T16:01:03.407 | Gawad, Mohamed | PS5 - Milestone H
PL-007316 | PS5-61-IDH-3100C-CH12 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T16:03:27.373 | Gawad, Mohamed | PS5 - Milestone H
PL-007317 | PS5-61-IV-0002A-CH03 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-08-26T08:07:04.000 | Closed |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T16:04:59.563 | Gawad, Mohamed | PS5 - Milestone B | 2026-08-15T10:56:49.000
PL-007318 | PS5-61-IV-0002B-CH01 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-08-26T08:07:44.000 | Closed |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T16:07:23.277 | Gawad, Mohamed | PS5 - Milestone B | 2026-08-12T08:50:48.000
PL-007319 | PS5-61-IV-0002B-CH02 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-08-26T08:08:00.000 | Closed |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T16:08:50.690 | Gawad, Mohamed | PS5 - Milestone B | 2026-08-12T08:51:30.000
PL-007333 | PS5-71-FCV-0018-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-13 - CFO Service Pump A/B | 2026-06-14T09:36:13.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-06-01T09:22:58.710 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:36:09.000
PL-007334 | PS5-71-HE-2300-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-71-04 - CFO Storage Tank | 2026-06-14T09:36:28.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-06-01T09:31:56.200 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:36:24.000
PL-007540 | PS5-82-UZ-8100 |  | A | M | 4:Nozzle flange distoration was observed on the Aerobic tank PS5-82-TR-4800 during inspection | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-03T07:18:26.453 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-007709 | PS5-25-XV-0053-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-05 - Crude Oil Export Pumps Bypass | 2026-06-14T09:37:48.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-06-04T06:26:41.367 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:37:44.000
PL-007710 | PS5-60-MOV-0005-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-12 - CFO Service Tank | 2026-06-14T09:38:02.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-06-04T06:31:04.173 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:37:58.000
PL-007711 | PS5-60-MOV-0006-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-12 - CFO Service Tank | 2026-06-14T09:38:15.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-06-04T06:34:25.537 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:38:11.000
PL-007713 | PS5-60-MOV-0011-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-12 - CFO Service Tank | 2026-06-14T09:38:30.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-06-04T06:40:19.920 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:38:26.000
PL-007715 | PS5-60-MOV-0012-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-12 - CFO Service Tank | 2026-06-14T09:38:46.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-06-04T06:44:45.967 | Gawad, Mohamed | PS5 - Milestone H | 2026-06-14T09:38:42.000
PL-007805 | PS5-75-UI-6100 |  | B | M | 4:The welding quality on the skid is not up to the required standard, and cracks were observed in the weld areas throughout the skid. (All welded areas). | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:11:00.470 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007806 | PS5-75-UI-6100 |  | B | M | 4.1:During inspection, the U-clamp was found missing | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:12:45.880 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007807 | PS5-75-UI-6100 |  | B | M | 4.2:During inspection, the U-clamp was found to be improperly installed | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:13:50.493 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007808 | PS5-75-UI-6100 |  | B | M | 4.3:During the inspection, oil leakage was observed from the diaphragm pump. (PS5-75-PB-3200A). | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  | To be monitored during precom stage | 2026-06-05T08:15:04.780 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007809 | PS5-75-UI-6100 |  | B | M | 4.4:During the inspection, oil leakage was observed from the diaphragm pump (PS5-75-PB-3200B). | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  | To be monitored during precom activities | 2026-06-05T08:16:24.617 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007810 | PS5-75-UI-6100 |  | C | M | 4.5:As per the packing list, Canopy Tag No. 3300A & 3300B but received Tag No. 3200A & 3200B. | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:17:08.580 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007811 | PS5-75-UI-6100 |  | B | M | 4.6:During inspection After welding the pad plate, the vent holes were required to be sealed. but no one vent hole was didnt sealed,. | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:18:15.537 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007812 | PS5-75-UI-6100 |  | B | M | 4.7:During the inspection, some diaphragm pump support bolts were found loose, and some bolts were missing. (PS5-75-PB-3200A/B) | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:19:02.503 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007813 | PS5-75-UI-6100 |  | B | M | 4.8:During the inspection, the support bracing was found missing. | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:20:56.643 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007814 | PS5-75-UI-6100 |  | A | M | 4.9:"During the inspection, the diaphragm valve was found broken (PS5-75-BAV-1024)" | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  | Parts to be replaced | 2026-06-05T08:21:45.620 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007815 | PS5-75-UI-6100 |  | B | E | 4.10:"During Inspection, unproper Glanding Cable Gland for Cable Tag PS5-75-LIT-4202A-CJ01" | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:22:47.653 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007816 | PS5-75-UI-6100 |  | B | E | 4.11:SS Hanging Tagging for all General Transmitteri is Missing | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:23:39.187 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007853 | PS5-61-ISR-0102 |  | C | E | 20: CP261 Pressure relay for main tank indicator was found without glass as manufactured from factory. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Vendor to clarify | 2026-06-06T07:06:02.493 | gregory, dismas | PS5 - Milestone D
PL-007854 | PS5-61-ISR-0102 |  | B | E | 20.1: BR321 Gas collection pipe for gas sampling have small diameter compared to its coupling point on the Bucholz relay | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Vendor to supply BR321 Gas collection pipe for gas sampling with correct diameter as coupling point on Bucholz relay | 2026-06-06T07:55:47.963 | gregory, dismas | PS5 - Milestone D
PL-008229 | PS5-25-PDIT-0034A |  | A | I | instrument to be replaced once the new transmitters arrive at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | The instruments currently available at site will be used only for hydro test purposes on a temporary basis. | 2026-06-10T05:04:58.957 | Thao-my, Alexandre | PS5 - Milestone H
PL-008230 | PS5-25-PDIT-0034B |  | A | I | instrument to be replaced once the new transmitters arrive at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | The instruments currently available at site will be used only for hydro test purposes on a temporary basis. | 2026-06-10T05:04:58.957 | Thao-my, Alexandre | PS5 - Milestone H
PL-008231 | PS5-25-PDIT-0034C |  | A | I | instrument to be replaced once the new transmitters arrive at site. | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | The instruments currently available at site will be used only for hydro test purposes on a temporary basis. | 2026-06-10T05:04:58.957 | Thao-my, Alexandre | PS5 - Milestone H
PL-008468 |  | EACOP-PS5-25-01-0050 | B | P | 18: Paint touchup to be done | CPP AGI | PS5-25-01 - Export Pipeline Pig Receiver |  | Completed |  | EACOP-PS5-25-01-0050 Paint touchup to be done | 2026-06-13T06:53:54.780 | Bhagavath, sangeeth | PS5 - Milestone H | 2026-08-28T12:39:09.000
PL-008469 |  | EACOP-PS5-25-07-0068 | B | P | 18: Paint touchup to be done | CPP AGI | PS5-25-07 - Export Pipeline Pig Launcher |  | Originated |  | EACOP-PS5-25-07-0068 Paint touchup to be done | 2026-06-13T07:07:40.273 | Bhagavath, sangeeth | PS5 - Milestone H
PL-008493 | PS5-05-BE-0001 |  | B | E | EDG PJB - Anti-condensation heater circuit is missing | EACOP | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  | Anti-condensation heater circuit (terminals, thermostat, heater, wiring) to be installed on DIN rail once received at site | 2026-06-15T11:32:05.000 | Dujancourt, Alban | PS5 - Milestone C
PL-008540 | PS5 - DIESEL FUEL STORAGE AND PUMP AREA_Earthing |  | B | E | 4 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 4 earthing points must be terminated per approved drawings. | 2026-06-16T06:16:15.000 | Gawad, Mohamed | PS5 - Milestone A
PL-008548 | PS5 - CHEMICAL AND WASTE STORAGE AREA_Earthing |  | B | E | 9 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 9 earthing points must be terminated per approved drawings. | 2026-06-16T06:36:32.647 | Gawad, Mohamed | PS5 - Milestone A
PL-008553 | PS5 - POWER DISTRIBUTION AREA_Earthing |  | B | E | 5 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 5 earthing points must be terminated per approved drawings. | 2026-06-16T06:54:36.810 | Gawad, Mohamed | PS5 - Milestone A
PL-008564 | PS5-84-OB-0003_Earthing |  | B | E | 2 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 2 earthing points must be terminated per approved drawings. | 2026-06-16T08:02:31.803 | Gawad, Mohamed | PS5 - Milestone A
PL-008567 | PS5-84-OB-0004_Earthing |  | B | E | 2 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 2 earthing points must be terminated per approved drawings. | 2026-06-16T08:05:10.067 | Gawad, Mohamed | PS5 - Milestone A
PL-008569 | PS5 - EXPORT PUMP VSD AREA_Earthing |  | B | E | 7 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | earthing points must be terminated per approved drawings. | 2026-06-16T08:43:41.160 | Gawad, Mohamed | PS5 - Milestone A
PL-008570 | PS5 - LAUNCHER/RECEIVER AREA_Earthing |  | B | E | 10 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 10 earthing points must be terminated per approved drawings. | 2026-06-16T08:51:27.787 | Gawad, Mohamed | PS5 - Milestone A
PL-008571 | PS5 - EXPORT LOADING PUMP AREA_Earthing |  | B | E | 6 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 6 earthing points must be terminated per approved drawings. | 2026-06-16T08:54:30.243 | Gawad, Mohamed | PS5 - Milestone A
PL-008572 | PS5 - POWER GENERATION BUILDING AREA_Earthing |  | B | E | 4 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 4 earthing points must be terminated per approved drawings. | 2026-06-16T09:11:02.223 | Gawad, Mohamed | PS5 - Milestone A
PL-008573 | PS5 - CLOSED DRAIN DRUM AREA_Earthing |  | B | E | 7points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 7 earthing points must be terminated per approved drawings. | 2026-06-16T09:14:14.680 | Gawad, Mohamed | PS5 - Milestone A
PL-008574 | PS5 - POWER GENERATION COOLING TOWER AREA_Earthing |  | B | E | 20 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 20 earthing points must be terminated per approved drawings. | 2026-06-16T09:17:32.840 | Gawad, Mohamed | PS5 - Milestone A
PL-008591 | PS5 - CFO AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection | 2026-06-17T04:27:16.410 | Gawad, Mohamed | PS5 - Milestone A
PL-008592 | PS5 - CFO AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag | 2026-06-17T04:41:33.910 | Gawad, Mohamed | PS5 - Milestone A
PL-008593 | PS5 - CFO AREA_Earthing |  | C | E | Earthing chamber tag installed | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag | 2026-06-17T04:43:23.163 | Gawad, Mohamed | PS5 - Milestone A
PL-008600 | PS5 - CHEMICAL AND WASTE STORAGE AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T12:26:36.510 | Gawad, Mohamed | PS5 - Milestone A
PL-008601 | PS5 - CHEMICAL AND WASTE STORAGE AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag | 2026-06-17T12:29:01.473 | Gawad, Mohamed | PS5 - Milestone A
PL-008602 | PS5 - CLOSED DRAIN DRUM AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection | 2026-06-17T12:36:33.393 | Gawad, Mohamed | PS5 - Milestone A
PL-008603 | PS5 - CLOSED DRAIN DRUM AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T12:37:32.347 | Gawad, Mohamed | PS5 - Milestone A
PL-008605 | PS5 - DIESEL FUEL STORAGE AND PUMP AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection | 2026-06-17T12:40:25.600 | Gawad, Mohamed | PS5 - Milestone A
PL-008607 | PS5 - DIESEL FUEL STORAGE AND PUMP AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag | 2026-06-17T12:42:54.893 | Gawad, Mohamed | PS5 - Milestone A
PL-008608 | PS5 - DIESEL FUEL STORAGE AND PUMP AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T12:43:35.390 | Gawad, Mohamed | PS5 - Milestone A
PL-008609 | PS5 - EXPORT PUMP VSD AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T12:45:45.890 | Gawad, Mohamed | PS5 - Milestone A
PL-008610 | PS5 - EXPORT PUMP VSD AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T12:46:20.530 | Gawad, Mohamed | PS5 - Milestone A
PL-008611 | PS5 - EXPORT PUMP VSD AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T12:47:47.830 | Gawad, Mohamed | PS5 - Milestone A
PL-008612 | PS5 - EXPORT LOADING PUMP AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T12:53:48.533 | Gawad, Mohamed | PS5 - Milestone A
PL-008613 | PS5 - EXPORT LOADING PUMP AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T12:54:07.627 | Gawad, Mohamed | PS5 - Milestone A
PL-008614 | PS5 - EXPORT LOADING PUMP AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T12:54:25.473 | Gawad, Mohamed | PS5 - Milestone A
PL-008615 | PS5 - FENCE WEST AREA_Earthing |  | B | E | 10 connections are not completed | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 10 earthing points must be terminated per approved drawings. | 2026-06-17T12:56:49.100 | Gawad, Mohamed | PS5 - Milestone A
PL-008616 | PS5 - FENCE WEST AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T13:00:01.383 | Gawad, Mohamed | PS5 - Milestone A
PL-008617 | PS5 - LAUNCHER/RECEIVER AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T13:29:05.313 | Gawad, Mohamed | PS5 - Milestone A
PL-008618 | PS5 - LAUNCHER/RECEIVER AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T13:29:33.733 | Gawad, Mohamed | PS5 - Milestone A
PL-008623 | PS5 - POWER DISTRIBUTION AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T14:17:37.033 | Gawad, Mohamed | PS5 - Milestone A
PL-008624 | PS5 - POWER DISTRIBUTION AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T14:18:22.593 | Gawad, Mohamed | PS5 - Milestone A
PL-008625 | PS5 - POWER DISTRIBUTION AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T14:18:49.853 | Gawad, Mohamed | PS5 - Milestone A
PL-008640 | PS5 - POWER GENERATION BUILDING AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T16:48:34.100 | Gawad, Mohamed | PS5 - Milestone A
PL-008641 | PS5 - POWER GENERATION BUILDING AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T16:56:50.527 | Gawad, Mohamed | PS5 - Milestone A
PL-008642 | PS5 - POWER GENERATION BUILDING AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T16:58:29.610 | Gawad, Mohamed | PS5 - Milestone A
PL-008643 | PS5 - POWER GENERATION COOLING TOWER AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T17:04:52.413 | Gawad, Mohamed | PS5 - Milestone A
PL-008644 | PS5 - POWER GENERATION COOLING TOWER AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T17:05:28.917 | Gawad, Mohamed | PS5 - Milestone A
PL-008645 | PS5 - POWER GENERATION COOLING TOWER AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T17:06:11.257 | Gawad, Mohamed | PS5 - Milestone A
PL-008646 | PS5 - UTILITY AREA_Earthing |  | B | E | 4 points are not terminated | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 4 earthing points must be terminated per approved drawings. | 2026-06-17T17:17:55.620 | Gawad, Mohamed | PS5 - Milestone A
PL-008647 | PS5 - UTILITY AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T17:19:05.120 | Gawad, Mohamed | PS5 - Milestone A
PL-008648 | PS5 - UTILITY AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T17:23:40.910 | Gawad, Mohamed | PS5 - Milestone A
PL-008649 | PS5 - UTILITY AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T17:24:24.860 | Gawad, Mohamed | PS5 - Milestone A
PL-008650 | PS5 - UTILITY/FIRE WATER STORAGE TANK AREA_Earthing |  | B | E | 7 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 7earthing points must be terminated per approved drawings. | 2026-06-17T17:29:28.523 | Gawad, Mohamed | PS5 - Milestone A
PL-008651 | PS5 - UTILITY/FIRE WATER STORAGE TANK AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T17:30:59.733 | Gawad, Mohamed | PS5 - Milestone A
PL-008652 | PS5 - UTILITY/FIRE WATER STORAGE TANK AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T17:32:09.880 | Gawad, Mohamed | PS5 - Milestone A
PL-008653 | PS5 - UTILITY/FIRE WATER STORAGE TANK AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T17:32:51.080 | Gawad, Mohamed | PS5 - Milestone A
PL-008654 | PS5-84-OB-0003_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T17:35:21.410 | Gawad, Mohamed | PS5 - Milestone A
PL-008655 | PS5-84-OB-0003_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T17:36:09.993 | Gawad, Mohamed | PS5 - Milestone A
PL-008656 | PS5-84-OB-0004_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T17:41:53.783 | Gawad, Mohamed | PS5 - Milestone A
PL-008657 | PS5-84-OB-0004_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T17:44:04.253 | Gawad, Mohamed | PS5 - Milestone A
PL-008658 | PS5-84-OB-0006_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T17:50:03.987 | Gawad, Mohamed | PS5 - Milestone A
PL-008659 | PS5-84-OB-0006_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T17:57:44.797 | Gawad, Mohamed | PS5 - Milestone A
PL-008660 | PS5-84-OB-0007_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T18:02:57.587 | Gawad, Mohamed | PS5 - Milestone A
PL-008661 | PS5-84-OB-0007_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T18:03:51.427 | Gawad, Mohamed | PS5 - Milestone A
PL-008674 | PS5-61-IV-0001A-CH01 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-06-18T11:50:36.900 | Gawad, Mohamed | PS5 - Milestone A
PL-008675 | PS5-61-IV-0001A-CH02 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-06-18T11:52:31.660 | Gawad, Mohamed | PS5 - Milestone A
PL-008676 | PS5-61-IV-0001A-CH03 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-06-18T11:54:30.143 | Gawad, Mohamed | PS5 - Milestone A
PL-008677 | PS5-61-IV-0001B-CH01 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-06-18T11:55:44.487 | Gawad, Mohamed | PS5 - Milestone A
PL-008678 | PS5-61-IV-0001B-CH02 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-06-18T11:57:24.583 | Gawad, Mohamed | PS5 - Milestone A
PL-008679 | PS5-61-IV-0001B-CH03 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-06-18T11:58:42.733 | Gawad, Mohamed | PS5 - Milestone A
PL-008773 | PS5-25-IES-3200A-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T12:35:07.710 | Gawad, Mohamed | PS5 - Milestone H
PL-008774 | PS5-25-IES-3200A-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T12:42:34.493 | Gawad, Mohamed | PS5 - Milestone H
PL-008775 | PS5-25-IES-3200B-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T12:46:58.940 | Gawad, Mohamed | PS5 - Milestone H
PL-008776 | PS5-25-IES-3200B-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T12:47:38.230 | Gawad, Mohamed | PS5 - Milestone H
PL-008780 | PS5-25-IES-3300A-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T13:15:28.743 | Gawad, Mohamed | PS5 - Milestone H
PL-008782 | PS5-25-IES-3300A-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T13:16:10.960 | Gawad, Mohamed | PS5 - Milestone H
PL-008787 | PS5-25-IES-3300B-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T13:22:39.630 | Gawad, Mohamed | PS5 - Milestone H
PL-008788 | PS5-25-IES-3300B-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T13:23:00.713 | Gawad, Mohamed | PS5 - Milestone H
PL-008793 | PS5-25-IES-3400B-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T13:50:56.303 | Gawad, Mohamed | PS5 - Milestone H
PL-008794 | PS5-25-IES-3400B-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T13:51:18.297 | Gawad, Mohamed | PS5 - Milestone H
PL-008795 | PS5-25-IES-6400A-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T13:55:39.793 | Gawad, Mohamed | PS5 - Milestone H
PL-008796 | PS5-25-IES-6400A-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T13:55:56.950 | Gawad, Mohamed | PS5 - Milestone H
PL-008797 | PS5-25-IES-6400B-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T14:02:48.717 | Gawad, Mohamed | PS5 - Milestone H
PL-008798 | PS5-25-IES-6400B-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T14:18:22.100 | Gawad, Mohamed | PS5 - Milestone H
PL-008799 | PS5-25-IES-6500B-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T14:25:37.237 | Gawad, Mohamed | PS5 - Milestone H
PL-008800 | PS5-25-IES-6500B-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T14:26:02.663 | Gawad, Mohamed | PS5 - Milestone H
PL-008801 | PS5-25-IES-6600A-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T14:29:00.230 | Gawad, Mohamed | PS5 - Milestone H
PL-008802 | PS5-25-IES-6600A-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T14:29:16.993 | Gawad, Mohamed | PS5 - Milestone H
PL-008803 | PS5-25-IES-6600B-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T14:32:20.330 | Gawad, Mohamed | PS5 - Milestone H
PL-008804 | PS5-25-IES-6600B-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T14:32:37.817 | Gawad, Mohamed | PS5 - Milestone H
PL-008805 | PS5-25-IES-3400A-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T16:38:37.953 | Gawad, Mohamed | PS5 - Milestone H
PL-008806 | PS5-25-IES-3400A-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T16:39:04.270 | Gawad, Mohamed | PS5 - Milestone H
PL-008807 | PS5-25-IES-6500A-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T16:47:32.170 | Gawad, Mohamed | PS5 - Milestone H
PL-008808 | PS5-25-IES-6500A-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T16:48:08.693 | Gawad, Mohamed | PS5 - Milestone H
PL-009490 | PS5-82-UZ-8100 |  | A | E | 4.1:"During inspection, items inside the panel were found shaking. Package No. PS5-PKG-001" | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T07:41:23.123 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009492 | PS5-82-UZ-8100 |  | B | E | 4.2:During inspection, keys were missing at the PLC control panel and MCC panel in Package No. PS5-PKG-001 | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T07:42:20.537 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009493 | PS5-82-UZ-8100 |  | A | E | 4.3:"During inspection, as per the packing list, 3 Nos. of lighting fixtures were required, but only 2 Nos. arrived in Package No. PS5-PKG-001." | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T07:43:32.550 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009495 | PS5-82-UZ-8100 |  | B | M | 4.4:"PS5-PKG-002 Bolt and nut set 24 nos and Self tapping screw 100 pcs missing Package No PS5-PKG-002" | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T07:44:52.100 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009496 | PS5-82-UZ-8100 |  | B | M | 4.5:"During inspection, 1 No. pipe with flange and 1 No. tee with flange arrived without a packing list in Package No. PS5-PKG-005." | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T07:46:35.480 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009497 | PS5-82-UZ-8100 |  | B | E | 4.6:"During inspection, the infrared suspended solid sensor was found damaged. Package No. PS5-PKG-006" | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T07:47:41.170 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009498 | PS5-82-UZ-8100 |  | B | E | 4.7:During inspection, 1 No PS5-82-AIT-8101. 1no PS5-82-AIT-8103 and PS5-82-NRV-0010/0011/0014 arrived without a packing list in Package No. PS5-PKG-006. | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T07:49:22.323 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009499 | PS5-82-UZ-8100 |  | C | M | 4.8:During inspection, rust was observed on the valve handle at sewage metering skid (Package no PS5-PKG-006) | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T07:50:54.873 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009500 | PS5-82-UZ-8100 |  | B | M | 4.9:"During inspection, support nuts were loose for sewage metering skid Pump support package No. PS5-PKG-006" | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T07:52:53.637 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009501 | PS5-82-UZ-8100 |  | C | M | 4.10:"During inspection, rust was observed on the motor, coupling, and shaft area of Sludge Pump Skid PS-SKID-2, Pump No. PS5-82-PE-3400A/B. (Package no PS5-PKG-007)" | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T07:54:02.947 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009502 | PS5-82-UZ-8100 |  | A | E | 4.11:During inspection, keys were missing at the Junction box of sludge pump skid Package No.PS5-PKG-007 | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T07:55:18.020 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009503 | PS5-82-UZ-8100 |  | B | M | 4.12:During inspection, support nuts were missing for Permeate Pump PS5-82-DM-3200A/B of permeate pump skid in Package No. PS5-PKG-008 | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T07:56:44.230 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009504 | PS5-82-UZ-8100 |  | A | M | 4.13:During inspection, flange bolts were found missing of permete pump skid in Package No. PS5-PKG-008 | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T07:58:07.640 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009505 | PS5-82-UZ-8100 |  | B | M | 4.14:During inspection, pipe U clamp support nuts were loosen permete pump skid in Package No. PS5-PKG-008 | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T07:59:02.310 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009506 | PS5-82-UZ-8100 |  | B | M | 4.15:During inspection, rust was observed on the motor wheel of roots blower skid in Package No. PS5-PKG-011 | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:00:24.623 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009507 | PS5-82-UZ-8100 |  | B | M | 4.16:During inspection, pump support bolt nuts were found on the floor of roots blower skid.in package no.PS5-PKG-011 | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:01:20.567 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009508 | PS5-82-UZ-8100 |  | B | M | 4.17:"During inspection, as per the packing list, 15 Nos. of operation columns , but only 1 No. arrived in Package No. PS5-PKG-023." | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:02:31.140 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009509 | PS5-82-UZ-8100 |  | B | M | 4.18:The welding quality on the dosing pump skid is not up to the required standard in package no PS5-PKG-017 | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:03:49.410 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009511 | PS5-82-UZ-8100 |  | B | M | 4.19:"The welding quality on the MDR membrane module skid is not up to the required standard in package no PS5-PKG-020" | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:08:24.007 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009512 | PS5-82-UZ-8100 |  | C | M | 4.20:During inspection, it was observed that pickling and passivation were not carried out at the MDR membrane module skid stainless welded area after welding package no PS5-PKG-020. | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:09:19.767 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009513 | PS5-71-BI-1110-CC01 |  | B | I | No segregation between INS cables as per project specification | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Originated |  | Re-route and separate INS cables as per spec requirements and resubmit for inspection | 2026-06-27T08:10:27.507 | Gawad, Mohamed | PS5 - Milestone A
PL-009514 | PS5-82-UZ-8100 |  | B | M | 4.21:During inspection, Dosing pump support nuts were found missing in package no. PS5-PKG-012 | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:10:43.587 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009515 | PS5-82-UZ-8100 |  | C | M | 4.22:During inspection, rust was observed on the gratings of sludge dewatering tank in Package No. PS5-PKG-024 | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:11:49.700 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009516 | PS5-82-UZ-8100 |  | B | M | 4.23:The welding quality on the explosion proof box is not up to the required standard in package no PS5-PKG-022 | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:13:16.797 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009518 | PS5-82-UZ-8100 |  | B | M | 4.24:During inspection,effluent pump skid flange stud bolts were found missing, and some stud bolts were found loose in package no. PS5-PKG-010 | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:14:11.490 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009519 | PS5-82-UZ-8100 |  | B | E | 4.25:During inspection, terminal block numbers were found missing in the junction box of Package No. PS5-PKG-008 | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:15:38.750 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009521 | PS5-82-UZ-8100 |  | B | E | 4.26:During inspection, a plug was found missing at the junction box in Package No. PS5-PKG-008 | CPP AGI | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:17:11.243 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009522 | PS5-71-BI-1116-CC01 |  | B | I | No segregation between INS cables as per project specification | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Completed |  | Re-route and separate INS cables as per spec requirements and resubmit for inspection | 2026-06-27T08:22:52.430 | Gawad, Mohamed | PS5 - Milestone A | 2026-08-16T08:29:18.000
PL-009523 | PS5-82-UZ-8100 |  | B | E | 4.27:During inspection, the Teflon sheet was found missing at the junction box in Package No. PS5-PKG-008 | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:23:26.907 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009524 | PS5-82-UZ-8100 |  | B | E | 4.28:During inspection, a plug was found missing at MCC Panel PS5-82-IN-0001 | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:24:26.930 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009525 | PS5-71-BI-1306-CC01 |  | B | I | No segregation between INS cables as per project specification | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Completed |  | Re-route and separate INS cables as per spec requirements and resubmit for inspection | 2026-06-27T08:24:29.143 | Gawad, Mohamed | PS5 - Milestone A | 2026-08-16T08:29:00.000
PL-009526 | PS5-82-UZ-8100 |  | B | E | 4.29:During inspection, improper cable laying was observed at PS5-83-PIT-8104-CC01. | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:25:52.533 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009527 | PS5-25-BI-2308-CC01 |  | B | I | No segregation between INS cables as per project specification | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Completed |  | Re-route and separate INS cables as per spec requirements and resubmit for inspection | 2026-06-27T08:25:53.773 | Gawad, Mohamed | PS5 - Milestone A | 2026-08-16T08:27:46.000
PL-009528 | PS5-82-UZ-8100 |  | B | E | 4.30:During inspection, cable stress was observed in Package No. PS5-PKG-008. | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:26:57.680 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009529 | PS5-25-BI-2108-CC01 |  | B | I | No segregation between INS cables as per project specification | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Completed |  | Re-route and separate INS cables as per spec requirements and resubmit for inspection | 2026-06-27T08:26:58.043 | Gawad, Mohamed | PS5 - Milestone A | 2026-08-16T08:27:23.000
PL-009530 | PS5-25-BI-2315-CC01 |  | B | I | No segregation between INS cables as per project specification | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Completed |  | Re-route and separate INS cables as per spec requirements and resubmit for inspection | 2026-06-27T08:27:58.757 | Gawad, Mohamed | PS5 - Milestone A | 2026-08-16T08:29:55.000
PL-009531 | PS5-82-UZ-8100 |  | B | E | 4.31:During inspection, no bonding jumper was found in Package No. PS5-PKG-008. | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:28:22.410 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009532 | PS5-25-BI-2109-CC01 |  | B | I | No segregation between INS cables as per project specification | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Completed |  | Re-route and separate INS cables as per spec requirements and resubmit for inspection | 2026-06-27T08:28:56.003 | Gawad, Mohamed | PS5 - Milestone A | 2026-08-16T08:32:21.000
PL-009533 | PS5-82-UZ-8100 |  | A | E | 4.32:During inspection, ferrules were found missing at Panel PS5-82-IN-0001 | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:29:39.037 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009534 | PS5-25-BI-2316-CC01 |  | B | I | No segregation between INS cables as per project specification | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Completed |  | Re-route and separate INS cables as per spec requirements and resubmit for inspection | 2026-06-27T08:29:57.620 | Gawad, Mohamed | PS5 - Milestone A | 2026-08-16T08:29:38.000
PL-009535 | PS5-25-BI-2312-CC01 |  | B | I | No segregation between INS cables as per project specification | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Completed |  | Re-route and separate INS cables as per spec requirements and resubmit for inspection | 2026-06-27T08:31:08.540 | Gawad, Mohamed | PS5 - Milestone A | 2026-08-16T08:28:06.000
PL-009536 | PS5-82-UZ-8100 |  | A | E | 4.33:"During inspection, equipment drop damage was observed in Package No. PS5-PKG-001" | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:31:36.343 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009537 | PS5-25-BI-1104-CC01 |  | B | I | No segregation between INS cables as per project specification | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Completed |  | Re-route and separate INS cables as per spec requirements and resubmit for inspection | 2026-06-27T08:32:12.757 | Gawad, Mohamed | PS5 - Milestone A | 2026-08-16T08:27:02.000
PL-009538 | PS5-82-UZ-8100 |  | B | E | 4.34:"During inspection, a plug was found missing at Panel PS5-82-IN-0001" | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:33:01.700 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009539 | PS5-03-BI-2502-CC01 |  | B | I | No segregation between INS cables as per project specification | CPP AGI | PS5-03-06 - FZ-06 - Transformer Area |  | Completed |  | Re-route and separate INS cables as per spec requirements and resubmit for inspection | 2026-06-27T08:33:18.353 | Gawad, Mohamed | PS5 - Milestone E | 2026-08-16T08:25:14.000
PL-009540 | PS5-82-UZ-8100 |  | B | E | 4.35:"During inspection, terminal block numbers were found missing in Panel PS5-82-IN-0001" | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:34:03.443 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009541 | PS5-71-BI-2317-CC01 |  | B | I | No segregation between INS cables as per project specification | CPP AGI | PS5-71-15 - Diesel Fuel Storage Tank |  | Completed |  | Re-route and separate INS cables as per spec requirements and resubmit for inspection | 2026-06-27T08:34:25.950 | Gawad, Mohamed | PS5 - Milestone F | 2026-08-16T08:28:29.000
PL-009542 | PS5-82-UZ-8100 |  | B | E | 4.36:Cover bend was observed on Panel PS5-82-IN-0001. | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:35:14.110 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009543 | PS5-25-BI-1103-CC01 |  | B | I | No segregation between INS cables as per project specification | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Completed |  | Re-route and separate INS cables as per spec requirements and resubmit for inspection | 2026-06-27T08:35:33.957 | Gawad, Mohamed | PS5 - Milestone A | 2026-08-16T08:26:40.000
PL-009544 | PS5-82-UZ-8100 |  | B | E | 4.37:During inspection, improper equipment tag installation was observed on the Ventilator Fan Selector in Package No. PS5-PKG-001) | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:36:28.427 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009545 | PS5-71-BI-2314-CC01 |  | B | I | No segregation between INS cables as per project specification | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Completed |  | Re-route and separate INS cables as per spec requirements and resubmit for inspection | 2026-06-27T08:37:20.823 | Gawad, Mohamed | PS5 - Milestone A | 2026-08-16T08:28:45.000
PL-009546 | PS5-82-UZ-8100 |  | C | M | 4.38:During inspection container PS5-82-OC-0001 name board bolts 2 nos missing | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:37:44.210 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009547 | PS5-82-UZ-8100 |  | B | M | 4.39:"During inspection, M12 stud bolts were found missing on the mechanical screw screen support, tag no. PS5-82-MES-9100. package no. PS5-PKG-008" | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:38:53.867 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009548 | PS5-82-UZ-8100 |  | B | M | 4.40:During inspection, the roof sheet connecting Angle was not received. | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:40:00.700 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009549 | PS5-82-UZ-8100 |  | B | M | 4.41:During inspection, it was found that all gaskets were improperly packed, resulting in damage to most of the gaskets. | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:40:50.597 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009550 | PS5-82-UZ-8100 |  | A | M | 4.42:During inspection, only the sludge dewatering tank supporting structure was received. The sludge dewatering tank, tag no. PS5-82-TR-4400, was not received in package no. PS5-PKG-021. | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Completed |  | 4.42:During inspection, only the sludge dewatering tank supporting structure was received. The sludge dewatering tank, tag no. PS5-82-TR-4400, was not received in package no. PS5-PKG-021. | 2026-06-27T08:42:37.357 | THANGARATHINAM, ajikumar | PS5 - Milestone I | 2026-07-14T13:15:09.000
PL-009551 | PS5-60-BE-0001-CL04 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T08:43:33.607 | Gawad, Mohamed | PS5 - Milestone B
PL-009552 | PS5-82-UZ-8100 |  | B | E | 4.43:As per the packing list, 100 Nos. of stainless steel bolt and nut sets, they were not received in Package No. PS-PKG-021. | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:43:42.250 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009553 | PS5-61-IK-0003-CL01 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T08:44:57.773 | Gawad, Mohamed | PS5 - Milestone B
PL-009554 | PS5-82-UZ-8100 |  | B | M | 4.44:The most items of package received does not match the packing list. The items have been mixed up and packed in different packages. | EPS VENDOR | PS5-82-02 - Sewage Treatment Plant Package |  | Originated |  |  | 2026-06-27T08:45:02.670 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-009555 | PS5-61-IK-0003-CL02 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T08:46:13.440 | Gawad, Mohamed | PS5 - Milestone B
PL-009557 | PS5-60-BE-0002-CL05 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-60-26 - Instrument Air Compressor Skid |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T08:51:12.857 | Gawad, Mohamed | PS5 - Milestone B
PL-009558 | PS5-60-BE-0002-CL01 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-60-26 - Instrument Air Compressor Skid |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T08:52:27.313 | Gawad, Mohamed | PS5 - Milestone B
PL-009559 | PS5-60-BE-0002-CL02 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-60-26 - Instrument Air Compressor Skid |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T08:54:08.293 | Gawad, Mohamed | PS5 - Milestone B
PL-009560 | PS5-60-BE-0007A-CL01 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T08:55:56.687 | Gawad, Mohamed | PS5 - Milestone B
PL-009561 | PS5-60-BE-0007A-CL02 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T08:57:50.297 | Gawad, Mohamed | PS5 - Milestone B
PL-009562 | PS5-60-BE-0007A-CL03 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T09:03:06.883 | Gawad, Mohamed | PS5 - Milestone B
PL-009564 | PS5-60-BE-0007B-CL01 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T09:12:34.320 | Gawad, Mohamed | PS5 - Milestone B
PL-009566 | PS5-60-BE-0007B-CL02 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T09:23:38.967 | Gawad, Mohamed | PS5 - Milestone B
PL-009567 | PS5-60-BE-0007B-CL03 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T09:24:59.897 | Gawad, Mohamed | PS5 - Milestone B
PL-009568 | PS5-60-BE-0001-CL01 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T09:26:13.573 | Gawad, Mohamed | PS5 - Milestone B
PL-009569 | PS5-60-BE-0001-CL02 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T09:27:23.770 | Gawad, Mohamed | PS5 - Milestone B
PL-009570 | PS5-60-BE-0002-CL03 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-60-26 - Instrument Air Compressor Skid |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T09:28:32.713 | Gawad, Mohamed | PS5 - Milestone B
PL-009571 | PS5-60-IE-0003A-CD15 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T09:29:39.417 | Gawad, Mohamed | PS5 - Milestone B
PL-009572 | PS5-60-IE-0003B-CD15 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T09:30:44.877 | Gawad, Mohamed | PS5 - Milestone B
PL-009573 | PS5-06-GU-0003A-CD02 |  | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | Separate 48VDC cables from 110/230/400VAC cables as per spec requirements | 2026-06-27T09:31:43.597 | Gawad, Mohamed | PS5 - Milestone B
PL-009686 | PS5-63-IV-0010 |  | B | M | 4:During inspection, rust was found on both sides inside the radiator. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-06-29T14:23:08.413 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-009687 | PS5-63-IV-0010 |  | B | M | 4.1:During inspection, rust was found on the integrated relay unit and CT trminal box bolts. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-06-29T14:24:47.640 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-009688 | PS5-63-IV-0010 |  | B | M | 4.2:The welding quality on the transformer is not up to the required standard (some welded area), | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-06-29T14:25:46.110 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-009689 | PS5-63-IV-0010 |  | B | M | 4.3:During inspection, only the anchor angle bolts were received. The nuts and washers were not received | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-06-29T14:27:05.363 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-009690 | PS5-63-IV-0011 |  | B | M | 4:During inspection, rust was found on both sides inside the radiator. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-06-29T14:29:18.460 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-009691 | PS5-63-IV-0011 |  | B | M | 4.1:During inspection, rust was found on the integrated relay unit and CT trminal box bolts. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-06-29T14:30:35.707 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-009692 | PS5-63-IV-0011 |  | B | M | 4.2:The welding quality on the transformer is not up to the required standard (some welded area), | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-06-29T14:32:28.533 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-009693 | PS5-63-IV-0011 |  | B | M | 4.3:During inspection, only the anchor angle bolts were received. The nuts and washers were not received | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-06-29T14:33:22.557 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-009745 | PS5-60-EA-2100A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-06-30T08:04:27.403 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T07:51:58.000
PL-009746 | PS5-60-EA-2100A |  | C | M | 10.1: Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | 10.1: Touch up / painting to be completed wherever required on the equipment | 2026-06-30T08:07:09.037 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-06-30T08:08:25.000
PL-009748 | PS5-25-PA-3100A |  | B | M | 21 Coupling spacer to be tinghtened properly after motor SOLO-RUN. (Shims are available in PS5 CPP store) | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | 21 Coupling spacer to be tinghtened properly after motor SOLO-RUN. (Shims are available in PS5 CPP store) | 2026-06-30T08:16:20.793 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-009749 | PS5-25-PA-3100A |  | B | M | 21.1: 3/4" blind flange to be installed on the suction nozzle of pump | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | 21.1: 3/4" blind flange to be installed on the suction nozzle of pump by commissioning team | 2026-06-30T08:19:21.893 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-009750 | PS5-25-PA-3100A |  | C | M | 21.2: Insulation (Flexible jackets) to be reinstated properly | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | 21.2: Insulation (Flexible jackets) to be reinstated properly | 2026-06-30T08:25:43.050 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-009751 | PS5-25-PA-3100B |  | B | M | 21:Coupling spacer to be tinghtened properly after motor SOLO-RUN. (Shims are available in PS5 CPP store) | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Coupling spacer to be tinghtened properly after motor SOLO-RUN. (Shims are available in PS5 CPP store) | 2026-06-30T08:40:58.527 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-009752 | PS5-25-PA-3100B |  | B | M | 21.1:3/4" blind flange to be installed on the suction nozzle of pump | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | 3/4" blind flange to be installed on the suction nozzle of pump by commissioning team | 2026-06-30T08:41:32.410 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-009753 | PS5-25-PA-3100B |  | C | M | 21.2:Insulation (Flexible jackets) to be reinstated properly | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Insulation (Flexible jackets) to be reinstated properly | 2026-06-30T08:41:59.223 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-009754 | PS5-25-PA-3100B |  | A | M | 21.3:Coupling spacer to be located and installed (Coupling received from vendor is not matching with Export pump - B , also coupling guard to be installed)) | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | 21.3:Coupling spacer to be located and check for the suitability | 2026-06-30T08:42:28.850 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-009755 | PS5-25-PA-3100C |  | B | M | 21:Coupling spacer to be tinghtened properly after motor SOLO-RUN. (Shims are available in PS5 CPP store) | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Coupling spacer to be tinghtened properly after motor SOLO-RUN. (Shims are available in PS5 CPP store) | 2026-06-30T09:33:40.413 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-009756 | PS5-25-PA-3100C |  | B | M | 21.1:3/4" blind flange to be installed on the suction nozzle of pump | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | 1" blind flange to be installed on the suction nozzle of pump | 2026-06-30T09:34:25.197 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-009757 | PS5-25-PA-3100C |  | C | M | 21.2:Insulation (Flexible jackets) to be reinstated properly | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Insulation (Flexible jackets) to be reinstated properly | 2026-06-30T09:35:24.130 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-009758 | PS5-60-EA-2100B |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-06-30T10:15:32.163 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T07:52:22.000
PL-009759 | PS5-60-EA-2100B |  | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-06-30T10:16:31.450 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-009760 | PS5-60-EA-2200A |  | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-06-30T10:18:38.583 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-009761 | PS5-60-EA-2200A |  | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-06-30T10:22:04.760 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-009762 | PS5-60-EA-2200B |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-06-30T10:24:12.310 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T07:52:51.000
PL-009763 | PS5-60-EA-2200B |  | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-06-30T10:24:53.280 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-009764 | PS5-60-EA-2300A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-06-30T10:27:28.433 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T07:53:28.000
PL-009765 | PS5-60-EA-2300A |  | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-06-30T10:29:04.580 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-009766 | PS5-60-EA-2300B |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-06-30T10:35:11.833 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T07:53:49.000
PL-009767 | PS5-60-EA-2300B |  | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-06-30T10:36:02.017 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-009768 | PS5-60-EA-2400A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-06-30T10:39:14.420 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T07:54:13.000
PL-009769 | PS5-60-EA-2400A |  | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-06-30T10:40:19.793 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-009770 | PS5-60-EA-2400B |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-06-30T10:46:08.023 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T07:54:44.000
PL-009772 | PS5-60-EA-2400B |  | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-06-30T10:46:51.150 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-009773 | PS5-60-EA-2500A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping | 2026-06-30T10:48:36.980 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T07:55:14.000
PL-009774 | PS5-60-EA-2500A |  | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-06-30T10:49:30.087 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-009775 | PS5-60-EA-2500B |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-06-30T10:51:22.650 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T07:55:35.000
PL-009776 | PS5-60-EA-2500B |  | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-06-30T10:53:09.970 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-009777 | PS5-60-EA-2600A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-06-30T11:00:13.680 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T07:55:54.000
PL-009778 | PS5-60-EA-2600A |  | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-06-30T11:01:01.540 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-009779 | PS5-60-EA-2600B |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-06-30T11:04:23.623 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T07:56:11.000
PL-009781 | PS5-60-EA-2600B |  | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-06-30T11:05:59.147 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-009782 | PS5-60-EA-2700A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-76 - Engine G Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-06-30T11:07:54.963 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-08-13T07:57:55.000
PL-009783 | PS5-60-EA-2700A |  | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-76 - Engine G Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-06-30T11:08:44.047 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-009784 | PS5-60-EA-2700B |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-76 - Engine G Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-06-30T11:10:36.200 | THANGARATHINAM, ajikumar | PS5 - Milestone E | 2026-08-13T07:58:41.000
PL-009785 | PS5-60-EA-2700B |  | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-76 - Engine G Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-06-30T11:11:22.077 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-009828 | PS5-25-PA-3100A |  | B | M | 17:Alignment to be verified while installing suction and discharge line valves. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | :Alignment to be verified while installing suction and discharge line valves. | 2026-07-01T11:06:31.693 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-009846 | PS5-25-PA-3100B |  | B | M | 17:Alignment to be verified while installing suction and discharge line valves | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Alignment to be verified while installing suction and discharge line valves | 2026-07-01T11:36:44.200 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-009847 | PS5-25-PA-3100C |  | B | M | 17:Alignment to be verified while installing suction and discharge line valves | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Alignment to be verified while installing suction and discharge line valves | 2026-07-01T11:44:44.513 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-010025 |  | PS5-61-IG-0007_CKT20 | B | E | Junction Box TAG is missing | CPP AGI | PS5-62-09 - Outdoor Normal Lighting DB - PS5-61-IG-0007 |  | Originated |  | Junction Box TAG to be Installed | 2026-07-02T10:32:40.050 | Gawad, Mohamed | PS5 - Milestone G
PL-010028 |  | PS5-61-IG-0007_CKT16 | B | E | Junction Box TAG is missing | CPP AGI | PS5-62-09 - Outdoor Normal Lighting DB - PS5-61-IG-0007 |  | Originated |  | Junction Box TAG to be Installed | 2026-07-02T10:47:04.533 | Gawad, Mohamed | PS5 - Milestone G
PL-010115 | PS5-28-IES-3900A-CD01 |  | B | E | Cable gland earthing is not yet installed | CPP AGI | PS5-28-17 - Reinjection Pump |  | Originated |  | Install the cable gland earthing as per the approved drawings and project specifications | 2026-07-03T13:01:05.657 | Gawad, Mohamed | PS5 - Milestone H
PL-010116 | PS5-71-IES-3200-CD01 |  | B | E | Cable gland earthing is not yet installed | CPP AGI | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  | Install the cable gland earthing as per the approved drawings and project specifications | 2026-07-03T13:30:45.343 | Gawad, Mohamed | PS5 - Milestone F
PL-010120 | PS5-71-IES-3300A-CD01 |  | B | E | Cable gland earthing is not yet installed | CPP AGI | PS5-71-05 - CFO Transfer Pump A/B |  | Originated |  | Install the cable gland earthing as per the approved drawings and project specifications | 2026-07-03T14:17:34.430 | Gawad, Mohamed | PS5 - Milestone H
PL-010121 | PS5-71-IES-3300B-CD01 |  | B | E | Cable gland earthing is not yet installed | CPP AGI | PS5-71-05 - CFO Transfer Pump A/B |  | Originated |  | Install the cable gland earthing as per the approved drawings and project specifications | 2026-07-03T14:21:05.583 | Gawad, Mohamed | PS5 - Milestone H
PL-010126 | PS5-71-IES-3400A-CD01 |  | B | E | Cable gland earthing is not yet installed | CPP AGI | PS5-71-13 - CFO Service Pump A/B |  | Originated |  | Install the cable gland earthing as per the approved drawings and project specifications | 2026-07-03T14:23:35.227 | Gawad, Mohamed | PS5 - Milestone H
PL-010131 | PS5-71-IES-3500A-CD01 |  | B | E | Cable gland earthing is not yet installed | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | Install the cable gland earthing as per the approved drawings and project specifications | 2026-07-03T14:26:56.577 | Gawad, Mohamed | PS5 - Milestone B
PL-010132 | PS5-71-IES-3500B-CD01 |  | B | E | Cable gland earthing is not yet installed | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | Install the cable gland earthing as per the approved drawings and project specifications | 2026-07-03T14:28:55.873 | Gawad, Mohamed | PS5 - Milestone B
PL-010133 | PS5-53-IES-3100A-CD01 |  | B | E | Cable gland earthing is not yet installed | CPP AGI | PS5-53-02 - Water Distribution Pump A/B |  | Originated |  | Install the cable gland earthing as per the approved drawings and project specifications | 2026-07-03T14:31:21.467 | Gawad, Mohamed | PS5 - Milestone E
PL-010134 | PS5-53-IES-3100B-CD01 |  | B | E | Cable gland earthing is not yet installed | CPP AGI | PS5-53-02 - Water Distribution Pump A/B |  | Originated |  | Install the cable gland earthing as per the approved drawings and project specifications | 2026-07-03T14:33:40.547 | Gawad, Mohamed | PS5 - Milestone E
PL-010183 | PS5-60-TX-41100A |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-07-05T06:47:50.330 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T07:59:57.000
PL-010184 | PS5-60-TX-41100A |  | C | M | 23.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-07-05T06:48:36.160 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-010185 | PS5-60-TX-41100A |  | B | E | 23.2:EARTHING TO BE DONE | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | EARTHING TO BE DONE | 2026-07-05T06:49:10.800 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-010186 | PS5-60-TX-41100B |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-07-05T06:52:31.547 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T08:00:35.000
PL-010187 | PS5-60-TX-41100B |  | C | M | 23.1:Touch up / painting to be completed wherever required on the equipmen | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipmen | 2026-07-05T06:53:06.153 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-010188 | PS5-60-TX-41100B |  | B | E | 23.2:EARTHING TO BE DONE | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | EARTHING TO BE DONE | 2026-07-05T06:53:46.827 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-010189 | PS5-60-TX-41200A |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-07-05T07:02:36.837 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T08:03:26.000
PL-010190 | PS5-60-TX-41200A |  | C | M | 23.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-07-05T07:03:47.660 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-010191 | PS5-60-TX-41200A |  | B | E | 23.2: ERTHING TO BE DONE | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | ERTHING TO BE DONE | 2026-07-05T07:05:26.643 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-010192 | PS5-60-TX-41200B |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-07-05T07:12:41.870 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T08:05:32.000
PL-010193 | PS5-60-TX-41200B |  | C | M | 23.1:Touch up / painting to be completed wherever required on the equipmen | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | Touch up / painting to be completed wherever required on the equipmen | 2026-07-05T07:13:44.410 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-010194 | PS5-60-TX-41200B |  | B | E | 23.2:EARTHING TO BE DONE | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | EARTHING TO BE DONE | 2026-07-05T07:14:19.190 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-010358 |  | EACOP-PS5-28-04-0090 | B | P | 18:Pickling and passivation to be done | CPP AGI | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  | Pickling and passivation to be done | 2026-07-07T10:39:24.240 | Bhagavath, sangeeth | PS5 - Milestone E
PL-010360 |  | EACOP-PS5-28-06-0096 | B | P | 18:Pickling and Passivation to be done | CPP AGI | PS5-28-06 - Relief Drum and Pump |  | Originated |  | Pickling and Passivation to be done on rusted area | 2026-07-07T10:52:17.127 | Bhagavath, sangeeth | PS5 - Milestone G
PL-010385 | PS5-08-01MP-0001-CC01 |  | B | T | Cable not Dressing at Both Ends | CPP AGI | PS5-08-01 - PAGA |  | Originated |  | Cable Need to be Dressing at Both Ends | 2026-07-08T06:36:57.290 | Gawad, Mohamed | PS5 - Milestone F
PL-010387 | PS5-08-01MP-0001-CC03 |  | B | T | Cable not Dressing at Both Ends | CPP AGI | PS5-08-01 - PAGA |  | Originated |  | Cable Need to be Dressing at Both Ends | 2026-07-08T06:44:55.290 | Gawad, Mohamed | PS5 - Milestone F
PL-010388 | PS5-08-01MP-0001-CC04 |  | B | T | Cable not Dressing at Both Ends | CPP AGI | PS5-08-01 - PAGA |  | Originated |  | Cable Need to be Dressing at Both Ends | 2026-07-08T06:48:17.943 | Gawad, Mohamed | PS5 - Milestone F
PL-010561 | PS5-71-PA-3500A |  | B | M | 21:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN | 2026-07-09T11:43:24.790 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-010562 | PS5-71-PA-3500A |  | C | M | 21.1:Touch up / painting to be completed wherever required on the equipmen | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | Touch up / painting to be completed wherever required on the equipmen | 2026-07-09T11:45:17.300 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-010563 | PS5-71-PA-3500B |  | B | M | 21:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN | 2026-07-09T11:47:47.427 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-010564 | PS5-71-PA-3500B |  | C | M | 21.1:Touch up / painting to be completed wherever required on the equipmen | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | Touch up / painting to be completed wherever required on the equipmen | 2026-07-09T11:48:55.840 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-010755 |  | EACOP-PS5-60-25-0388 | B | P | 18:Pickling and passivation to be done | CPP AGI | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | Pickling and passivation to be done in Rusted Area | 2026-07-10T08:29:49.937 | Bhagavath, sangeeth | PS5 - Milestone E
PL-010756 |  | EACOP-PS5-71-01-0294 | B | P | 18:Paint touchup to be done | CPP AGI | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  | Paint touchup to be done in damaged area | 2026-07-10T08:38:11.387 | Bhagavath, sangeeth | PS5 - Milestone H
PL-010765 |  | EACOP-PS5-28-03-0081 | B | P | 18: Pickling and passivation to be don | CPP AGI | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  | Pickling and passivation to be done in rusted area | 2026-07-10T11:47:49.723 | Bhagavath, sangeeth | PS5 - Milestone G
PL-010766 |  | EACOP-PS5-28-06-0095 | B | P | 18:Paint touchup to be done | CPP AGI | PS5-28-06 - Relief Drum and Pump |  | Originated |  | Paint touchup to be done in damaged area | 2026-07-10T11:56:05.743 | Bhagavath, sangeeth | PS5 - Milestone G
PL-010865 | PS5-05-IE-8100 |  | B | E | bar not connected to earth grid | CPP AGI | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | bar connected to earth grid | 2026-07-11T04:42:57.973 | Gawad, Mohamed | PS5 - Milestone C
PL-010868 | PS5-05-IE-8100 |  | C | E | The Panel Frame not to be touch up paint | CPP AGI | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | The Panel Frame need to be touch up paint | 2026-07-11T04:44:20.963 | Gawad, Mohamed | PS5 - Milestone C
PL-010904 |  | EACOP-PS5-60-25-0388 | B | P | 18.1: RLMU to be done | CPP AGI | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | 1" GATE VALVE commodity code RLMU to be done, Drawing No-TZ-MID-68-WPR2-207603 | 2026-07-11T06:46:37.757 | Bhagavath, sangeeth | PS5 - Milestone E
PL-010912 | PS5-60-LA-0002B |  | B | I | bar not connected to isolated earth grid | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | we need bar connected to isolated earth grid | 2026-07-11T07:00:51.283 | Gawad, Mohamed | PS5 - Milestone D
PL-010921 | PS5-60-LA-0002C |  | B | I | bar not connected to isolated earth grid | CPP AGI | PS5-60-16 - Power Generation Package F |  | Originated |  | we need bar connected to isolated earth grid | 2026-07-11T07:06:29.220 | Gawad, Mohamed | PS5 - Milestone D
PL-010964 |  | EACOP-PS5-01-05-0425 | B | P | 18: Paint touch up to be done | CPP AGI | PS5-01-05 - Foam Skid |  | Originated |  | Paint touchup to be done in damaged area | 2026-07-11T12:28:58.830 | Bhagavath, sangeeth | PS5 - Milestone F
PL-010965 |  | EACOP-PS5-01-06-0020 | B | P | 18:Pickling and passivation to be done | CPP AGI | PS5-01-06 - Foam Concentrate Distribution |  | Originated |  | Pickling and passivation to be done in rusted area | 2026-07-11T12:44:57.983 | Bhagavath, sangeeth | PS5 - Milestone F
PL-010967 |  | EACOP-PS5-01-06-0020 | B | P | 18.1:RLMU to be done | CPP AGI | PS5-01-06 - Foam Concentrate Distribution |  | Originated |  | CTR commodity code to be add. design change RLMU to be done | 2026-07-11T12:50:42.853 | Bhagavath, sangeeth | PS5 - Milestone F
PL-010968 |  | EACOP-PS5-28-12-0110 | B | P | 18:Paint touchup to be done | CPP AGI | PS5-28-12 - Open Drains (OD3) |  | Originated |  | Paint touchup to be done in damaged area | 2026-07-11T12:55:49.640 | Bhagavath, sangeeth | PS5 - Milestone I
PL-011075 |  | EACOP-PS5-60-24-0173 | B | P | 18:Paint touchup to be done | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  | Paint touchup to be done in damaged area | 2026-07-13T05:28:32.003 | Bhagavath, sangeeth | PS5 - Milestone E
PL-011077 |  | EACOP-PS5-60-24-0174 | B | P | 18:Pickling and passivation to be done | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  | Pickling and passivation to be done in the rusted area | 2026-07-13T05:35:39.993 | Bhagavath, sangeeth | PS5 - Milestone E
PL-011079 |  | EACOP-PS5-60-25-0179 | B | P | 18:Paint touchup to be don | CPP AGI | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | Paint touchup to be done in damaged area | 2026-07-13T05:43:53.520 | Bhagavath, sangeeth | PS5 - Milestone E
PL-011080 |  | EACOP-PS5-60-25-0180 | B | P | 18:Pickling and passivation to be done | CPP AGI | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | Pickling and passivation to be done in rusted area | 2026-07-13T05:49:04.660 | Bhagavath, sangeeth | PS5 - Milestone E
PL-011103 | PS5-08-01LS-0101-CR01 |  | B | T | Cable no Dressing at Both Ends | CPP AGI | PS5-08-01 - PAGA |  | Originated |  | Cable Need to be Dressing at Both Ends | 2026-07-13T08:10:31.360 | Gawad, Mohamed | PS5 - Milestone F
PL-011108 | PS5-08-01BT-1904-CR01 |  | B | T | Cable no Dressing at Both Ends | CPP AGI | PS5-08-01 - PAGA |  | Originated |  | Cable Need to be Dressing at Both Ends | 2026-07-13T08:58:41.713 | Gawad, Mohamed | PS5 - Milestone F
PL-011109 | PS5-08-01BT-1902-CR02 |  | B | T | Cable no Dressing at Both Ends | CPP AGI | PS5-08-01 - PAGA |  | Originated |  | Cable Need to be Dressing at Both Ends | 2026-07-13T09:11:32.140 | Gawad, Mohamed | PS5 - Milestone F
PL-011110 | PS5-08-01BT-1903-CR01 |  | B | T | Cable no Dressing at Both Ends | CPP AGI | PS5-08-01 - PAGA |  | Originated |  | Cable Need to be Dressing at Both Ends | 2026-07-13T09:14:10.227 | Gawad, Mohamed | PS5 - Milestone F
PL-011111 | PS5-08-01LS-0201-CR01 |  | B | T | Cable no Dressing at Both Ends | CPP AGI | PS5-08-01 - PAGA |  | Originated |  | Cable Need to be Dressing at Both Ends | 2026-07-13T09:16:09.223 | Gawad, Mohamed | PS5 - Milestone F
PL-011146 |  | EACOP-PS5-60-26-0183 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-26 - Instrument Air Compressor Skid |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-13T14:38:13.257 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T10:52:25.000
PL-011147 |  | EACOP-PS5-60-26-0183 | B | P | 18.1:1" ValveCTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-26 - Instrument Air Compressor Skid |  | Originated |  | 1" ValveCTR commodity code to be add. RLMU to be done | 2026-07-13T14:39:49.920 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011148 |  | EACOP-PS5-60-26-0183 | B | P | 18.2:Paint touchup to be done | CPP AGI | PS5-60-26 - Instrument Air Compressor Skid |  | Completed |  | Paint touchup to be done in damaged area | 2026-07-13T14:42:16.113 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T10:53:09.000
PL-011149 |  | EACOP-PS5-60-26-0184 | B | P | 18:F1 flange connection to PS5-60-UA-5200/TP-311 is pending. | CPP AGI | PS5-60-26 - Instrument Air Compressor Skid |  | Originated |  | F1 flange connection to PS5-60-UA-5200/TP-311 is pending. Flange management and final connection to be completed. | 2026-07-13T14:54:02.120 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011150 |  | EACOP-PS5-60-26-0184 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-26 - Instrument Air Compressor Skid |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-13T14:55:36.930 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T10:54:00.000
PL-011151 |  | EACOP-PS5-60-26-0184 | B | P | 18.2:Paint touchup to be done | CPP AGI | PS5-60-26 - Instrument Air Compressor Skid |  | Completed |  | Paint touchup to be done in damaged area | 2026-07-13T14:56:16.957 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T10:54:42.000
PL-011152 |  | EACOP-PS5-60-27-0185 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-07-13T15:06:09.623 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T10:55:14.000
PL-011153 |  | EACOP-PS5-60-27-0185 | B | P | 18.1:Sleeve Penetration to be install | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Completed |  | Sleeve Penetration to be install with PS-60-UA-5100/TP-314 | 2026-07-13T15:07:00.213 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T10:56:10.000
PL-011154 |  | EACOP-PS5-60-27-0185 | B | P | 18.2:Paint touchup to be done | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Completed |  | Paint touchup to be done in damaged area | 2026-07-13T15:08:39.560 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T10:56:36.000
PL-011158 |  | EACOP-PS5-71-18-0326 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-14T05:57:20.777 | Bhagavath, sangeeth | PS5 - Milestone F | 2026-08-30T13:56:57.000
PL-011159 |  | EACOP-PS5-71-18-0326 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Completed |  | Paint touchup to be done | 2026-07-14T05:59:11.400 | Bhagavath, sangeeth | PS5 - Milestone F | 2026-08-30T13:57:26.000
PL-011207 |  | EACOP-PS5-71-18-0326 | B | P | 18.2:cladding penetration to be install | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Completed |  | Cladding penetration to be install | 2026-07-14T14:34:08.017 | Bhagavath, sangeeth | PS5 - Milestone F | 2026-08-30T14:03:13.000
PL-011209 | PS5-71-BE-0001B-CL01 |  | A | E | Cable is damaged | CPP AGI | PS5-71-07 - Crude Fuel Separation Module (UCP) |  | Originated |  | Replacement of the cable | 2026-07-14T17:39:14.220 | Kashinde, Severine | PS5 - Milestone H
PL-011313 |  | EACOP-PS5-25-02-0351 | B | P | 18:Electrical heat tracing to be done | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Electrical heat tracing to be done | 2026-07-16T08:09:02.363 | Bhagavath, sangeeth | PS5 - Milestone H
PL-011314 |  | EACOP-PS5-25-02-0351 | B | P | 18.1:Insulatoin to be done | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Insulatoin to be done | 2026-07-16T08:10:25.723 | Bhagavath, sangeeth | PS5 - Milestone H
PL-011315 |  | EACOP-PS5-25-02-0351 | B | P | 18.2:Paint touchup to be done | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Paint touchup to be done | 2026-07-16T08:11:12.060 | Bhagavath, sangeeth | PS5 - Milestone H
PL-011317 |  | EACOP-PS5-25-03-0352 | B | P | 18:Electrical heat tracing to be done | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Electrical heat tracing to be done | 2026-07-16T08:15:26.643 | Bhagavath, sangeeth | PS5 - Milestone H
PL-011318 |  | EACOP-PS5-25-03-0352 | B | P | 18.1:Insulatoin to be done | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Insulatoin to be done | 2026-07-16T08:16:03.003 | Bhagavath, sangeeth | PS5 - Milestone H
PL-011319 |  | EACOP-PS5-25-03-0352 | B | P | 18.2:Paint touchup to be done | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Paint touchup to be done | 2026-07-16T08:16:34.343 | Bhagavath, sangeeth | PS5 - Milestone H
PL-011320 |  | EACOP-PS5-25-04-0353 | B | P | 18:Electrical heat tracing to be done | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Electrical heat tracing to be done | 2026-07-16T08:19:27.617 | Bhagavath, sangeeth | PS5 - Milestone H
PL-011321 |  | EACOP-PS5-25-04-0353 | B | P | 18.1:Insulatoin to be done | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Insulatoin to be done | 2026-07-16T08:20:03.817 | Bhagavath, sangeeth | PS5 - Milestone H
PL-011323 |  | EACOP-PS5-25-04-0353 | B | P | 18.2:Paint touchup to be done | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Paint touchup to be done | 2026-07-16T08:20:34.763 | Bhagavath, sangeeth | PS5 - Milestone H
PL-011328 |  | EACOP-PS5-60-24-0175 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-16T09:01:24.630 | Bhagavath, sangeeth | PS5 - Milestone E | 2026-08-30T14:03:48.000
PL-011330 |  | EACOP-PS5-60-24-0175 | B | P | 18.1:Pickling & Passivation to be done in rusted area | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  | Pickling & Passivation to be done in rusted area | 2026-07-16T09:01:58.220 | Bhagavath, sangeeth | PS5 - Milestone E
PL-011331 |  | EACOP-PS5-60-24-0443 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-16T09:05:33.973 | Bhagavath, sangeeth | PS5 - Milestone E | 2026-08-30T14:04:09.000
PL-011332 |  | EACOP-PS5-60-24-0443 | B | P | 18.1:Pickling & Passivation to be done in rusted area | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  | Pickling & Passivation to be done in rusted area | 2026-07-16T09:06:10.843 | Bhagavath, sangeeth | PS5 - Milestone E
PL-011333 |  | EACOP-PS5-71-02-0431 | B | P | 18:Valve Commodity code RLMU to be done | CPP AGI | PS5-71-02 - CFO Allocation Metering Package |  | Originated |  | Valve Commodity code RLMU to be done | 2026-07-16T10:25:36.110 | Bhagavath, sangeeth | PS5 - Milestone H
PL-011334 |  | EACOP-PS5-71-02-0431 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-71-02 - CFO Allocation Metering Package |  | Originated |  | Paint touchup to be done | 2026-07-16T10:26:14.123 | Bhagavath, sangeeth | PS5 - Milestone H
PL-011335 |  | EACOP-PS5-28-04-0089 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-16T10:54:53.897 | Bhagavath, sangeeth | PS5 - Milestone E
PL-011336 |  | EACOP-PS5-28-04-0089 | B | P | 18.1:Pickling & Passivation to be done in rusted area | CPP AGI | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  | Pickling & Passivation to be done in rusted area | 2026-07-16T10:55:39.873 | Bhagavath, sangeeth | PS5 - Milestone E
PL-011337 |  | EACOP-PS5-28-07-0377 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-28-07 - Open Drains (OD2) |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-16T11:05:58.150 | Bhagavath, sangeeth | PS5 - Milestone G | 2026-08-30T14:04:31.000
PL-011338 |  | EACOP-PS5-28-07-0377 | B | P | 18.1:Pickling & Passivation to be done in rusted area | CPP AGI | PS5-28-07 - Open Drains (OD2) |  | Originated |  | Pickling & Passivation to be done in rusted area | 2026-07-16T11:06:51.570 | Bhagavath, sangeeth | PS5 - Milestone G
PL-011339 |  | EACOP-PS5-28-07-0377 | B | P | 18.2:Pickling & Passivation to be done in rusted area | CPP AGI | PS5-28-07 - Open Drains (OD2) |  | Originated |  | Pickling & Passivation to be done in rusted area | 2026-07-16T11:07:22.960 | Bhagavath, sangeeth | PS5 - Milestone G
PL-011340 |  | EACOP-PS5-60-25-0181 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-16T11:13:01.420 | Bhagavath, sangeeth | PS5 - Milestone E | 2026-08-30T14:04:52.000
PL-011341 |  | EACOP-PS5-60-25-0181 | B | P | 18.1:Pickling & Passivation to be done in rusted area | CPP AGI | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | Pickling & Passivation to be done in rusted area | 2026-07-16T11:13:43.703 | Bhagavath, sangeeth | PS5 - Milestone E
PL-011342 |  | EACOP-PS5-28-07-0102 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-28-07 - Open Drains (OD2) |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-16T11:29:37.010 | Bhagavath, sangeeth | PS5 - Milestone G
PL-011343 |  | EACOP-PS5-28-07-0102 | B | P | 18.1:Pickling & Passivation to be done in rusted area | CPP AGI | PS5-28-07 - Open Drains (OD2) |  | Originated |  | Pickling & Passivation to be done in rusted area | 2026-07-16T11:30:28.693 | Bhagavath, sangeeth | PS5 - Milestone G
PL-011344 |  | EACOP-PS5-74-03-0338 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-74-03 - Nitrogen Receiver |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-16T11:35:01.473 | Bhagavath, sangeeth | PS5 - Milestone F
PL-011345 |  | EACOP-PS5-74-03-0338 | B | P | 18.1:CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-74-03 - Nitrogen Receiver |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-16T11:35:43.863 | Bhagavath, sangeeth | PS5 - Milestone F
PL-011346 |  | EACOP-PS5-74-03-0338 | B | P | 18.2:Paint Touch up to be done | CPP AGI | PS5-74-03 - Nitrogen Receiver |  | Originated |  | Paint Touch up to be done | 2026-07-16T11:36:22.260 | Bhagavath, sangeeth | PS5 - Milestone F
PL-011347 |  | EACOP-PS5-28-07-0098 | B | P | 18:Paint touch up to be done | CPP AGI | PS5-28-07 - Open Drains (OD2) |  | Originated |  | Paint touch up to be done | 2026-07-16T13:06:01.300 | Bhagavath, sangeeth | PS5 - Milestone G
PL-011348 |  | EACOP-PS5-60-01-0151 | B | P | 18:CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-16T13:12:57.883 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011349 |  | EACOP-PS5-60-01-0151 | B | P | 18.1:Hose Connection FM to be Done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Hose Connection FM to be Done | 2026-07-16T13:13:43.970 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011350 |  | EACOP-PS5-60-01-0151 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-01 - Power Generation Package A |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-16T13:14:22.450 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:31:39.000
PL-011351 |  | EACOP-PS5-60-01-0151 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Completed |  | Paint touch up to be done | 2026-07-16T13:15:05.370 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T10:57:12.000
PL-011352 |  | EACOP-PS5-60-24-0178 | B | P | 18:CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-16T13:22:30.073 | Bhagavath, sangeeth | PS5 - Milestone E
PL-011353 |  | EACOP-PS5-60-24-0178 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-16T13:23:29.370 | Bhagavath, sangeeth | PS5 - Milestone E | 2026-08-30T14:05:30.000
PL-011354 |  | EACOP-PS5-60-24-0178 | B | P | 18.2:Pickling & passivation to be done in rusted area | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  | Pickling & passivation to be done in rusted area | 2026-07-16T13:24:49.660 | Bhagavath, sangeeth | PS5 - Milestone E
PL-011355 |  | EACOP-PS5-71-20-0329 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-16T13:37:04.530 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-30T14:05:48.000
PL-011356 |  | EACOP-PS5-71-20-0329 | B | P | 18.1:Paint touch up to be done | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Completed |  | Paint touch up to be done | 2026-07-16T13:38:09.203 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-30T14:06:14.000
PL-011408 |  | EACOP-PS5-60-01-0152 | B | P | 18:Hose Connection FM to be Done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Hose Connection FM to be Done | 2026-07-17T12:49:13.800 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011409 |  | EACOP-PS5-60-01-0152 | B | P | 18.1:Wear pad support holes shall be sealed. | CPP AGI | PS5-60-01 - Power Generation Package A |  | Completed |  | Wear pad support holes shall be sealed. | 2026-07-17T12:49:51.133 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-10T14:31:28.000
PL-011410 |  | EACOP-PS5-60-01-0152 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-01 - Power Generation Package A |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-17T12:50:26.160 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:32:12.000
PL-011411 |  | EACOP-PS5-60-01-0152 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Completed |  | Paint touch up to be done | 2026-07-17T12:50:57.737 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T10:58:06.000
PL-011412 |  | EACOP-PS5-60-01-0153 | B | P | 18:CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | 1" Valve CTR commodity code to be add. RLMU to be done | 2026-07-17T12:56:26.427 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011414 |  | EACOP-PS5-60-01-0153 | B | P | 18.1:Hose Connection FM to be Done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Hose Connection Flange management to be Done | 2026-07-17T12:57:18.120 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011416 |  | EACOP-PS5-60-01-0153 | B | P | 18.2:Wear pad support holes shall be sealed. | CPP AGI | PS5-60-01 - Power Generation Package A |  | Completed |  | Wear pad support holes shall be sealed. | 2026-07-17T12:57:56.997 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-10T14:33:35.000
PL-011418 |  | EACOP-PS5-60-01-0153 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-01 - Power Generation Package A |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-17T12:58:36.263 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:32:44.000
PL-011419 |  | EACOP-PS5-60-01-0153 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Completed |  | Paint touch up to be done | 2026-07-17T12:59:06.050 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T10:58:37.000
PL-011420 |  | EACOP-PS5-60-04-0154 | B | P | 18:CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | 1" Valve CTR commodity code to be add. RLMU to be done | 2026-07-17T13:04:54.340 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011421 |  | EACOP-PS5-60-04-0154 | B | P | 18.1:Hose Connection FM to be Done | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Hose Connection FM to be Done | 2026-07-17T13:05:37.880 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011422 |  | EACOP-PS5-60-04-0154 | B | P | 18.2:Wear pad support holes shall be sealed. | CPP AGI | PS5-60-04 - Power Generation Package B |  | Completed |  | Wear pad support holes shall be sealed. | 2026-07-17T13:06:25.497 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-10T14:35:15.000
PL-011423 |  | EACOP-PS5-60-04-0154 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-04 - Power Generation Package B |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-17T13:07:08.567 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:33:12.000
PL-011424 |  | EACOP-PS5-60-04-0154 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Paint touch up to be done | 2026-07-17T13:07:36.173 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011425 |  | EACOP-PS5-60-04-0155 | B | P | 18:Hose Connection FM to be Done | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Hose Connection FM to be Done | 2026-07-17T13:13:03.490 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011426 |  | EACOP-PS5-60-04-0155 | B | P | 18.1:Wear pad support holes shall be sealed | CPP AGI | PS5-60-04 - Power Generation Package B |  | Completed |  | Wear pad support holes shall be sealed | 2026-07-17T13:13:38.623 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-10T14:36:22.000
PL-011427 |  | EACOP-PS5-60-04-0155 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-04 - Power Generation Package B |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-17T13:14:10.907 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T10:59:22.000
PL-011428 |  | EACOP-PS5-60-04-0155 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-04 - Power Generation Package B |  | Completed |  | Paint touch up to be done | 2026-07-17T13:14:40.760 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T10:59:47.000
PL-011435 |  | EACOP-PS5-60-04-0156 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-17T13:22:22.797 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011437 |  | EACOP-PS5-60-04-0156 | B | P | 18.1:Hose Connection FM to be Done | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Hose Connection FM to be Done | 2026-07-17T13:23:01.583 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011438 |  | EACOP-PS5-60-04-0156 | B | P | 18.2:Wear pad support holes shall be sealed. | CPP AGI | PS5-60-04 - Power Generation Package B |  | Completed |  | Wear pad support holes shall be sealed. | 2026-07-17T13:23:34.277 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-10T14:37:21.000
PL-011440 |  | EACOP-PS5-60-04-0156 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-04 - Power Generation Package B |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-17T13:24:03.447 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:33:37.000
PL-011441 |  | EACOP-PS5-60-04-0156 | B | P | 18.4:Cladding Penetration to be Fix | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Cladding Penetration to be Fix | 2026-07-17T13:24:32.343 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011443 |  | EACOP-PS5-60-04-0156 | B | P | 18.5:Paint touch up to be done | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Paint touch up to be done | 2026-07-17T13:25:02.320 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011447 |  | EACOP-PS5-71-22-0333 | B | P | 18:1" valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-17T13:32:25.610 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011448 |  | EACOP-PS5-71-22-0333 | B | P | 18.1:Valve Handle missing | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Completed |  | MissingValve Handle to be install | 2026-07-17T13:33:19.197 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-10T14:38:55.000
PL-011449 |  | EACOP-PS5-71-22-0333 | B | P | 18.2:PR01 (PS-71493) to be install | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Completed |  | PR01 (PS-71493) to be install | 2026-07-17T13:34:16.340 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-10T14:40:19.000
PL-011450 |  | EACOP-PS5-71-22-0333 | B | P | 18.3:PR01 (PS-504481) to be install | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Completed |  | PR01 (PS-504481) to be install | 2026-07-17T13:34:54.100 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-10T14:41:27.000
PL-011451 |  | EACOP-PS5-71-22-0333 | B | P | 18.4:Wear pad support holes shall be sealed | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Completed |  | Wear pad support holes shall be sealed | 2026-07-17T13:36:17.800 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-10T14:42:11.000
PL-011452 |  | EACOP-PS5-71-22-0333 | B | P | 18.5:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-17T13:37:26.007 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:13:22.000
PL-011453 |  | EACOP-PS5-71-22-0333 | B | P | 18.6:Cladding Penetration to be Fix | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | Cladding Penetration to be Fix | 2026-07-17T13:38:10.603 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011454 |  | EACOP-PS5-71-22-0333 | B | P | 18.7:Paint touch up to be done | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Completed |  | Paint touch up to be done | 2026-07-17T13:38:46.767 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:14:03.000
PL-011562 |  | EACOP-PS5-60-49-0223 | B | P | 18:PR01 to be install | CPP AGI | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A |  | Completed |  | TZ-MID-68-WPR2-208360 & TZ-MID-68-WPR2-208521 PR01 to be install | 2026-07-18T08:17:35.100 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-10T14:43:53.000
PL-011563 |  | EACOP-PS5-60-49-0223 | B | P | 18.1:Hose Connection FM to be Done | CPP AGI | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A |  | Originated |  | TZ-MID-68-WPR2-208360 & TZ-MID-68-WPR2-208382 Hose Connection FM to be Done | 2026-07-18T08:19:01.043 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011564 |  | EACOP-PS5-60-49-0223 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-18T08:24:04.980 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:33:53.000
PL-011565 |  | EACOP-PS5-60-49-0223 | B | P | 18.3:Floor penetration gratings shall be fixed properly. | CPP AGI | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A |  | Originated |  | Floor penetration gratings shall be fixed properly. | 2026-07-18T08:24:35.463 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011566 |  | EACOP-PS5-60-49-0223 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A |  | Completed |  | Paint touch up to be done | 2026-07-18T08:25:06.937 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:45:56.000
PL-011567 |  | EACOP-PS5-60-56-0236 | B | P | 18:PR01 to be install | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Completed |  | TZ-MID-68-WPR2-207904 PR01 to be install | 2026-07-18T08:31:26.687 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-10T14:45:11.000
PL-011568 |  | EACOP-PS5-60-56-0236 | B | P | 18.1:1" valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-18T08:32:16.057 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011569 |  | EACOP-PS5-60-56-0236 | B | P | 18.2:Floor & Clading penetration gratings shall be fixed properly. | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Floor & Clading penetration gratings shall be fixed properly. | 2026-07-18T08:33:03.267 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011570 |  | EACOP-PS5-60-56-0236 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-07-18T08:34:13.997 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:34:01.000
PL-011571 |  | EACOP-PS5-60-56-0236 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Paint touch up to be done | 2026-07-18T08:34:46.070 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011572 |  | EACOP-PS5-60-58-0238 | B | P | 18:1" valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-18T08:38:16.230 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011573 |  | EACOP-PS5-60-58-0238 | B | P | 18.1:Floor & Clading penetration gratings shall be fixed properly. | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | :Floor & Clading penetration gratings shall be fixed properly. | 2026-07-18T08:39:08.300 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011574 |  | EACOP-PS5-60-58-0238 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-18T08:39:55.870 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:34:32.000
PL-011575 |  | EACOP-PS5-60-58-0238 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Paint touch up to be done | 2026-07-18T08:40:35.760 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011601 |  | EACOP-PS5-60-35-0195 | B | P | 18:CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-35 - Injector Tip Cooling Module A |  | Originated |  | 1" valve CTR commodity code to be add. RLMU to be done | 2026-07-18T12:57:45.953 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011602 |  | EACOP-PS5-60-35-0195 | B | P | 18.1:Hose Connection FM to be Done | CPP AGI | PS5-60-35 - Injector Tip Cooling Module A |  | Originated |  | PS5-60-UR--8100A_TP-786 & TP-785 Hose Connection FM to be Done | 2026-07-18T12:58:38.583 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011604 |  | EACOP-PS5-60-35-0195 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-35 - Injector Tip Cooling Module A |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-18T12:59:45.197 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:35:13.000
PL-011606 |  | EACOP-PS5-60-35-0195 | B | P | 18.3:Floor Penetration Gratings to be Fixed | CPP AGI | PS5-60-35 - Injector Tip Cooling Module A |  | Originated |  | Floor Penetration Gratings to be Fixed | 2026-07-18T13:01:15.273 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011607 |  | EACOP-PS5-60-35-0195 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-60-35 - Injector Tip Cooling Module A |  | Originated |  | Paint touch up to be done | 2026-07-18T13:02:13.063 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011619 |  | EACOP-PS5-60-36-0197 | B | P | 18:CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-36 - Injector Tip Cooling Module B |  | Originated |  | 1" Valve CTR commodity code to be add. RLMU to be done | 2026-07-18T13:09:16.530 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011620 |  | EACOP-PS5-60-36-0197 | B | P | 18.1:Hose Connection FM to be Done | CPP AGI | PS5-60-36 - Injector Tip Cooling Module B |  | Originated |  | PS5-60-UR--8100B_ TP-806 &TP-807 Hose Connection FM to be Done | 2026-07-18T13:10:51.367 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011622 |  | EACOP-PS5-60-36-0197 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-36 - Injector Tip Cooling Module B |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-18T13:12:28.647 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:35:47.000
PL-011623 |  | EACOP-PS5-60-36-0197 | B | P | 18.3:Floor Penetration Gratings to be Fixed | CPP AGI | PS5-60-36 - Injector Tip Cooling Module B |  | Originated |  | Floor Penetration Gratings to be Fixed | 2026-07-18T13:12:58.067 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011624 |  | EACOP-PS5-60-36-0197 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-60-36 - Injector Tip Cooling Module B |  | Originated |  | Paint touch up to be done | 2026-07-18T13:13:39.697 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011626 |  | EACOP-PS5-60-56-0237 | B | P | 18:1" ValveCTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-18T13:17:42.610 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011628 |  | EACOP-PS5-60-56-0237 | B | P | 18.1:Hose Connection FM to be Done | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | PS5-60-UR-8100A_TP-783 & TP-784 Hose Connection FM to be Done | 2026-07-18T13:18:39.653 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011629 |  | EACOP-PS5-60-56-0237 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-18T13:19:38.747 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:35:26.000
PL-011631 |  | EACOP-PS5-60-56-0237 | B | P | 18.3:Floor Penetration Gratings to be Fixed | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Floor Penetration Gratings to be Fixed | 2026-07-18T13:20:16.423 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011632 |  | EACOP-PS5-60-56-0237 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Completed |  | Paint touch up to be done | 2026-07-18T13:20:46.010 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:46:31.000
PL-011635 |  | EACOP-PS5-60-58-0239 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-18T13:24:24.947 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011650 |  | EACOP-PS5-60-58-0239 | B | P | 18.1:Hose Connection FM to be Done | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | PS5-60-UR-8100B_TP-804 & TP-805 Hose Connection FM to be Done | 2026-07-18T13:25:15.217 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011652 |  | EACOP-PS5-60-58-0239 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-18T13:26:11.943 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:35:51.000
PL-011653 |  | EACOP-PS5-60-58-0239 | B | P | 18.3:Floor Penetration Gratings to be Fixed | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Floor Penetration Gratings to be Fixed | 2026-07-18T13:26:47.430 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011654 |  | EACOP-PS5-60-58-0239 | B | P | 18.4:Floor Penetration Gratings to be Fixed | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Floor Penetration Gratings to be Fixed | 2026-07-18T13:27:21.290 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011655 |  | EACOP-PS5-60-58-0239 | B | P | 18.5:Paint touch up to be done | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Completed |  | Paint touch up to be done | 2026-07-18T13:28:37.267 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:46:53.000
PL-011656 |  | EACOP-PS5-71-20-0358 | B | P | 18:Instruments to be Install | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Originated |  | PS5-71-LIT-1202A,PS5-71-LIT-1202B,PS5-71-LIT-1201A & PS5-71-LIT-1201B Instruments to be Install | 2026-07-18T13:40:52.400 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011659 |  | EACOP-PS5-71-20-0358 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-18T13:42:56.730 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-30T14:06:39.000
PL-011660 |  | EACOP-PS5-71-20-0358 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Completed |  | Paint touch up to be done | 2026-07-18T13:44:41.887 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-30T14:07:13.000
PL-011846 |  | EACOP-PS5-60-50-0225 | B | P | 18:1" CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-20T11:20:42.247 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011847 |  | EACOP-PS5-60-50-0225 | B | P | 18.1:Hose Connection FM to be Done | CPP AGI | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B |  | Originated |  | PS5-60-UR-8100B_TP-810& TP-811 Hose Connection FM to be Done | 2026-07-20T11:21:23.957 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011848 |  | EACOP-PS5-60-50-0225 | B | P | 18.2:PR01 Bottom shim to be sealed. | CPP AGI | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B |  | Completed |  | PR01 Bottom shim to be sealed. | 2026-07-20T11:22:34.427 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-10T14:47:34.000
PL-011849 |  | EACOP-PS5-60-50-0225 | B | P | 18.3:Floor Penetration Gratings to be Fixed. | CPP AGI | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B |  | Originated |  | Floor Penetration Gratings to be Fixed. | 2026-07-20T11:23:29.737 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011850 |  | EACOP-PS5-60-50-0225 | B | P | 18.4:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-20T11:24:01.483 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:36:16.000
PL-011851 |  | EACOP-PS5-60-50-0225 | B | P | 18.5:Paint touch up to be done | CPP AGI | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B |  | Originated |  | Paint touch up to be done | 2026-07-20T11:24:42.093 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011852 |  | EACOP-PS5-60-70-0254 | B | P | 18:Provide shim as required | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | Provide shim as required | 2026-07-20T11:29:02.240 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:47:29.000
PL-011853 |  | EACOP-PS5-60-70-0254 | B | P | 18.1:PR01 (PS-58240) to be installed and sealed | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | PR01 (PS-58240) to be installed and sealed | 2026-07-20T11:34:48.630 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:48:07.000
PL-011854 |  | EACOP-PS5-60-70-0254 | B | P | 18.2:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-20T11:35:19.417 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011855 |  | EACOP-PS5-60-70-0254 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-20T11:36:03.043 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:36:15.000
PL-011856 |  | EACOP-PS5-60-70-0254 | B | P | 18.4:Through wall penetration to be Fixed. | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Through wall penetration to be Fixed. | 2026-07-20T11:36:36.520 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011857 |  | EACOP-PS5-60-70-0254 | B | P | 18.5:Paint touch up to be done | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | Paint touch up to be done | 2026-07-20T11:37:08.657 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:48:29.000
PL-011858 |  | EACOP-PS5-60-70-0255 | B | P | 18:Provide shim as required | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | Provide shim as required | 2026-07-20T11:40:56.960 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:36:58.000
PL-011859 |  | EACOP-PS5-60-70-0255 | B | P | 18.1:Bottom shim to be sealed. | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | Bottom shim to be sealed. | 2026-07-20T11:41:58.777 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:37:44.000
PL-011860 |  | EACOP-PS5-60-70-0255 | B | P | 18.2:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-20T11:43:06.020 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011861 |  | EACOP-PS5-60-70-0255 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-20T11:43:53.170 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:38:17.000
PL-011862 |  | EACOP-PS5-60-70-0255 | B | P | 18.4:Through wall penetration to be Fixed. | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Through wall penetration to be Fixed. | 2026-07-20T11:44:50.800 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011863 |  | EACOP-PS5-60-70-0255 | B | P | 18.5:Paint touch up to be done | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Paint touch up to be done | 2026-07-20T11:45:27.417 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011864 |  | EACOP-PS5-60-71-0260 | B | P | 18:Provide shim as required | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | Provide shim as required | 2026-07-20T11:55:56.800 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T11:00:38.000
PL-011865 |  | EACOP-PS5-60-71-0260 | B | P | 18.1:1" valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | 1" valve CTR commodity code to be add. RLMU to be done | 2026-07-20T11:57:04.620 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011866 |  | EACOP-PS5-60-71-0260 | B | P | 18.2:Through wall penetration to be Fixed. | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | Through wall penetration to be Fixed. | 2026-07-20T12:01:19.033 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T11:01:21.000
PL-011867 |  | EACOP-PS5-60-71-0260 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-20T12:02:22.483 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T11:01:53.000
PL-011868 |  | EACOP-PS5-60-71-0260 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | Paint touch up to be done | 2026-07-20T12:02:55.097 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T11:02:21.000
PL-011869 |  | EACOP-PS5-60-71-0261 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | 1" Valve CTR commodity code to be add. RLMU to be done | 2026-07-20T12:07:00.593 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011870 |  | EACOP-PS5-60-71-0261 | B | P | 18.1:Provide shim as required | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | Provide shim as required | 2026-07-20T12:07:53.820 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T11:02:59.000
PL-011871 |  | EACOP-PS5-60-71-0261 | B | P | 18.2:Through wall penetration to be Fixed. | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | Through wall penetration to be Fixed. | 2026-07-20T12:08:55.370 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T11:04:00.000
PL-011872 |  | EACOP-PS5-60-71-0261 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-20T12:10:12.497 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T11:05:00.000
PL-011873 |  | EACOP-PS5-60-71-0261 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | Paint touch up to be done | 2026-07-20T12:10:49.227 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T11:05:35.000
PL-011925 |  | EACOP-PS5-60-71-0260 | B | P | 18.5: S8 GL01 (PS-61260) GAP to be verify after PTFE installed. | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | S8 GL01 (PS-61260) Support GAP to be verify after PTFE installed. | 2026-07-21T06:34:59.173 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T11:06:35.000
PL-011929 |  | EACOP-PS5-60-71-0256 | B | P | 18:1" valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-21T10:22:03.110 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011930 |  | EACOP-PS5-60-71-0256 | B | P | 18.1:TZ-MID-68-WPR2-207040 F6 & TZ-MID-68-WPR2-207034 F5 Stud bolt protrusion is less than 2 threads | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | Stud bolt protrusion is less than 2 threads | 2026-07-21T10:23:22.393 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011931 |  | EACOP-PS5-60-71-0256 | B | P | 18.2:S16 (PS-61210)-GL01 gap shall be verified after PTFE pad installation | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | Drg No TZ-MID-68-WPR2-207042 S16 (PS-61210) - GL01 gap shall be verified after PTFE pad installatio | 2026-07-21T10:25:34.173 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:36:50.000
PL-011932 |  | EACOP-PS5-60-71-0256 | B | P | 18.3:PS5-60-TX-41200A/TP-614 & TP-600, PS5-60-UR-8100B-TP-800 & TP-802 Equpiment connection Flange Management to be done | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | Equpiment connection Flange Management to be done | 2026-07-21T10:28:25.713 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011933 |  | EACOP-PS5-60-71-0256 | B | P | 18.4:PS5-60-TG-0006B F9 - Stud bolt protrusion is less than 2 threads | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | PS5-60-TG-0006B F9 - Stud bolt protrusion is less than 2 threads | 2026-07-21T10:32:28.573 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011934 |  | EACOP-PS5-60-71-0256 | B | P | 18.5:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-21T10:34:34.940 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:37:16.000
PL-011935 |  | EACOP-PS5-60-71-0256 | B | P | 18.6:Paint touch up to be done | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | Paint touch up to be done | 2026-07-21T10:35:26.347 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:48:50.000
PL-011936 |  | EACOP-PS5-60-71-0258 | B | P | 18:Drg no TZ-MID-68-WPR2-207045 S10 (PS-61220)- GL01 gap shall be verified after PTFE pad installation | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | Drg no TZ-MID-68-WPR2-207045 S10 (PS-61220)- GL01 gap shall be verified after PTFE pad installation | 2026-07-21T10:40:28.037 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:37:58.000
PL-011937 |  | EACOP-PS5-60-71-0258 | B | P | 18.1:Drg No TZ-MID-68-WPR2-207045 S9 (PS-61218)-PR01 to be install | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | S9 (PS-61218)-PR01 to be install | 2026-07-21T10:42:39.387 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:49:12.000
PL-011938 |  | EACOP-PS5-60-71-0258 | B | P | 18.2:PS5-60-TG-0007B F-7 Stud bolt protrusion is less than 2 threads | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | PS5-60-TG-0007B F-7 Stud bolt protrusion is less than 2 threads | 2026-07-21T10:44:05.827 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011939 |  | EACOP-PS5-60-71-0258 | B | P | 18.3:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-21T10:45:07.380 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011940 |  | EACOP-PS5-60-71-0258 | B | P | 18.4:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-21T10:46:18.323 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:38:30.000
PL-011941 |  | EACOP-PS5-60-71-0258 | B | P | 18.5:Paint touch up to be done | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | Paint touch up to be done | 2026-07-21T10:46:44.847 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:49:30.000
PL-011942 |  | EACOP-PS5-60-71-0259 | B | P | 18:Drg no TZ-MID-68-WPR2-207053 S14 (PS-61239,61236,61243)- GL01 gap shall be verified after PTFE pad installation | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | S14 (PS-61239,61236,61243)- GL01 gap shall be verified after PTFE pad installation | 2026-07-21T11:13:32.470 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:40:01.000
PL-011943 |  | EACOP-PS5-60-71-0259 | B | P | 18.1:Drg No TZ-MID-68-WPR2-207053 S13(PS-61236, 61237, 61242,61243,61244) - PR01 To be install | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | 3 S13(PS-61236, 61237, 61242,61243,61244) - PR01 To be install | 2026-07-21T11:15:01.430 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:50:39.000
PL-011944 |  | EACOP-PS5-60-71-0259 | B | P | 18.2:PS5-60-TG-0008B- F-8 Stud bolt protrusion is less than 2 threads | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | PS5-60-TG-0008B- F-8 Stud bolt protrusion is less than 2 threads | 2026-07-21T11:16:17.453 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011945 |  | EACOP-PS5-60-71-0259 | B | P | 18.3:Drg No TZ-MID-68-WPR2-207059,S4(PS-61252)-Shoe stiffener sharp edges shall be ground smooth. | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | Drg No TZ-MID-68-WPR2-207059,S4(PS-61252)-Shoe stiffener sharp edges shall be ground smooth. | 2026-07-21T11:17:21.880 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:53:45.000
PL-011946 |  | EACOP-PS5-60-71-0259 | B | P | 18.4:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-21T11:19:03.347 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011947 |  | EACOP-PS5-60-71-0259 | B | P | 18.5:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-21T11:19:50.887 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:40:33.000
PL-011948 |  | EACOP-PS5-60-71-0259 | B | P | 18.6:Paint touch up to be done | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | Paint touch up to be done | 2026-07-21T11:20:48.640 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:54:20.000
PL-011949 |  | EACOP-PS5-71-22-0334 | B | P | 18:Drg No TZ-MID-68-WPR2-20773,F-02 -Flange Management to be done | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | Drg No TZ-MID-68-WPR2-20773,F-02 -Flange Management to be done | 2026-07-21T11:25:42.600 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011950 |  | EACOP-PS5-71-22-0334 | B | P | 18.1:Drg No TZ-MID-68-WPR2-207735, S13(PS-74840)-PR01 to be install | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Completed |  | S13(PS-74840)-PR01 to be install | 2026-07-21T11:27:14.347 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:14:50.000
PL-011951 |  | EACOP-PS5-71-22-0334 | B | P | 18.2:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-21T11:28:42.227 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011952 |  | EACOP-PS5-71-22-0334 | B | P | 18.3:Through Wall Penetration to be Fixed. | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | Through Wall Penetration to be Fixed. | 2026-07-21T11:29:40.253 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011953 |  | EACOP-PS5-71-22-0334 | B | P | 18.4:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-21T11:31:25.650 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:15:25.000
PL-011954 |  | EACOP-PS5-71-22-0334 | B | P | 18.5:Paint touch up to be done | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Completed |  | Paint touch up to be done | 2026-07-21T11:31:57.410 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:15:59.000
PL-011955 |  | EACOP-PS5-71-22-0336 | B | P | 18:-TZ-MID-68-WPR2-208152, F2- Flange Management report to be Closed | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  |  | 2026-07-21T11:38:10.993 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011956 |  | EACOP-PS5-71-22-0336 | B | P | 18.1:Drg No TZ-MID-68-WPR2-208152, S14(PS-86745)- LS01 one-side gap to be adjusted | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | S14(PS-86745)- LS01 one-side gap to be adjusted | 2026-07-21T11:40:49.090 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011957 |  | EACOP-PS5-71-22-0336 | B | P | 18.2:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-21T11:43:12.843 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011958 |  | EACOP-PS5-71-22-0336 | B | P | 18.3:Through Wall Penetration to be Fixed. | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | Through Wall Penetration to be Fixed. | 2026-07-21T11:44:07.670 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011959 |  | EACOP-PS5-71-22-0336 | B | P | 18.4:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-21T11:45:03.333 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011960 |  | EACOP-PS5-71-22-0336 | B | P | 18.5:Paint touch up to be done | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | Paint touch up to be done | 2026-07-21T11:45:41.023 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011973 |  | EACOP-PS5-60-70-0250 | B | P | 18:TZ-MID-68-WPR2-206797 F5 & TZ-MID-68-WPR2-206806F6- Stud bolt protrusion is less than 2 threads | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | Stud bolt protrusion is less than 2 threads | 2026-07-21T13:21:55.900 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:39:31.000
PL-011974 |  | EACOP-PS5-60-70-0250 | B | P | 18.1:TZ-MID-68-WPR2-206798,Item 04-Gate Valve Handle Clash With Handrail | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Gate Valve Handle Clash With Handrail | 2026-07-21T13:23:43.440 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011979 |  | EACOP-PS5-60-70-0250 | B | P | 18.2:PS5-60-TG-0006A & PS5-60-TG-0005A - Stud bolt protrusion is less than 2 threads | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | Stud bolt protrusion is less than 2 threads | 2026-07-21T13:30:46.887 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:42:35.000
PL-011981 |  | EACOP-PS5-60-70-0250 | B | P | 18.3:PS5-60-UR-8100A-TP-770 & TP-781,PS5-60-TX-41100A-TP-598- Equpiment connection joint Flange Management to be done | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Equpiment connection joint Flange Management to be done | 2026-07-21T13:32:31.623 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011983 |  | EACOP-PS5-60-70-0250 | B | P | 18.4:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-21T13:37:15.890 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011984 |  | EACOP-PS5-60-70-0250 | B | P | 18.5:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-21T13:38:10.730 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:43:06.000
PL-011985 |  | EACOP-PS5-60-70-0250 | B | P | 18.6:Paint touch up to be done | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Paint touch up to be done | 2026-07-21T13:38:48.487 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011986 |  | EACOP-PS5-60-70-0252 | B | P | 18:S11 Drg No TZ-MID-68-WPR2-206810 (PS-51551)-GL01 gap shall be verified after PTFE pad installation | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | GL01 gap shall be verified after PTFE pad installation | 2026-07-21T13:43:29.880 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:43:53.000
PL-011987 |  | EACOP-PS5-60-70-0252 | B | P | 18.1:PS5-60-TG-0007A-Stud bolt protrusion is less than 2 threads | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | Stud bolt protrusion is less than 2 threads | 2026-07-21T13:45:09.133 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:44:40.000
PL-011988 |  | EACOP-PS5-60-70-0252 | B | P | 18.2:Drg No TZ-MID-68-WPR2-206798, Item 06- Gate valve handle operation is stiff | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Gate valve handle operation is stiff to be Rectify | 2026-07-21T13:46:14.263 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011989 |  | EACOP-PS5-60-70-0252 | B | P | 18.3:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-21T13:47:50.083 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011990 |  | EACOP-PS5-60-70-0252 | B | P | 18.4:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-21T13:48:41.510 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:45:43.000
PL-011991 |  | EACOP-PS5-60-70-0252 | B | P | 18.5:Paint touch up to be done | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Paint touch up to be done | 2026-07-21T13:49:47.897 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011992 |  | EACOP-PS5-60-70-0253 | B | P | 18:Drg No TZ-MID-68-WPR2-206817, S14 (PS-51614) & TZ-MID-68-WPR2-206818 S4 (PS-58097) -GL01 gap shall be verified after PTFE pad installation | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | GL01 gap shall be verified after PTFE pad installation | 2026-07-21T13:54:15.027 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:46:34.000
PL-011993 |  | EACOP-PS5-60-70-0253 | B | P | 18.1:PS5-60-TG-0008A - Stud bolt protrusion is less than 2 threads | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | Stud bolt protrusion is less than 2 threads | 2026-07-21T13:56:31.010 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:47:09.000
PL-011994 |  | EACOP-PS5-60-70-0253 | B | P | 18.2:TZ-MID-68-WPR2-2067888, ITEM 06 - Gate valve handle operation is stiff | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Gate valve handle operation is stiff to be rectify | 2026-07-21T13:57:49.380 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011995 |  | EACOP-PS5-60-70-0253 | B | P | 18.3:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-21T13:59:40.847 | Bhagavath, sangeeth | PS5 - Milestone B
PL-011996 |  | EACOP-PS5-60-70-0253 | B | P | 18.4:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-21T14:00:36.037 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:47:56.000
PL-011997 |  | EACOP-PS5-60-70-0253 | B | P | 18.5:Paint touch up to be done | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Paint touch up to be done | 2026-07-21T14:01:26.313 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012137 | PS5_PNC_Install |  | C | I | PS005-PNC-COW - PS5-04-PNC-0001 ICSS Network Cabinet to be installed | EITS | PS5-83-01 - EITS Building | 2026-09-02T13:33:33.000 | Closed |  |  | 2026-07-22T12:10:33.000 | Thao-my, Alexandre | PS5 - Milestone A | 2026-08-24T10:55:44.000
PL-012138 | PS5_PNC_NewCable |  | C | I | PS005-PNC-COW - PS5-04-PNC-0002 ICSS Network Cabinet to be installed | EITS | PS5-83-01 - EITS Building | 2026-09-02T13:36:43.000 | Closed |  |  | 2026-07-22T12:10:33.057 | Thao-my, Alexandre | PS5 - Milestone A | 2026-08-19T17:04:03.000
PL-012139 | PS5_INS |  | C | I | PS005-INS-COW - Cable TAG labels to be changed | EITS | PS5-83-01 - EITS Building |  | Completed |  |  | 2026-07-22T12:10:33.057 | Thao-my, Alexandre | PS5 - Milestone A | 2026-08-19T17:05:39.000
PL-012140 | PS5_ECS |  | C | E | PS005-ECS-COW - Cable TAG labels to be changed | EITS | PS5-83-01 - EITS Building |  | Completed |  |  | 2026-07-22T12:10:33.057 | Thao-my, Alexandre | PS5 - Milestone A | 2026-08-19T17:07:01.000
PL-012141 | PS5_ELE |  | C | E | PS005-ELE-COW - Cable TAG labels to be changed | EITS | PS5-83-01 - EITS Building |  | Completed |  |  | 2026-07-22T12:10:33.057 | Thao-my, Alexandre | PS5 - Milestone A | 2026-08-19T17:08:06.000
PL-012142 | PS5_TEL |  | C | T | PS005-TEL-COW - Cable TAG labels to be changed | EITS | PS5-83-01 - EITS Building |  | Completed |  |  | 2026-07-22T12:10:33.057 | Thao-my, Alexandre | PS5 - Milestone A | 2026-08-19T17:09:01.000
PL-012143 | PS5_HVAC |  | C | E | PS005-HVAC-COW - Cable TAG labels to be changed | EITS | PS5-83-01 - EITS Building |  | Completed |  |  | 2026-07-22T12:10:33.057 | Thao-my, Alexandre | PS5 - Milestone A | 2026-08-19T17:10:06.000
PL-012147 |  | EACOP-PS5-60-07-0158 | B | P | 18:PS5-60-UR-8100C_TP1035 - Hose Connection FM to be Done | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | PS5-60-UR-8100C_TP1035 - Hose Connection FM to be Done | 2026-07-22T12:36:59.940 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012148 |  | EACOP-PS5-60-07-0158 | B | P | 18.1:Drg No TZ-MID-68-WPR2-207275, S13 (PS-64776) - PR01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-07 - Power Generation Package C |  | Completed |  | S13 (PS-64776) - PR01 PTFE Isolation Pad to be Fixed. | 2026-07-22T12:38:26.030 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:48:20.000
PL-012149 |  | EACOP-PS5-60-07-0158 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-07 - Power Generation Package C |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-22T12:39:39.473 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:49:21.000
PL-012150 |  | EACOP-PS5-60-07-0158 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-07 - Power Generation Package C |  | Completed |  | Paint touch up to be done | 2026-07-22T12:40:12.013 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:50:05.000
PL-012151 |  | EACOP-PS5-60-07-0159 | B | P | 18:1" valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-22T12:48:04.120 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012152 |  | EACOP-PS5-60-07-0159 | B | P | 18.1:Drg No TZ-MID-68-WPR2-207266- Valve Handle Missing | CPP AGI | PS5-60-07 - Power Generation Package C |  | Completed |  | Valve Handle Missing to be Fiixed | 2026-07-22T12:50:25.103 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:51:12.000
PL-012153 |  | EACOP-PS5-60-07-0159 | B | P | 18.2:PS5-60-UR-8100C_TP1034- Hose Connection FM to be Done | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | Equpiment Hose Connection FM to be Done | 2026-07-22T12:52:10.190 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012154 |  | EACOP-PS5-60-07-0159 | B | P | 18.3:Cladding Penetration to be Fixed | CPP AGI | PS5-60-07 - Power Generation Package C |  | Completed |  | Cladding Penetration to be Fixed | 2026-07-22T12:53:53.533 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:51:56.000
PL-012155 |  | EACOP-PS5-60-07-0159 | B | P | 18.4:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-07 - Power Generation Package C |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-22T12:54:24.087 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:52:17.000
PL-012156 |  | EACOP-PS5-60-07-0159 | B | P | 18.5:Paint touch up to be done | CPP AGI | PS5-60-07 - Power Generation Package C |  | Completed |  | Paint touch up to be done | 2026-07-22T12:55:02.917 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:52:50.000
PL-012157 |  | EACOP-PS5-60-10-0160 | B | P | 18:1" valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-22T13:07:17.233 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012158 |  | EACOP-PS5-60-10-0160 | B | P | 18.1:TZ-MID-68-WPR2-207276 - Valve Handle Missing | CPP AGI | PS5-60-10 - Power Generation Package D |  | Completed |  | Valve Handle Missing to be Fixed | 2026-07-22T13:08:30.977 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:08:04.000
PL-012159 |  | EACOP-PS5-60-10-0160 | B | P | 18.2:PS5-60-UR-8100D_TP1036 & TP1037 - Hose Connection FM to be Done | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | Hose Connection joint FM to be Done | 2026-07-22T13:09:44.797 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012160 |  | EACOP-PS5-60-10-0160 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-10 - Power Generation Package D |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-07-22T13:11:10.193 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:08:42.000
PL-012161 |  | EACOP-PS5-60-10-0160 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-60-10 - Power Generation Package D |  | Completed |  | Paint touch up to be done | 2026-07-22T13:11:43.580 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:09:12.000
PL-012162 | PS5-03-GDHS-E202-CW01 |  | B | I | Wrong tag number and not found at IO List | EITS | PS5-03-23 - FZ-E1 to E3 - EITS Building |  | Originated |  | To change the name plate as per IO list | 2026-07-22T13:12:13.000 | Carlos, Jose | PS5 - Milestone A
PL-012163 | PS5-03-GDHS-E201-CW01 |  | B | I | Wrong tag number as per IO List | EITS | PS5-03-23 - FZ-E1 to E3 - EITS Building |  | Originated |  | To change the name plate as per IO List | 2026-07-22T13:15:46.000 | Carlos, Jose | PS5 - Milestone A
PL-012164 |  | EACOP-PS5-60-10-0161 | B | P | 18:PS5-60-UR-8100D_TP1039 - Hose Connection FM to be Done | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | Hose Connection FM to be Done | 2026-07-22T13:21:08.570 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012165 |  | EACOP-PS5-60-10-0161 | B | P | 18.1:Cladding Penetration to be Fixed | CPP AGI | PS5-60-10 - Power Generation Package D |  | Completed |  | Cladding Penetration to be Fixed | 2026-07-22T13:22:09.470 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:09:46.000
PL-012166 |  | EACOP-PS5-60-10-0161 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-10 - Power Generation Package D |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-22T13:22:46.380 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:10:07.000
PL-012167 |  | EACOP-PS5-60-10-0161 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-10 - Power Generation Package D |  | Completed |  | Paint touch up to be done | 2026-07-22T13:23:21.907 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:10:36.000
PL-012168 |  | EACOP-PS5-60-10-0162 | B | P | 18:1" valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-22T13:29:32.913 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012169 |  | EACOP-PS5-60-10-0162 | B | P | 18.1:PS5-60-UR-8100D_TP1038 - Hose Connection FM to be Done | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | Hose Connection FM to be Done | 2026-07-22T13:31:08.507 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012170 |  | EACOP-PS5-60-10-0162 | B | P | 18.2:Cladding Penetration to be Fixed | CPP AGI | PS5-60-10 - Power Generation Package D |  | Completed |  | Cladding Penetration to be Fixed | 2026-07-22T13:32:41.260 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:11:21.000
PL-012171 |  | EACOP-PS5-60-10-0162 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-10 - Power Generation Package D |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-22T13:33:23.427 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:11:41.000
PL-012172 |  | EACOP-PS5-60-10-0162 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-60-10 - Power Generation Package D |  | Completed |  | Paint touch up to be done | 2026-07-22T13:33:59.577 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:12:07.000
PL-012207 | PS5-63-IEB-0001 |  | B | E | The cable quantity shown in Drawing No. TZ-MID-68-SSF1-150005 does not match the site installation. A total of 22 cables were verified on site | EITS | PS5-63-04 - Electrical Earthing - EITS Building |  | Originated |  | The drawing should be updated to reflect the as-built site conditions and uploaded to Aconex prior to AOC. | 2026-07-23T06:05:12.000 | Shirima, Frank | PS5 - Milestone A
PL-012222 | PS5-63-IEB-0002 |  | B | E | The cable quantity shown in Drawing No. TZ-MID-68-SSF1-150005 does not match the site installation. A total of 27 cables were verified on site | EITS | PS5-63-04 - Electrical Earthing - EITS Building |  | Originated |  | The drawing should be updated to reflect the as-built site conditions and uploaded to Aconex prior to AOC. | 2026-07-23T08:17:07.000 | Shirima, Frank | PS5 - Milestone A
PL-012223 | PS5-63-IEB-0003 |  | B | E | The cable quantity shown in Drawing No. TZ-MID-68-SSF1-150005 does not match the site installation. A total of 04 cables were verified on site. | EITS | PS5-63-04 - Electrical Earthing - EITS Building |  | Originated |  | The drawing should be updated to reflect the as-built site conditions and uploaded to Aconex prior to AOC | 2026-07-23T08:19:45.000 | Shirima, Frank | PS5 - Milestone A
PL-012224 | PS5-63-IEB-0004 |  | B | E | The cable quantity shown in Drawing No. TZ-MID-68-SSF1-150005 does not match the site installation. A total of 38 cables were verified on site. | EITS | PS5-63-04 - Electrical Earthing - EITS Building |  | Originated |  | The drawing shall be updated to reflect the as-built site conditions and uploaded to Aconex prior to AOC | 2026-07-23T08:21:49.000 | Shirima, Frank | PS5 - Milestone A
PL-012225 | PS5-63-IEB-0005 |  | B | E | The cable quantity shown in Drawing No. TZ-MID-68-SSF1-150005 does not match the site installation. A total of 29 cables were verified on site. | EITS | PS5-63-04 - Electrical Earthing - EITS Building |  | Originated |  | The drawing should be updated to reflect the as-built site conditions and uploaded to Aconex prior to AOC. | 2026-07-23T08:32:38.000 | Shirima, Frank | PS5 - Milestone A
PL-012226 | PS5-63-IEB-0006 |  | B | E | The cable quantity shown in Drawing No. TZ-MID-68-SSF1-150005 does not match the site installation. A total of 32 cables were verified on site. | EITS | PS5-63-04 - Electrical Earthing - EITS Building |  | Originated |  | The drawing shall be updated to reflect the as-built site conditions and uploaded to Aconex prior to AOC. | 2026-07-23T08:33:45.000 | Shirima, Frank | PS5 - Milestone A
PL-012237 |  | EACOP-PS5-71-06-0308 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-23T14:43:52.023 | Bhagavath, sangeeth | PS5 - Milestone H
PL-012238 |  | EACOP-PS5-71-06-0308 | B | P | 18.1:PS5-71-SPZQ-0070 Tubing Connection FM to be Done | CPP AGI | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  | PS5-71-SPZQ-0070 Tubing Connection FM to be Done | 2026-07-23T14:44:59.703 | Bhagavath, sangeeth | PS5 - Milestone H
PL-012239 |  | EACOP-PS5-71-06-0308 | B | P | 18.2:Cladding Penetration to be Fixed | CPP AGI | PS5-71-06 - Crude Fuel Separation Module |  | Completed |  | Cladding Penetration to be Fixed | 2026-07-23T14:45:48.600 | Bhagavath, sangeeth | PS5 - Milestone H | 2026-08-30T14:08:20.000
PL-012240 |  | EACOP-PS5-71-06-0308 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-71-06 - Crude Fuel Separation Module |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-23T14:46:14.390 | Bhagavath, sangeeth | PS5 - Milestone H | 2026-08-30T14:08:52.000
PL-012241 |  | EACOP-PS5-71-06-0308 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-71-06 - Crude Fuel Separation Module |  | Completed |  | Paint touch up to be done | 2026-07-23T14:46:41.777 | Bhagavath, sangeeth | PS5 - Milestone H | 2026-08-30T14:09:18.000
PL-012243 |  | EACOP-PS5-71-08-0310 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-71-08 - CFO Pre-Pressure Modules |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-23T14:50:23.377 | Bhagavath, sangeeth | PS5 - Milestone H
PL-012244 |  | EACOP-PS5-71-08-0310 | B | P | 18.1:Through Wall Penetration to be Fixed | CPP AGI | PS5-71-08 - CFO Pre-Pressure Modules |  | Completed |  | Through Wall Penetration to be Fixed | 2026-07-23T14:51:04.773 | Bhagavath, sangeeth | PS5 - Milestone H | 2026-08-30T14:09:54.000
PL-012246 |  | EACOP-PS5-71-08-0310 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-71-08 - CFO Pre-Pressure Modules |  | Completed |  | Paint touch up to be done | 2026-07-23T14:51:33.760 | Bhagavath, sangeeth | PS5 - Milestone H | 2026-08-30T14:10:20.000
PL-012250 |  | EACOP-PS5-71-18-0327 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-23T14:56:59.740 | Bhagavath, sangeeth | PS5 - Milestone F
PL-012251 |  | EACOP-PS5-71-18-0327 | B | P | 18.1:Cladding Penetration to be Fixed | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Completed |  | Cladding Penetration to be Fixed | 2026-07-23T14:57:40.067 | Bhagavath, sangeeth | PS5 - Milestone F | 2026-08-30T14:10:48.000
PL-012252 |  | EACOP-PS5-71-18-0327 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-23T14:58:08.950 | Bhagavath, sangeeth | PS5 - Milestone F | 2026-08-30T14:11:51.000
PL-012253 |  | EACOP-PS5-71-18-0327 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Completed |  | Paint touch up to be done | 2026-07-23T14:58:42.913 | Bhagavath, sangeeth | PS5 - Milestone F | 2026-08-30T14:12:24.000
PL-012254 |  | EACOP-PS5-71-21-0332 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-23T15:05:17.160 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012255 |  | EACOP-PS5-71-21-0332 | B | P | 18.1:PS5-71-PGD-0049A & PS5-71-PGD-0049B - to be install & FM to be done | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | :PS5-71-PGD-0049A & PS5-71-PGD-0049B - to be install & FM to be done | 2026-07-23T15:05:51.283 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012256 |  | EACOP-PS5-71-21-0332 | B | P | 18.2:TZ-MID-68-WPR2-208033 Drawing RLMU To be done | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | TZ-MID-68-WPR2-208033 Drawing RLMU To be done | 2026-07-23T15:06:44.857 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012257 |  | EACOP-PS5-71-21-0332 | B | P | 18.3:TZ-MID-68-WPR2-208033 Blank to ne Installed | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Completed |  | Blank to ne Installed | 2026-07-23T15:07:29.323 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-30T14:12:58.000
PL-012258 |  | EACOP-PS5-71-21-0332 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Completed |  | Paint touch up to be done | 2026-07-23T15:08:06.860 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-30T14:13:28.000
PL-012369 |  | EACOP-PS5-60-52-0229 | B | P | 18:1" valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-24T12:36:25.900 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012371 |  | EACOP-PS5-60-52-0229 | B | P | 18.1:TZ-MID-68-WPR2-208365 CTR commodity code to be add & Valve Orientation RLMU to be done | CPP AGI | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D |  | Originated |  | CTR commodity code to be add & Valve Orientation RLMU to be done | 2026-07-24T12:37:36.553 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012372 |  | EACOP-PS5-60-52-0229 | B | P | 18.2:PS5-60-UR-8100D_TP852 & TP853 - Hose Connection FM to be Done | CPP AGI | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D |  | Originated |  | PS5-60-UR-8100D_TP852 & TP853 - Hose Connection FM to be Done | 2026-07-24T12:39:39.740 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012373 | PS5-60-BE-0011A-CL01 |  | C | E | Cable Tagging not yet install at both ends | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | we need Cable Tagging install at both ends | 2026-07-24T12:40:27.380 | Gawad, Mohamed | PS5 - Milestone B
PL-012374 |  | EACOP-PS5-60-52-0229 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-24T12:41:03.633 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:12:29.000
PL-012375 | BF_PS5-61-IG-0003_CKT05 |  | B | E | DRAWING TO BE UPDATE AS PER SITE INSTALLATION | EITS | PS5-62-13 - EITS 33kV Bld. Normal L&SP DP - PS5-61-IG-0003 |  | Originated |  | LIGHTINGANDSMALLPOWERBLOCKDIAGRAM & LIGHTING SMALL POWER - INTERCONNECTION WIRING DIAGRAM TO BE UPDATE AS PER SITE CONDITION | 2026-07-24T12:41:26.000 | Saravanan, Raja | PS5 - Milestone A
PL-012376 | PS5-60-BE-0011A-CL02 |  | C | E | Cable Tagging not yet install at both ends | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | we need Cable Tagging install at both ends | 2026-07-24T12:41:46.210 | Gawad, Mohamed | PS5 - Milestone B
PL-012377 |  | EACOP-PS5-60-52-0229 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D |  | Completed |  | Paint touch up to be done | 2026-07-24T12:41:46.783 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:14:01.000
PL-012378 | PS5-60-BE-0011A-CL03 |  | C | E | Cable Tagging not yet install at both ends | CPP AGI | PS5-60-01 - Power Generation Package A |  | Completed |  | we need Cable Tagging install at both ends | 2026-07-24T12:43:00.070 | Gawad, Mohamed | PS5 - Milestone B | 2026-08-12T09:48:44.000
PL-012379 | PS5-60-BE-0011B-CL01 |  | C | E | Cable Tagging not yet install at both ends | CPP AGI | PS5-60-01 - Power Generation Package A |  | Completed |  | we need Cable Tagging install at both ends | 2026-07-24T12:45:45.820 | Gawad, Mohamed | PS5 - Milestone B | 2026-08-12T09:47:19.000
PL-012381 |  | EACOP-PS5-71-18-0328 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-24T12:46:35.580 | Bhagavath, sangeeth | PS5 - Milestone F
PL-012382 | PS5-60-BE-0011B-CL03 |  | C | E | Cable Tagging not yet install at both ends | CPP AGI | PS5-60-01 - Power Generation Package A |  | Completed |  | we need Cable Tagging install at both ends | 2026-07-24T12:47:19.973 | Gawad, Mohamed | PS5 - Milestone B | 2026-08-12T09:46:05.000
PL-012383 |  | EACOP-PS5-71-18-0328 | B | P | 18.1:Sample Connection Inlet Connection FM to be Done | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Originated |  | Sample Connection Inlet Connection FM to be Done | 2026-07-24T12:47:57.123 | Bhagavath, sangeeth | PS5 - Milestone F
PL-012384 | PS5-60-BE-0011B-CL05 |  | C | E | Cable Tagging not yet install at both ends | CPP AGI | PS5-60-01 - Power Generation Package A |  | Completed |  | we need Cable Tagging install at both ends | 2026-07-24T12:48:57.923 | Gawad, Mohamed | PS5 - Milestone B | 2026-08-12T09:43:39.000
PL-012385 |  | EACOP-PS5-71-18-0328 | B | P | 18.2:Drg No - TZ-MID-68-WPR2-207627, S12(PS-98188) - GL01 Missing | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Completed |  | S12(PS-98188) - GL01 Missing | 2026-07-24T12:49:04.467 | Bhagavath, sangeeth | PS5 - Milestone F | 2026-08-30T14:14:16.000
PL-012386 |  | EACOP-PS5-71-18-0328 | B | P | 18.3:Drg No- TZ-MID-68-WPR2-207627, S12 & S13 (PS-49018)- GL01 & PR01 Missing Structure support not Installed | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Originated |  | S12 & S13 (PS-49018)- GL01 & PR01 Missing Structure support not Installed | 2026-07-24T12:51:06.220 | Bhagavath, sangeeth | PS5 - Milestone F
PL-012389 |  | EACOP-PS5-71-18-0328 | B | P | 18.4:TZ-MID-68-WPR2-207469, F2 - Flange Management to be done | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Originated |  | F2 - Flange Management to be done | 2026-07-24T12:53:10.460 | Bhagavath, sangeeth | PS5 - Milestone F
PL-012390 | PS5-60-BE-0012A-CL03 |  | C | E | Cable Tagging not yet install at both ends | CPP AGI | PS5-60-04 - Power Generation Package B |  | Completed |  | Cable tagging to be installed at both ends | 2026-07-24T12:53:47.017 | Gawad, Mohamed | PS5 - Milestone B | 2026-08-12T09:40:53.000
PL-012391 |  | EACOP-PS5-71-18-0328 | B | P | 18.5:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-24T12:54:03.990 | Bhagavath, sangeeth | PS5 - Milestone F | 2026-08-30T14:15:37.000
PL-012392 |  | EACOP-PS5-71-18-0328 | B | P | 18.6:Paint touch up to be done | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Completed |  | Paint touch up to be done | 2026-07-24T12:54:39.000 | Bhagavath, sangeeth | PS5 - Milestone F | 2026-08-30T14:16:06.000
PL-012393 | PS5-60-BE-0012A-CL05 |  | C | E | Cable tagging to be installed at both ends | CPP AGI | PS5-60-04 - Power Generation Package B |  | Completed |  | Cable tagging to be installed at both ends | 2026-07-24T12:55:25.427 | Gawad, Mohamed | PS5 - Milestone B | 2026-08-12T09:37:17.000
PL-012396 |  | EACOP-PS5-71-22-0337 | B | P | 18:1"Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-24T12:59:02.033 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012405 |  | EACOP-PS5-71-20-0330 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-24T13:08:58.933 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012408 |  | EACOP-PS5-71-20-0330 | B | P | 18.1:Drg No- TZ-MID-68-WPR2-206863, S10 & S11 (51586 - PR01 & GL01 Not done bottom structure supports have not yet been installed. | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Originated |  | S10 & S11 (51586 - PR01 & GL01 Not done bottom structure supports have not yet been installed. | 2026-07-24T13:09:57.650 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012410 |  | EACOP-PS5-71-20-0330 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-24T13:11:46.127 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-30T14:17:36.000
PL-012411 |  | EACOP-PS5-71-20-0330 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Completed |  | Paint touch up to be done | 2026-07-24T13:12:20.013 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-30T14:18:02.000
PL-012427 | PS5-60-TG-0007A |  | C | I | Cable Tagging not yet install at both ends | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Cable tagging to be installed at both ends | 2026-07-24T14:31:37.780 | Gawad, Mohamed | PS5 - Milestone B
PL-012430 | PS5-60-TG-0008A |  | C | I | Cable Tagging not yet install at both ends | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Cable tagging to be installed at both ends | 2026-07-24T14:40:54.643 | Gawad, Mohamed | PS5 - Milestone B
PL-012433 | PS5-60-TG-0006A |  | C | I | Cable Tagging not yet install at both ends | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Cable tagging to be installed at both ends | 2026-07-24T14:46:56.200 | Gawad, Mohamed | PS5 - Milestone B
PL-012434 | PS5-60-TG-0006B |  | C | I | Cable Tagging not yet install at both ends | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | Cable tagging to be installed at both ends | 2026-07-24T16:37:15.930 | Gawad, Mohamed | PS5 - Milestone B
PL-012435 | PS5-60-TG-0005A |  | C | I | Cable Tagging not yet install at both ends | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Cable tagging to be installed at both ends | 2026-07-24T16:41:50.190 | Gawad, Mohamed | PS5 - Milestone B
PL-012436 | PS5-60-TG-0005B |  | C | I | Cable Tagging not yet install at both ends | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | Cable tagging to be installed at both ends | 2026-07-24T16:44:29.823 | Gawad, Mohamed | PS5 - Milestone B
PL-012467 | PS5-61-IK-0001-CL01 |  | C | E | Missing cable tag - Inside Panel & Cabin (Yellow tag with black font) | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To arrange/install cable tag as per specification | 2026-07-25T12:50:37.127 | Kumar, Senthil | PS5 - Milestone A
PL-012469 | PS5-61-IK-0001-CL01 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T13:02:15.260 | Kumar, Senthil | PS5 - Milestone A
PL-012471 | PS5-61-IJ-0010-CL01 |  | C | E | Missing Indoor & Inside Cabin Yellow Colour Black Font Cable Tag | KENT | PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010) |  | Originated |  | To be arrange the Proper Cable Tag | 2026-07-25T13:18:27.000 | Kumar, Senthil | PS5 - Milestone G
PL-012472 | PS5-61-IJ-0010-CL01 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010) |  | Originated |  | To be Use the Proper Nut Bolts for Transformer Side Termination points | 2026-07-25T13:22:14.290 | Kumar, Senthil | PS5 - Milestone G
PL-012473 | PS5-61-IK-0001-CL03 |  | C | E | Missing cable tag - Indoor & Inside cabin (Yellow tag with black font) | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To arrange/install proper cable tag as per specification | 2026-07-25T13:35:27.683 | Kumar, Senthil | PS5 - Milestone A
PL-012474 | PS5-61-IK-0001-CL03 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T13:41:12.130 | Kumar, Senthil | PS5 - Milestone A
PL-012475 |  | EACOP-PS5-71-06-0307 | B | P | 18:Gladding Penetration to be fixed | CPP AGI | PS5-71-06 - Crude Fuel Separation Module |  | Completed |  | Gladding Penetration to be fixed | 2026-07-25T13:56:47.367 | Bhagavath, sangeeth | PS5 - Milestone H | 2026-08-30T14:18:38.000
PL-012476 |  | EACOP-PS5-71-06-0307 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-71-06 - Crude Fuel Separation Module |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-25T13:57:28.920 | Bhagavath, sangeeth | PS5 - Milestone H | 2026-08-30T14:19:20.000
PL-012477 |  | EACOP-PS5-71-06-0307 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-71-06 - Crude Fuel Separation Module |  | Completed |  | Paint touch up to be done | 2026-07-25T13:58:04.013 | Bhagavath, sangeeth | PS5 - Milestone H | 2026-08-30T14:20:08.000
PL-012478 |  | EACOP-PS5-71-22-0335 | B | P | 18:Drg No -TZ-MID-68-WPR2-208146, S13 (PS86704)- PR01 to be fixed | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Completed |  | S13 (PS86704)- PR01 to be fixed | 2026-07-25T14:08:56.680 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T11:14:53.000
PL-012479 |  | EACOP-PS5-71-22-0335 | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-25T14:10:29.680 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012480 |  | EACOP-PS5-71-22-0335 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-25T14:11:53.387 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T11:15:24.000
PL-012481 |  | EACOP-PS5-71-22-0335 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Completed |  | Paint touch up to be done | 2026-07-25T14:12:24.600 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T11:15:51.000
PL-012484 |  | EACOP-PS5-71-08-0309 | B | P | 18:Gladding Penetration to be fixed | CPP AGI | PS5-71-08 - CFO Pre-Pressure Modules |  | Completed |  | Gladding Penetration to be fixed | 2026-07-25T14:30:48.557 | Bhagavath, sangeeth | PS5 - Milestone H | 2026-08-30T14:20:43.000
PL-012485 |  | EACOP-PS5-71-08-0309 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-71-08 - CFO Pre-Pressure Modules |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-25T14:31:17.243 | Bhagavath, sangeeth | PS5 - Milestone H | 2026-08-30T14:21:47.000
PL-012486 |  | EACOP-PS5-71-08-0309 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-71-08 - CFO Pre-Pressure Modules |  | Completed |  | Paint touch up to be done | 2026-07-25T14:31:54.823 | Bhagavath, sangeeth | PS5 - Milestone H | 2026-08-30T14:22:26.000
PL-012487 | PS5-61-IK-0001-CL04 |  | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Provide the indoor Cable Tags | 2026-07-25T16:35:04.883 | Kumar, Senthil | PS5 - Milestone A
PL-012488 | PS5-61-IK-0001-CL04 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T16:39:34.903 | Kumar, Senthil | PS5 - Milestone A
PL-012489 | PS5-61-IK-0001-CL05 |  | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To Provide the indoor Cable Tags as per Specification | 2026-07-25T16:47:01.607 | Kumar, Senthil | PS5 - Milestone A
PL-012490 | PS5-61-IK-0001-CL05 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T16:49:36.563 | Kumar, Senthil | PS5 - Milestone A
PL-012491 | PS5-61-IK-0001-CL06 |  | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To Provide the indoor Cable Tags as per Specification | 2026-07-25T17:28:21.117 | Kumar, Senthil | PS5 - Milestone A
PL-012492 | PS5-61-IK-0001-CL06 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T17:30:17.737 | Kumar, Senthil | PS5 - Milestone A
PL-012493 | PS5-61-IK-0001-CL07 |  | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To Provide the indoor Cable Tags as per Specification | 2026-07-25T17:47:14.937 | Kumar, Senthil | PS5 - Milestone A
PL-012494 | PS5-61-IK-0001-CL07 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T17:48:46.710 | Kumar, Senthil | PS5 - Milestone A
PL-012495 | PS5-61-IK-0001-CL08 |  | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To Provide the indoor Cable Tags as per Specification | 2026-07-25T18:03:09.580 | Kumar, Senthil | PS5 - Milestone A
PL-012496 | PS5-61-IK-0001-CL08 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T18:05:03.133 | Kumar, Senthil | PS5 - Milestone A
PL-012497 | PS5-61-IK-0001-CL09 |  | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To Provide the indoor Cable Tags as per Specification | 2026-07-25T18:15:47.173 | Kumar, Senthil | PS5 - Milestone A
PL-012498 | PS5-61-IK-0001-CL09 |  | B | E | Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T18:18:39.647 | Kumar, Senthil | PS5 - Milestone A
PL-012499 | PS5-61-IK-0001-CL10 |  | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T18:27:38.800 | Kumar, Senthil | PS5 - Milestone A
PL-012500 | PS5-61-IK-0001-CL10 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T18:28:49.547 | Kumar, Senthil | PS5 - Milestone A
PL-012501 | PS5-61-IK-0001-CL11 |  | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To Provide the indoor Cable Tags as per Specification | 2026-07-25T18:38:45.503 | Kumar, Senthil | PS5 - Milestone A
PL-012502 | PS5-61-IK-0001-CL11 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T18:40:21.787 | Kumar, Senthil | PS5 - Milestone A
PL-012503 | PS5-61-IK-0001-CL12 |  | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To Provide the indoor Cable Tags as per Specification | 2026-07-25T18:58:01.937 | Kumar, Senthil | PS5 - Milestone A
PL-012504 | PS5-61-IK-0001-CL12 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T18:59:59.713 | Kumar, Senthil | PS5 - Milestone A
PL-012505 | PS5-61-IK-0001-CL13 |  | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To Provide the indoor Cable Tags as per Specification | 2026-07-25T19:08:28.193 | Kumar, Senthil | PS5 - Milestone A
PL-012506 | PS5-61-IK-0001-CL13 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T19:09:44.977 | Kumar, Senthil | PS5 - Milestone A
PL-012507 | PS5-61-IK-0001-CL14 |  | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To Provide the indoor Cable Tags as per Specification | 2026-07-25T19:17:11.737 | Kumar, Senthil | PS5 - Milestone A
PL-012508 | PS5-61-IK-0001-CL14 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T19:18:36.477 | Kumar, Senthil | PS5 - Milestone A
PL-012509 | PS5-61-IK-0001-CL15 |  | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To Provide the indoor Cable Tags as per Specification | 2026-07-25T19:30:00.210 | Kumar, Senthil | PS5 - Milestone A
PL-012510 | PS5-61-IK-0001-CL15 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T19:31:05.767 | Kumar, Senthil | PS5 - Milestone A
PL-012511 | PS5-61-IK-0001-CL16 |  | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To Provide the indoor Cable Tags as per Specification | 2026-07-25T19:38:26.133 | Kumar, Senthil | PS5 - Milestone A
PL-012512 | PS5-61-IK-0001-CL16 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T19:41:01.333 | Kumar, Senthil | PS5 - Milestone A
PL-012513 | PS5-61-IK-0001-CL17 |  | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To Provide the indoor Cable Tags as per Specification | 2026-07-25T19:48:57.980 | Kumar, Senthil | PS5 - Milestone A
PL-012514 | PS5-61-IK-0001-CL17 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T19:50:29.717 | Kumar, Senthil | PS5 - Milestone A
PL-012515 | PS5-61-IK-0001-CL18 |  | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To Provide the indoor Cable Tags as per Specification | 2026-07-25T19:57:50.337 | Kumar, Senthil | PS5 - Milestone A
PL-012516 | PS5-61-IK-0001-CL18 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-07-25T19:59:23.107 | Kumar, Senthil | PS5 - Milestone A
PL-012690 |  | EACOP-PS5-60-27-0186 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-27T13:10:11.570 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012691 |  | EACOP-PS5-60-27-0186 | B | P | 18.1:Through Wall Penetration to be Fixed. | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  | Through Wall Penetration to be Fixed. | 2026-07-27T13:11:03.273 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012692 |  | EACOP-PS5-60-27-0186 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-27T13:11:35.163 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:16:28.000
PL-012693 |  | EACOP-PS5-60-27-0186 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Completed |  | Paint touch up to be done | 2026-07-27T13:12:07.300 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:17:01.000
PL-012694 |  | EACOP-PS5-60-38-0201 | B | P | 18:PS5-60-UR-8100D_TP-848 & TP-849- Hose connection joint FM to be done | CPP AGI | PS5-60-38 - Injector Tip Cooling Module D |  | Originated |  | Hose connection joint FM to be done | 2026-07-27T13:21:22.240 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012695 |  | EACOP-PS5-60-38-0201 | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-38 - Injector Tip Cooling Module D |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-27T13:22:32.533 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012696 |  | EACOP-PS5-60-38-0201 | B | P | 18.2:Floor Penetration to be Fixed. | CPP AGI | PS5-60-38 - Injector Tip Cooling Module D |  | Originated |  | Floor Penetration to be Fixed. | 2026-07-27T13:23:23.467 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012697 |  | EACOP-PS5-60-38-0201 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-38 - Injector Tip Cooling Module D |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-27T13:24:14.250 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:16:29.000
PL-012698 |  | EACOP-PS5-60-38-0201 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-60-38 - Injector Tip Cooling Module D |  | Completed |  | Paint touch up to be done | 2026-07-27T13:24:45.277 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:16:59.000
PL-012699 |  | EACOP-PS5-60-71-0257 | B | P | 18:PS5-60-UR-8100B_TP-812,TP-813 & TP-814-Hose connection joint FM to be done | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | Hose connection joint FM to be done | 2026-07-27T13:29:08.640 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012700 |  | EACOP-PS5-60-71-0257 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-27T13:31:24.830 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:41:15.000
PL-012701 |  | EACOP-PS5-60-71-0257 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Completed |  | Paint touch up to be done | 2026-07-27T13:32:46.920 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:55:06.000
PL-012703 | PS5-05-BI-0002-CC11 |  | C | I | Missing Indoor Cable Tag (Yellow Colour with Black font) | KENT | PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure |  | Originated |  | To arrange the Cable Tag | 2026-07-27T18:16:05.110 | Kumar, Senthil | PS5 - Milestone C
PL-012704 | PS5-05-BI-0002-CC11 |  | B | I | No Proper Heat Sleeve for Screen | KENT | PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure |  | Originated |  | To arrange the Clear Heat Sleeve for Screen | 2026-07-27T18:33:54.737 | Kumar, Senthil | PS5 - Milestone C
PL-012705 | PS5-05-BI-0002-CC11 |  | B | I | No Proper Earth Clamp | KENT | PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure |  | Originated |  | To be arrange the Proper Earth Clamp | 2026-07-27T18:38:21.857 | Kumar, Senthil | PS5 - Milestone C
PL-012706 | PS5-05-BI-0002-CC11 |  | B | I | No Proper MCT Packing | KENT | PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure |  | Originated |  | To be proper Pack the MCT | 2026-07-27T18:42:46.093 | Kumar, Senthil | PS5 - Milestone C
PL-012707 | PS5-05-BI-0002-CC12 |  | C | I | Missing Indoor Cable Tag (Yellow Colour with Black font) | KENT | PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure |  | Originated |  | To arrange the Cable Tag | 2026-07-27T19:00:05.003 | Kumar, Senthil | PS5 - Milestone C
PL-012708 | PS5-05-BI-0002-CC12 |  | B | I | No Proper Heat Sleeve for Screen | KENT | PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure |  | Originated |  | To Arrange the Clear Tube Heat Sleeve for Screen | 2026-07-27T19:01:50.560 | Kumar, Senthil | PS5 - Milestone C
PL-012709 | PS5-05-BI-0002-CC12 |  | B | I | No Proper Earth Clamp for Armour Earth | KENT | PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure |  | Originated |  | To be arrange Proper Earth Clamp for Armour Earth | 2026-07-27T19:03:49.013 | Kumar, Senthil | PS5 - Milestone C
PL-012710 | PS5-05-BI-0002-CC12 |  | B | I | No Proper pack the MCT | KENT | PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure |  | Originated |  | To be proper Pack the MCT | 2026-07-27T19:05:51.900 | Kumar, Senthil | PS5 - Milestone C
PL-012729 |  | EACOP-PS5-60-07-0157 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-28T12:46:58.953 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012730 |  | EACOP-PS5-60-07-0157 | B | P | 18.1:PS5-60-UR-8100C_TP-1032 & TP-1033 - Hose connection joint FM to be done | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | Hose connection joint FM to be done | 2026-07-28T12:47:57.273 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012731 |  | EACOP-PS5-60-07-0157 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-07 - Power Generation Package C |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-28T12:48:50.270 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:53:21.000
PL-012732 |  | EACOP-PS5-60-07-0157 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-07 - Power Generation Package C |  | Completed |  | Paint touch up to be done | 2026-07-28T12:49:37.563 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:53:56.000
PL-012733 |  | EACOP-PS5-60-37-0199 | B | P | 18:PS5-60-UR-8100C_TP-828 & TP-827, PS5-60-UZ-8100C_TP-354 & TP-357 - connection joint FM to be done | CPP AGI | PS5-60-37 - Injector Tip Cooling Module C |  | Originated |  | connection joint Flange Management to be done | 2026-07-28T12:59:29.270 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012734 |  | EACOP-PS5-60-37-0199 | B | P | 18.1:1" valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-37 - Injector Tip Cooling Module C |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-28T13:03:14.647 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012735 |  | EACOP-PS5-60-37-0199 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-37 - Injector Tip Cooling Module C |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-28T13:03:58.520 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:54:23.000
PL-012736 |  | EACOP-PS5-60-37-0199 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-37 - Injector Tip Cooling Module C |  | Completed |  | Paint touch up to be done | 2026-07-28T13:04:41.020 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:54:58.000
PL-012737 |  | EACOP-PS5-60-51-0227 | B | P | 18:PS5-60-UR-8100C_TP-831 & TP-832- Hose connection joint FM to be done | CPP AGI | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C |  | Originated |  | Hose connection joint FM to be done | 2026-07-28T13:09:56.970 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012738 |  | EACOP-PS5-60-51-0227 | B | P | 18.1:1" valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-28T13:10:41.027 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012739 |  | EACOP-PS5-60-51-0227 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-28T13:11:23.240 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:17:55.000
PL-012740 |  | EACOP-PS5-60-51-0227 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C |  | Completed |  | Paint touch up to be done | 2026-07-28T13:11:52.080 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:18:22.000
PL-012741 |  | EACOP-PS5-60-60-0240 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-28T13:22:27.863 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012742 |  | EACOP-PS5-60-60-0240 | B | P | 18.1:Floor Penetration Gratings to be Fixed. | CPP AGI | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C |  | Originated |  | Floor Penetration Gratings to be Fixed. | 2026-07-28T13:23:05.240 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012743 |  | EACOP-PS5-60-60-0240 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-28T13:23:37.227 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:55:26.000
PL-012744 |  | EACOP-PS5-60-60-0240 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C |  | Completed |  | Paint touch up to be done | 2026-07-28T13:24:42.653 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:56:16.000
PL-012745 |  | EACOP-PS5-60-70-0251 | B | P | 18:PS5-60-UR-8100A_TP-791, TP-792 & TP-793 - Hose connection joint FM to be done | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Hose connection joint FM to be done | 2026-07-28T13:29:23.393 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012746 |  | EACOP-PS5-60-70-0251 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-28T13:30:58.157 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:48:20.000
PL-012747 |  | EACOP-PS5-60-70-0251 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Paint touch up to be done | 2026-07-28T13:31:30.697 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012768 | PS5-60-BI-0016A-CC02 |  | C | I | Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Install cable tags on both ends as per cable schedule | 2026-07-29T04:56:05.300 | Gawad, Mohamed | PS5 - Milestone B
PL-012769 | PS5-60-IE-0003A-CC02 |  | C | I | Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | Install cable tags on both ends as per cable schedule | 2026-07-29T05:02:06.870 | Gawad, Mohamed | PS5 - Milestone B
PL-012770 | PS5-60-IE-0003A-CC03 |  | C | I | Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | Install cable tags on both ends as per cable schedule | 2026-07-29T05:03:45.630 | Gawad, Mohamed | PS5 - Milestone B
PL-012771 | PS5-60-IE-0003A-CC04 |  | C | I | Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | Install cable tags on both ends as per cable schedule | 2026-07-29T05:06:07.797 | Gawad, Mohamed | PS5 - Milestone B
PL-012772 | PS5-60-IE-0003A-CC15 |  | C | I | Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | Install cable tags on both ends as per cable schedule | 2026-07-29T05:07:55.473 | Gawad, Mohamed | PS5 - Milestone B
PL-012783 |  | EACOP-PS5-71-22-0337 | B | P | 18.1:Through Wall penetration to be Fixed | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | Through Wall penetration to be Fixed | 2026-07-29T06:40:19.473 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012784 |  | EACOP-PS5-71-22-0337 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-29T06:40:55.373 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012785 |  | EACOP-PS5-71-22-0337 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | Paint touch up to be done | 2026-07-29T06:41:22.030 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012828 |  | EACOP-PS5-60-28-0187 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-28 - Air Receiver A & Air Regulator A |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-29T11:59:58.027 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012829 |  | EACOP-PS5-60-28-0187 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-28 - Air Receiver A & Air Regulator A |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-29T12:00:45.140 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:48:47.000
PL-012831 |  | EACOP-PS5-60-28-0187 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-60-28 - Air Receiver A & Air Regulator A |  | Originated |  | Paint touch up to be done | 2026-07-29T12:01:24.427 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012836 |  | EACOP-PS5-60-29-0188 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-29 - Air Receiver B & Air Regulator B |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-29T12:07:34.913 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012838 |  | EACOP-PS5-60-29-0188 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-29 - Air Receiver B & Air Regulator B |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-29T12:08:19.790 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:41:50.000
PL-012839 |  | EACOP-PS5-60-29-0188 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-60-29 - Air Receiver B & Air Regulator B |  | Completed |  | Paint touch up to be done | 2026-07-29T12:08:57.530 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:56:09.000
PL-012844 |  | EACOP-PS5-60-42-0209 | B | P | 18:Paint touchup to be done | CPP AGI | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A |  | Originated |  | Paint touchup to be done in damaged area | 2026-07-29T12:13:17.883 | Bhagavath, sangeeth | PS5 - Milestone B
PL-012847 |  | EACOP-PS5-60-43-0211 | B | P | 18:Paint touchup to be done | CPP AGI | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B |  | Completed |  | Paint touchup to be done in damaged area | 2026-07-29T12:18:27.280 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-22T11:18:48.000
PL-012851 |  | EACOP-PS5-60-73-0269 | B | P | 18:PS5-60-UR-8100D_TP-854, TP-855 & TP-856 - Hose connection joint Flange management to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | Hose connection joint Flange management to be done | 2026-07-29T12:24:46.840 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012852 |  | EACOP-PS5-60-73-0269 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-29T12:26:39.903 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012853 |  | EACOP-PS5-60-73-0269 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | Paint touch up to be done | 2026-07-29T12:27:11.097 | Bhagavath, sangeeth | PS5 - Milestone D
PL-012884 | PS5-60-PG-0002A |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-28 - Air Receiver A & Air Regulator A |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-07-29T16:45:43.280 | Gawad, Mohamed | PS5 - Milestone B
PL-012885 | PS5-60-PG-0002B |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-29 - Air Receiver B & Air Regulator B |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-07-29T16:52:57.877 | Gawad, Mohamed | PS5 - Milestone B
PL-012928 | PS5-60-IH-0001A-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-07-30T05:05:58.480 | Gawad, Mohamed | PS5 - Milestone B
PL-012937 | PS5-60-IH-0001A-CL01 |  | C | E | Core marking to be installed at both side | CPP AGI | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs |  | Originated |  | Install core markings at both ends of the cable | 2026-07-30T05:11:27.847 | Gawad, Mohamed | PS5 - Milestone B
PL-012941 | PS5-60-IH-0001A-CL02 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-07-30T05:13:16.307 | Gawad, Mohamed | PS5 - Milestone B
PL-012942 | PS5-60-IH-0001A-CL02 |  | C | E | Core marking to be installed at both side | CPP AGI | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs |  | Originated |  | Install core markings at both ends of the cable | 2026-07-30T05:13:36.300 | Gawad, Mohamed | PS5 - Milestone B
PL-012945 | PS5-60-IH-0001A-CL03 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-07-30T05:15:05.957 | Gawad, Mohamed | PS5 - Milestone B
PL-012947 | PS5-60-IH-0001A-CL03 |  | C | E | Core marking to be installed at both side | CPP AGI | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs |  | Originated |  | Install core markings at both ends of the cable | 2026-07-30T05:15:27.407 | Gawad, Mohamed | PS5 - Milestone B
PL-012950 | PS5-60-IH-0001A-CL04 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-07-30T05:17:14.760 | Gawad, Mohamed | PS5 - Milestone B
PL-012952 | PS5-60-IH-0001A-CL04 |  | C | E | Core marking to be installed at both side | CPP AGI | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs |  | Originated |  | Install core markings at both ends of the cable | 2026-07-30T05:17:37.927 | Gawad, Mohamed | PS5 - Milestone B
PL-012956 | PS5-60-IH-0001B-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-07-30T05:19:30.913 | Gawad, Mohamed | PS5 - Milestone B
PL-012957 | PS5-60-IH-0001B-CL01 |  | C | E | Core marking to be installed at both side | CPP AGI | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs |  | Originated |  | Install core markings at both ends of the cable | 2026-07-30T05:19:49.210 | Gawad, Mohamed | PS5 - Milestone B
PL-012963 | PS5-60-IH-0001B-CL02 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-07-30T05:22:45.890 | Gawad, Mohamed | PS5 - Milestone B
PL-012965 | PS5-60-IH-0001B-CL02 |  | C | E | Core marking to be installed at both side | CPP AGI | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs |  | Originated |  | Install core markings at both ends of the cable | 2026-07-30T05:23:33.550 | Gawad, Mohamed | PS5 - Milestone B
PL-012966 | PS5-60-IH-0001B-CL03 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-07-30T05:25:11.757 | Gawad, Mohamed | PS5 - Milestone B
PL-012967 | PS5-60-IH-0001B-CL03 |  | C | E | Core marking to be installed at both side | CPP AGI | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs |  | Originated |  | Install core markings at both ends of the cable | 2026-07-30T05:25:34.190 | Gawad, Mohamed | PS5 - Milestone B
PL-012970 | PS5-60-IH-0001B-CL04 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-07-30T05:27:08.310 | Gawad, Mohamed | PS5 - Milestone B
PL-012971 | PS5-60-IH-0001B-CL04 |  | C | E | Core marking to be installed at both side | CPP AGI | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs |  | Originated |  | Install core markings at both ends of the cable | 2026-07-30T05:27:26.367 | Gawad, Mohamed | PS5 - Milestone B
PL-013023 |  | EACOP-PS5-60-45-0215 | B | P | 18:Paint touch up to be done | CPP AGI | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D |  | Originated |  | Paint touchup to be done in damaged area | 2026-07-30T12:12:20.210 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013024 |  | EACOP-PS5-60-60-0241 | B | P | 18:PS5-60-UR-8100C_TP-825 7 TP_826 - Equpiment connection joint Flange Management to be done | CPP AGI | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C |  | Originated |  | Equpiment connection joint Flange Management to be done | 2026-07-30T12:17:19.810 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013025 |  | EACOP-PS5-60-60-0241 | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-30T12:18:22.140 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013026 |  | EACOP-PS5-60-60-0241 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-30T12:19:29.847 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:19:17.000
PL-013027 |  | EACOP-PS5-60-60-0241 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C |  | Completed |  | Paint touch up to be done | 2026-07-30T12:20:04.330 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:19:43.000
PL-013029 |  | EACOP-PS5-60-62-0242 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-30T12:31:03.340 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013030 |  | EACOP-PS5-60-62-0242 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-30T12:32:07.053 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:20:02.000
PL-013031 |  | EACOP-PS5-60-62-0242 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D |  | Completed |  | Paint touchup to be done in damaged area | 2026-07-30T12:32:43.560 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:20:34.000
PL-013053 | PS5-60-TX-41300A |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  |  | 2026-07-30T14:02:35.450 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T08:06:55.000
PL-013056 | PS5-60-TX-41300A |  | C | E | 23.1:EARHING TO BE DONE | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  |  | 2026-07-30T14:03:23.677 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-013058 | PS5-60-TX-41300B |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  |  | 2026-07-30T14:06:08.840 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T08:07:14.000
PL-013063 | PS5-60-TX-41300B |  | C | M | 23.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  |  | 2026-07-30T14:11:10.633 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-013065 | PS5-60-TX-41300B |  | C | E | 23.2: EARTHING TO BE DONE | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  |  | 2026-07-30T14:11:46.080 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-013067 | PS5-60-TX-41300A |  | C | M | 23.2:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  |  | 2026-07-30T14:12:52.917 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-013068 | PS5-60-TX-41400A |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Completed |  |  | 2026-07-30T14:14:37.350 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T08:07:55.000
PL-013070 | PS5-60-TX-41400A |  | C | M | 23.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2026-07-30T14:15:13.470 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-013071 | PS5-60-TX-41400A |  | C | E | 23.2: EARTHING TO BE DONE | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2026-07-30T14:15:52.260 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-013077 | PS5-60-TX-41400B |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Completed |  |  | 2026-07-30T14:22:11.620 | THANGARATHINAM, ajikumar | PS5 - Milestone D | 2026-08-13T08:08:39.000
PL-013078 | PS5-60-TX-41400B |  | C | M | 23.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2026-07-30T14:23:07.480 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-013079 | PS5-60-TX-41400B |  | C | E | 23.2:EARTHING TO BE DONE | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2026-07-30T14:23:28.647 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-013084 | PS5-71-VSV-1200 |  | B | P | 18:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Completed |  |  | 2026-07-30T14:28:14.777 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T08:10:08.000
PL-013086 | PS5-71-VSV-1200 |  | C | M | 18.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Completed |  |  | 2026-07-30T14:28:56.463 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-09-04T08:14:24.000
PL-013088 | PS5-71-VSV-1200 |  | C | E | 18.2:EARTHING TO BE DONE | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Originated |  |  | 2026-07-30T14:29:49.493 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-013120 | PS5-71-VSV-1200 |  | B | P | 11:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Completed |  |  | 2026-07-31T05:38:05.127 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-13T08:10:30.000
PL-013124 | PS5-71-VSV-1200 |  | C | M | 11.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Originated |  |  | 2026-07-31T05:39:43.380 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-013125 | PS5-71-VSV-1200 |  | C | E | 11.2:EARTHING TO BE DONE | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Originated |  |  | 2026-07-31T05:40:23.200 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-013252 |  | EACOP-PS5-60-30-0189 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-30 - Air Receiver C & Air Regulator C |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-31T13:40:39.423 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013253 |  | EACOP-PS5-60-30-0189 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-30 - Air Receiver C & Air Regulator C |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-31T13:41:46.237 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:56:47.000
PL-013254 |  | EACOP-PS5-60-30-0189 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-60-30 - Air Receiver C & Air Regulator C |  | Completed |  | Paint touch up to be done | 2026-07-31T13:42:19.190 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:57:13.000
PL-013256 |  | EACOP-PS5-60-31-0190 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-31 - Air Receiver D & Air Regulator D |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-31T13:57:01.040 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013257 |  | EACOP-PS5-60-31-0190 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-31 - Air Receiver D & Air Regulator D |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-31T13:57:38.390 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:21:01.000
PL-013258 |  | EACOP-PS5-60-31-0190 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-60-31 - Air Receiver D & Air Regulator D |  | Completed |  | Paint touchup to be done in damaged area | 2026-07-31T13:58:12.487 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:21:49.000
PL-013260 |  | EACOP-PS5-60-62-0243 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-07-31T14:02:22.587 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013261 |  | EACOP-PS5-60-62-0243 | B | P | 18.1:PS5-60-UR-8100D-TP_846 & 847 - Equpiment joint Flange Management to be done | CPP AGI | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D |  | Originated |  | Equpiment joint Flange Management to be done | 2026-07-31T14:03:02.013 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013262 |  | EACOP-PS5-60-62-0243 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-07-31T14:03:55.500 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013263 |  | EACOP-PS5-60-62-0243 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D |  | Originated |  | Paint touch up to be done | 2026-07-31T14:04:23.400 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013448 | PS5-60-IE-0003A-CD02 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-01T13:44:35.790 | Gawad, Mohamed | PS5 - Milestone B
PL-013451 | PS5-60-IE-0003A-CD03 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-01T13:47:03.057 | Gawad, Mohamed | PS5 - Milestone B
PL-013455 | PS5-60-IE-0003A-CD05 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-01T13:48:38.243 | Gawad, Mohamed | PS5 - Milestone B
PL-013461 | PS5-60-IE-0003A-CD08 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-01T13:58:16.570 | Gawad, Mohamed | PS5 - Milestone B
PL-013466 | PS5-60-IE-0003A-CD12 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-01T14:04:08.277 | Gawad, Mohamed | PS5 - Milestone B
PL-013471 | PS5-60-IE-0003A-CD14 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-01T14:13:15.940 | Gawad, Mohamed | PS5 - Milestone B
PL-013476 | PS5-71-DM-3500A-CL01 |  | B | E | Earthing stud of motor not connected to earthing boss at field side | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | Connect earthing stud of motor to earthing boss at field side as per project earthing standard/drawing | 2026-08-01T14:20:45.500 | Gawad, Mohamed | PS5 - Milestone B
PL-013478 | PS5-71-DM-3500B-CL01 |  | B | E | Earthing stud of motor not connected to earthing boss at field side | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | Connect earthing stud of motor to earthing boss at field side as per project earthing standard/drawing | 2026-08-01T14:25:55.863 | Gawad, Mohamed | PS5 - Milestone B
PL-013514 | PS5-60-PG-0002C |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-30 - Air Receiver C & Air Regulator C |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-08-02T05:31:57.433 | Gawad, Mohamed | PS5 - Milestone D
PL-013516 | PS5-60-PG-0002D |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-31 - Air Receiver D & Air Regulator D |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-08-02T05:37:22.340 | Gawad, Mohamed | PS5 - Milestone D
PL-013517 | PS5-60-TG-0005C |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-08-02T05:42:22.100 | Gawad, Mohamed | PS5 - Milestone D
PL-013518 | PS5-60-TG-0006C |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-08-02T05:45:17.213 | Gawad, Mohamed | PS5 - Milestone D
PL-013519 | PS5-60-TG-0007C |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-08-02T05:47:57.663 | Gawad, Mohamed | PS5 - Milestone D
PL-013521 | PS5-60-TG-0008C |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-08-02T05:51:14.813 | Gawad, Mohamed | PS5 - Milestone D
PL-013608 | PS5-71-SPZQ-0067 |  | B | P | 8:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Completed |  |  | 2026-08-03T08:13:21.177 | THANGARATHINAM, ajikumar | PS5 - Milestone B | 2026-08-03T08:14:10.000
PL-013609 | PS5-71-SPZQ-0067 |  | C | M | 8.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  |  | 2026-08-03T08:14:26.453 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-013610 | PS5-71-SPZQ-0066 |  | B | P | 8:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Completed |  |  | 2026-08-03T08:17:03.127 | THANGARATHINAM, ajikumar | PS5 - Milestone F | 2026-08-13T08:10:55.000
PL-013611 | PS5-71-SPZQ-0066 |  | C | M | 8.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Originated |  |  | 2026-08-03T08:17:25.410 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-013614 |  | EACOP-PS5-60-23-0172 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-23 - Instrument Air Distribution lines |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-03T11:28:44.047 | Bhagavath, sangeeth | PS5 - Milestone B
PL-013615 |  | EACOP-PS5-60-23-0172 | B | P | 18.1:TZ-MID-68-WPR2-207161,TZ-MID-68-WPR2-207162,TZ-MID-68-WPR2-207166,TZ-MID-68-WPR2-208131 & TZ-MID-68-WPR2-20802 - ISO RLMU to be done | CPP AGI | PS5-60-23 - Instrument Air Distribution lines |  | Originated |  | ISO RLMU to be done | 2026-08-03T11:29:37.700 | Bhagavath, sangeeth | PS5 - Milestone B
PL-013616 |  | EACOP-PS5-60-23-0172 | B | P | 18.2:Equpiment connection joint Flange Management to be done | CPP AGI | PS5-60-23 - Instrument Air Distribution lines |  | Originated |  | Equpiment connection joint Flange Management to be done | 2026-08-03T11:31:42.920 | Bhagavath, sangeeth | PS5 - Milestone B
PL-013617 |  | EACOP-PS5-60-23-0172 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-23 - Instrument Air Distribution lines |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-03T11:33:07.740 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:17:44.000
PL-013618 |  | EACOP-PS5-60-23-0172 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-60-23 - Instrument Air Distribution lines |  | Completed |  | Paint touch up to be done | 2026-08-03T11:33:54.007 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:18:18.000
PL-013619 |  | EACOP-PS5-71-21-0331 | B | P | 18:1" valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-03T11:38:01.470 | Bhagavath, sangeeth | PS5 - Milestone B
PL-013620 |  | EACOP-PS5-71-21-0331 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-03T11:38:49.140 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-30T14:23:16.000
PL-013621 |  | EACOP-PS5-71-21-0331 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-03T11:39:35.110 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-30T14:23:59.000
PL-013622 |  | EACOP-PS5-71-21-0331 | A | P | 18.3:Iten 04, TZ-MID-68-WPR2-206788 - Orifice Flange 1/2" Nipple & Flange to be install | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  |  | 2026-08-03T11:40:05.587 | Bhagavath, sangeeth | PS5 - Milestone B
PL-013623 |  | EACOP-PS5-71-21-0331 | A | P | 18.4:ITEM 01, 02 & 03-(TZ-MID-68-WPR2-206883 & TZ-MID-68-WPR2-206883) - PS5-71-FIT-0019 _01 & 02 to be installed. | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | PS5-71-FIT-0019 _01 & 02– to be installed | 2026-08-03T11:41:23.760 | Bhagavath, sangeeth | PS5 - Milestone B
PL-013624 |  | EACOP-PS5-71-21-0331 | A | P | 18.5:PS5 71 PG-0050A & PS5 71 PG-0050B - PRESSURE INSTRUMENT to be install & Flange Management to be done | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | PS5 71 PG-0050A & PS5 71 PG-0050B - PRESSURE INSTRUMENT to be install & Flange Management to be done | 2026-08-03T11:44:31.163 | Bhagavath, sangeeth | PS5 - Milestone B
PL-013625 |  | EACOP-PS5-60-46-0217 | B | P | 18:Paint touch up to be done | CPP AGI | PS5-60-46 - Oil Mist Separator Skid PS5-60-VS-9100E |  | Originated |  | Paint touch up to be done | 2026-08-03T11:50:58.900 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013626 |  | EACOP-PS5-60-72-0263 | B | P | 18:PS5-60-UR-8100C-TP_833, TP_834 & TP_835 - Equpiment joint Flange Management to be done | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  |  | 2026-08-03T11:57:06.970 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013627 |  | EACOP-PS5-60-72-0263 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-03T11:58:18.853 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:57:37.000
PL-013628 |  | EACOP-PS5-60-72-0263 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | Paint touch up to be done | 2026-08-03T11:58:51.760 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:58:04.000
PL-013636 | PS5-05-IE-8100-CC01 |  | C | I | Missing Indoor Cable tag (Yellow tag With Black Font) | KENT | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | To be arrange the Indoor Cable tag (Yellow tag With Black Font) | 2026-08-03T13:54:57.663 | Kumar, Senthil | PS5 - Milestone C
PL-013637 | PS5-05-IE-8100-CC01 |  | B | I | MCT not Properly Closed | KENT | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | To be Close the MCT Proper | 2026-08-03T13:59:13.260 | Kumar, Senthil | PS5 - Milestone C
PL-013638 | PS5-05-IE-8100-CC01 |  | B | I | No Proper Armour Earth | KENT | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | To be arrange the Proper Armour Earth | 2026-08-03T14:01:27.237 | Kumar, Senthil | PS5 - Milestone C
PL-013639 | PS5-05-IE-8100-CC01 |  | B | I | No Proper Cable Dressing inside the Panel | KENT | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | To be arrange the Proper Cable Dressing | 2026-08-03T14:03:37.773 | Kumar, Senthil | PS5 - Milestone C
PL-013640 | PS5-05-IE-8100-CC02 |  | C | I | Missing Indoor Cable tag (Yellow tag With Black Font) | KENT | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | To be arrange the Indoor Cable tag (Yellow tag With Black Font) | 2026-08-03T14:14:20.077 | Kumar, Senthil | PS5 - Milestone C
PL-013641 | PS5-05-IE-8100-CC02 |  | B | I | No Proper Armour Earthing | KENT | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | To be arrange the Armour Earthing Proper | 2026-08-03T14:15:39.160 | Kumar, Senthil | PS5 - Milestone C
PL-013642 | PS5-05-IE-8100-CC02 |  | B | I | No Properly closed the MCT Entry | KENT | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | To be close properly the MCT entry | 2026-08-03T14:17:12.583 | Kumar, Senthil | PS5 - Milestone C
PL-013643 | PS5-05-IE-8100-CC02 |  | C | I | No Cable Tag (Outdoor Metal Tag) | CPP AGI | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | To be arrange the Outdoor Metal Tag for Cable | 2026-08-03T14:19:20.700 | Kumar, Senthil | PS5 - Milestone C
PL-013645 | PS5-05-IE-8100-CD09 |  | C | E | Missing Indoor Cable Tag (Yellow Colour With Black Font) | KENT | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | To be arrange the Missing Indoor Cable Tag (Yellow Colour With Black Font) | 2026-08-03T15:50:12.303 | Kumar, Senthil | PS5 - Milestone C
PL-013646 | PS5-05-IE-8100-CD22 |  | C | E | Missing Indoor Cable Tag (Yellow Colour With Black Font) | KENT | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | To be arrange the Missing Indoor Cable Tag (Yellow Colour With Black Font) | 2026-08-03T16:02:01.043 | Kumar, Senthil | PS5 - Milestone C
PL-013647 | PS5-05-IE-8100-CD24 |  | C | E | Missing Indoor Cable Tag (Yellow Colour With Black Font) | KENT | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | To be arrange the Missing Indoor Cable Tag (Yellow Colour With Black Font) | 2026-08-03T16:09:09.143 | Kumar, Senthil | PS5 - Milestone C
PL-013648 | PS5-61-IK-0001-CL02 |  | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Use the proper Nut Bolts for Transformer Side Termination points | 2026-08-04T05:00:16.137 | Kumar, Senthil | PS5 - Milestone A
PL-013649 | PS5-61-IK-0001-CL02 |  | C | E | Missing cable tag - Indoor & Inside cabin (Yellow tag with black font) | KENT | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | To be Provide the indoor Cable Tags (Yellow tag with black font) | 2026-08-04T05:00:34.323 | Kumar, Senthil | PS5 - Milestone A
PL-013655 | PS5-60-TG-0006E |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-08-04T05:39:13.067 | Gawad, Mohamed | PS5 - Milestone D
PL-013657 | PS5-60-TG-0007E |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-08-04T05:41:34.890 | Gawad, Mohamed | PS5 - Milestone D
PL-013659 | PS5-60-TG-0008E |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-08-04T05:43:37.037 | Gawad, Mohamed | PS5 - Milestone D
PL-013681 |  | EACOP-PS5-60-13-0163 | B | P | 18: 1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-13 - Power Generation Package E |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-04T08:42:48.193 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013682 |  | EACOP-PS5-60-13-0163 | B | P | 18.1:PS5-60-UR-8100E-TP_1040 & TP_1041 - Equpiment joint Flange Management to be done | CPP AGI | PS5-60-13 - Power Generation Package E |  | Originated |  | Equpiment joint Flange Management to be done | 2026-08-04T08:43:33.290 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013683 |  | EACOP-PS5-60-13-0163 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-13 - Power Generation Package E |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-04T08:44:41.603 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:25:37.000
PL-013684 |  | EACOP-PS5-60-13-0163 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-13 - Power Generation Package E |  | Completed |  | Paint touch up to be done | 2026-08-04T08:45:17.797 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:26:15.000
PL-013685 | PS5-60-BE-0025A-CL01 |  | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | CPP AGI | PS5-60-35 - Injector Tip Cooling Module A |  | Originated |  | Install the earthing cable for the cable gland earthing tags at both ends | 2026-08-04T09:48:01.007 | Gawad, Mohamed | PS5 - Milestone B
PL-013687 | PS5-60-BE-0025B-CL01 |  | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | CPP AGI | PS5-60-36 - Injector Tip Cooling Module B |  | Originated |  | Install the earthing cable for the cable gland earthing tags at both ends | 2026-08-04T10:02:29.613 | Gawad, Mohamed | PS5 - Milestone B
PL-013688 | PS5-60-BE-0026A-CL02 |  | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Install the earthing cable for the cable gland earthing tags at both ends | 2026-08-04T10:06:29.703 | Gawad, Mohamed | PS5 - Milestone B
PL-013689 | PS5-60-BE-0026B-CL02 |  | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | Install the earthing cable for the cable gland earthing tags at both ends | 2026-08-04T10:08:29.857 | Gawad, Mohamed | PS5 - Milestone B
PL-013690 | PS5-60-BI-0015A-CL01 |  | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Install the earthing cable for the cable gland earthing tags at both ends | 2026-08-04T10:13:42.730 | Gawad, Mohamed | PS5 - Milestone B
PL-013691 | PS5-60-BI-0015A-CL01 |  | B | E | Mismatching Drawing at Skid Side | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Review the drawing and rectify the installation at the skid side to match the latest approved drawing | 2026-08-04T10:14:02.650 | Gawad, Mohamed | PS5 - Milestone B
PL-013692 | PS5-60-BI-0015A-CL02 |  | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Install the earthing cable for the cable gland earthing tags at both ends | 2026-08-04T10:20:06.123 | Gawad, Mohamed | PS5 - Milestone B
PL-013693 | PS5-60-BI-0015A-CL02 |  | B | E | Mismatching Drawing at Skid Side | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Review the drawing and rectify the installation at the skid side to match the latest approved drawing | 2026-08-04T10:20:31.820 | Gawad, Mohamed | PS5 - Milestone B
PL-013694 | PS5-60-BI-0015B-CL01 |  | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Install the earthing cable for the cable gland earthing tags at both ends | 2026-08-04T10:22:42.660 | Gawad, Mohamed | PS5 - Milestone B
PL-013695 | PS5-60-BI-0015B-CL01 |  | B | E | Mismatching Drawing at Skid Side | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Review the drawing and rectify the installation at the skid side to match the latest approved drawing | 2026-08-04T10:23:04.003 | Gawad, Mohamed | PS5 - Milestone B
PL-013696 | PS5-60-BI-0015B-CL02 |  | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Install the earthing cable for the cable gland earthing tags at both ends | 2026-08-04T10:24:44.573 | Gawad, Mohamed | PS5 - Milestone B
PL-013697 | PS5-60-BI-0015B-CL02 |  | B | E | Mismatching Drawing at Skid Side | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Review the drawing and rectify the installation at the skid side to match the latest approved drawing | 2026-08-04T10:25:31.363 | Gawad, Mohamed | PS5 - Milestone B
PL-013698 | PS5-60-BI-0015B-CL03 |  | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Install the earthing cable for the cable gland earthing tags at both ends | 2026-08-04T10:29:51.050 | Gawad, Mohamed | PS5 - Milestone B
PL-013699 | PS5-60-BI-0015B-CL03 |  | B | E | Mismatching Drawing at Skid Side | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Review the drawing and rectify the installation at the skid side to match the latest approved drawing | 2026-08-04T10:30:14.660 | Gawad, Mohamed | PS5 - Milestone B
PL-013700 | PS5-60-IN-0001A-CL01 |  | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | CPP AGI | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A |  | Originated |  | Install the earthing cable for the cable gland earthing tags at both ends | 2026-08-04T10:33:08.573 | Gawad, Mohamed | PS5 - Milestone B
PL-013701 | PS5-60-IN-0001B-CL01 |  | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | CPP AGI | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B |  | Originated |  | Install the earthing cable for the cable gland earthing tags at both ends | 2026-08-04T10:35:07.877 | Gawad, Mohamed | PS5 - Milestone B
PL-013702 | PS5-60-VS-9100A-CL01 |  | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | CPP AGI | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A |  | Originated |  | Install the earthing cable for the cable gland earthing tags at both ends | 2026-08-04T10:37:42.590 | Gawad, Mohamed | PS5 - Milestone B
PL-013703 | PS5-60-VS-9100B-CL01 |  | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | CPP AGI | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B |  | Originated |  | Install the earthing cable for the cable gland earthing tags at both ends | 2026-08-04T10:40:36.717 | Gawad, Mohamed | PS5 - Milestone B
PL-013704 |  | EACOP-PS5-60-13-0164 | B | P | 18:PS5-60-UR-8100E-TP_1043 - Equpiment joint Flange Management to be done | CPP AGI | PS5-60-13 - Power Generation Package E |  | Originated |  | Equpiment joint Flange Management to be done | 2026-08-04T10:52:10.347 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013705 |  | EACOP-PS5-60-13-0164 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-13 - Power Generation Package E |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-04T10:52:56.307 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:27:29.000
PL-013706 |  | EACOP-PS5-60-13-0164 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-60-13 - Power Generation Package E |  | Completed |  | Paint touch up to be done | 2026-08-04T10:53:38.747 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:28:08.000
PL-013708 |  | EACOP-PS5-60-53-0231 | B | P | 18:PS5-60-UR-8100E-TP_0873 & TP_0874 - Equpiment joint Flange Management to be done | CPP AGI | PS5-60-53 - Lube Oil Separator Module PS5-60-UO-81100E |  | Originated |  | Equpiment joint Flange Management to be done | 2026-08-04T11:23:51.593 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013709 |  | EACOP-PS5-60-53-0231 | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-53 - Lube Oil Separator Module PS5-60-UO-81100E |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-04T11:26:14.527 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013710 |  | EACOP-PS5-60-53-0231 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-53 - Lube Oil Separator Module PS5-60-UO-81100E |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-04T11:27:21.420 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:28:33.000
PL-013711 |  | EACOP-PS5-60-53-0231 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-53 - Lube Oil Separator Module PS5-60-UO-81100E |  | Completed |  | Paint touch up to be done | 2026-08-04T11:27:54.653 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:29:04.000
PL-013712 |  | EACOP-PS5-60-64-0244 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-04T11:34:04.830 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013713 |  | EACOP-PS5-60-64-0244 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-04T11:34:47.190 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:29:59.000
PL-013714 |  | EACOP-PS5-60-64-0244 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E |  | Completed |  | Paint touch up to be done | 2026-08-04T11:35:17.330 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:30:30.000
PL-013715 |  | EACOP-PS5-60-66-0246 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-04T11:46:40.270 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013716 |  | EACOP-PS5-60-66-0246 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-04T11:47:29.193 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013717 |  | EACOP-PS5-60-66-0246 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Originated |  | Paint touch up to be done | 2026-08-04T11:48:02.380 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013719 | PS5-28-PA-3300 |  | B | M | 14:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN | CPP AGI | PS5-28-06 - Relief Drum and Pump |  | Originated |  |  | 2026-08-04T12:25:49.587 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-013720 | PS5-28-PA-3300 |  | C | M | 14.1:TOUCH UP/PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | CPP AGI | PS5-28-06 - Relief Drum and Pump |  | Originated |  |  | 2026-08-04T12:27:41.717 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-013721 | PS5-28-PA-3300 |  | C | M | 14.2:EARTHING TO BE DONE | CPP AGI | PS5-28-06 - Relief Drum and Pump |  | Originated |  |  | 2026-08-04T12:28:56.003 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-013722 | PS5-75-UI-6100 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-75-02 - Biocide Injection Package |  | Completed |  |  | 2026-08-04T12:40:04.997 | THANGARATHINAM, ajikumar | PS5 - Milestone G | 2026-08-13T08:11:22.000
PL-013723 | PS5-75-UI-6100 |  | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-08-04T12:41:02.790 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-013764 | PS5-60-01_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-08-05T08:29:29.273 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-013821 |  | EACOP-PS5-60-35-0194 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-35 - Injector Tip Cooling Module A |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-05T14:31:19.073 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-14T08:49:13.000
PL-013822 |  | EACOP-PS5-60-35-0194 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-60-35 - Injector Tip Cooling Module A |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-05T14:31:44.880 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:56:38.000
PL-013828 |  | EACOP-PS5-60-36-0196 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-36 - Injector Tip Cooling Module B |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-05T14:47:06.147 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:42:38.000
PL-013829 |  | EACOP-PS5-60-36-0196 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-60-36 - Injector Tip Cooling Module B |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-05T14:47:41.153 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:56:56.000
PL-013831 |  | EACOP-PS5-60-42-0208 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-05T14:53:39.790 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:43:06.000
PL-013832 |  | EACOP-PS5-60-42-0208 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-05T14:54:37.713 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:57:20.000
PL-013833 |  | EACOP-PS5-60-43-0210 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-05T14:59:35.950 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:43:35.000
PL-013834 |  | EACOP-PS5-60-43-0210 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-05T15:00:07.997 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:57:49.000
PL-013836 |  | EACOP-PS5-60-49-0222 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-05T15:04:55.097 | Bhagavath, sangeeth | PS5 - Milestone B
PL-013838 |  | EACOP-PS5-60-49-0222 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A |  | Originated |  | Paint touchup to be done in damaged area | 2026-08-05T15:05:28.607 | Bhagavath, sangeeth | PS5 - Milestone B
PL-013859 |  | EACOP-PS5-60-50-0224 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-06T04:09:26.310 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:44:07.000
PL-013860 |  | EACOP-PS5-60-50-0224 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-06T04:09:58.130 | Bhagavath, sangeeth | PS5 - Milestone B | 2026-08-17T12:58:13.000
PL-013909 |  | EACOP-PS5-60-13-0165 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-13 - Power Generation Package E |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-06T08:22:41.553 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013910 |  | EACOP-PS5-60-13-0165 | B | P | 18.1:PS5-60-UR-8100E_TP-1042 - Equpiment Hose connection Flange Management to be done | CPP AGI | PS5-60-13 - Power Generation Package E |  | Originated |  | Equpiment Hose connection Flange Management to be done | 2026-08-06T08:23:22.870 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013911 |  | EACOP-PS5-60-13-0165 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-13 - Power Generation Package E |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-06T08:24:30.280 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:31:00.000
PL-013913 |  | EACOP-PS5-60-13-0165 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-13 - Power Generation Package E |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-06T08:25:04.110 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:31:26.000
PL-013922 |  | EACOP-PS5-60-16-0166 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-16 - Power Generation Package F |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-06T08:46:34.290 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013923 |  | EACOP-PS5-60-16-0166 | C | P | 18.1:PS5-60-UR-8100F_TP-1044 & TP-1045 - Equpiment Hose connection Flange Management to be done | CPP AGI | PS5-60-16 - Power Generation Package F |  | Originated |  | Equpiment Hose connection Flange Management to be done | 2026-08-06T08:47:39.747 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013924 |  | EACOP-PS5-60-16-0166 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-16 - Power Generation Package F |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-06T08:48:34.140 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:32:01.000
PL-013925 |  | EACOP-PS5-60-16-0166 | B | P | 18.3:Paint touchup to be done | CPP AGI | PS5-60-16 - Power Generation Package F |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-06T08:49:11.713 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:32:24.000
PL-013926 |  | EACOP-PS5-60-16-0167 | B | P | 18:PS5-60-UR-8100F_TP-1047 - Equpiment Hose connection Flange Management to be done | CPP AGI | PS5-60-16 - Power Generation Package F |  | Originated |  | Equpiment Hose connection Flange Management to be done | 2026-08-06T08:53:15.740 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013927 |  | EACOP-PS5-60-16-0167 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-16 - Power Generation Package F |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-06T08:54:02.793 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:32:47.000
PL-013928 |  | EACOP-PS5-60-16-0167 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-60-16 - Power Generation Package F |  | Completed |  | Paint touch up to be done | 2026-08-06T08:56:24.927 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:33:17.000
PL-013931 | PS5-60-BE-0001-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-06T09:55:16.397 | Gawad, Mohamed | PS5 - Milestone B
PL-013932 | PS5-60-BE-0001-CL02 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-06T09:57:20.327 | Gawad, Mohamed | PS5 - Milestone B
PL-013933 | PS5-60-BE-0001-CL04 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-06T09:59:51.960 | Gawad, Mohamed | PS5 - Milestone B
PL-013935 | PS5-60-BE-0002-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-26 - Instrument Air Compressor Skid |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-06T10:01:56.397 | Gawad, Mohamed | PS5 - Milestone B
PL-013936 | PS5-60-BE-0002-CL02 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-26 - Instrument Air Compressor Skid |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both endsEarthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | 2026-08-06T10:03:46.237 | Gawad, Mohamed | PS5 - Milestone B
PL-013939 | PS5-60-BE-0002-CL03 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-26 - Instrument Air Compressor Skid |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-06T10:05:57.980 | Gawad, Mohamed | PS5 - Milestone B
PL-013943 | PS5-60-IH-0002-CL07 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-22 - Power Gen Master UCP |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-06T10:12:49.363 | Gawad, Mohamed | PS5 - Milestone B
PL-013944 | PS5-60-IH-0002-CL07 |  | C | E | Permanent Core marking to be installed at both side | CPP AGI | PS5-60-22 - Power Gen Master UCP |  | Originated |  | Installed permanent core markings at both sides of the cable as per the approved wiring drawing | 2026-08-06T10:13:06.797 | Gawad, Mohamed | PS5 - Milestone B
PL-013945 | PS5-60-IH-0002-CL08 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-22 - Power Gen Master UCP |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-06T10:14:36.253 | Gawad, Mohamed | PS5 - Milestone B
PL-013947 | PS5-60-IH-0002-CL08 |  | C | E | Permanent Core marking to be installed at both side | CPP AGI | PS5-60-22 - Power Gen Master UCP |  | Originated |  | Installed permanent core markings at both sides of the cable as per the approved wiring drawing | 2026-08-06T10:14:53.377 | Gawad, Mohamed | PS5 - Milestone B
PL-013948 | PS5-60-IH-0002-CL09 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-22 - Power Gen Master UCP |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-06T10:16:52.777 | Gawad, Mohamed | PS5 - Milestone B
PL-013949 | PS5-60-IH-0002-CL09 |  | C | E | Permanent Core marking to be installed at both side | CPP AGI | PS5-60-22 - Power Gen Master UCP |  | Originated |  | Installed permanent core markings at both sides of the cable as per the approved wiring drawing | 2026-08-06T10:17:13.363 | Gawad, Mohamed | PS5 - Milestone B
PL-013952 | PS5-60-IH-0002-CL10 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-22 - Power Gen Master UCP |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-06T10:22:09.990 | Gawad, Mohamed | PS5 - Milestone B
PL-013954 | PS5-60-IH-0002-CL10 |  | C | E | Permanent Core marking to be installed at both side | CPP AGI | PS5-60-22 - Power Gen Master UCP |  | Originated |  | Installed permanent core markings at both sides of the cable as per the approved wiring drawing | 2026-08-06T10:22:30.240 | Gawad, Mohamed | PS5 - Milestone B
PL-013958 |  | EACOP-PS5-60-16-0168 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-16 - Power Generation Package F |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-06T10:56:33.440 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013960 |  | EACOP-PS5-60-16-0168 | B | P | 18.1:PS5-60-UR-8100F_TP-1046 - Equpiment Hose connection Flange Management to be done | CPP AGI | PS5-60-16 - Power Generation Package F |  | Originated |  | Equpiment Hose connection Flange Management to be done | 2026-08-06T10:57:41.007 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013961 |  | EACOP-PS5-60-16-0168 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-16 - Power Generation Package F |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-06T10:58:26.237 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:33:42.000
PL-013962 |  | EACOP-PS5-60-16-0168 | B | P | 18.3:Paint touchup to be done | CPP AGI | PS5-60-16 - Power Generation Package F |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-06T10:58:55.207 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:34:06.000
PL-013964 |  | EACOP-PS5-60-54-0233 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-54 - Lube Oil Separator Module PS5-60-UO-81100F |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-06T11:15:34.283 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013965 |  | EACOP-PS5-60-54-0233 | B | P | 18.1:PS5-60-UR-8100F_TP-894 & TP_895 - Equpiment Hose connection Flange Management to be done | CPP AGI | PS5-60-54 - Lube Oil Separator Module PS5-60-UO-81100F |  | Originated |  | Equpiment Hose connection Flange Management to be done | 2026-08-06T11:16:39.047 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013966 |  | EACOP-PS5-60-54-0233 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-54 - Lube Oil Separator Module PS5-60-UO-81100F |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-06T11:17:32.180 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:34:32.000
PL-013968 |  | EACOP-PS5-60-54-0233 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-54 - Lube Oil Separator Module PS5-60-UO-81100F |  | Completed |  | Paint touch up to be done | 2026-08-06T11:22:31.313 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:35:09.000
PL-013973 |  | EACOP-PS5-60-64-0245 | B | P | 18:PS5-60-UR-8100E_TP-867 & TP-868 - Equpiment connection Flange Management to be done | CPP AGI | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E |  | Originated |  | Equpiment connection Flange Management to be done | 2026-08-06T11:32:14.810 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013974 |  | EACOP-PS5-60-64-0245 | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-06T11:34:04.720 | Bhagavath, sangeeth | PS5 - Milestone D
PL-013975 |  | EACOP-PS5-60-64-0245 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-06T11:35:19.003 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:35:32.000
PL-013976 |  | EACOP-PS5-60-64-0245 | B | P | 18.3:Paint touchup to be done | CPP AGI | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-06T11:35:56.823 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:36:09.000
PL-014011 | PS5-61-IK-0001-CL38 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-06T12:30:25.080 | Gawad, Mohamed | PS5 - Milestone A
PL-014012 | PS5-61-IK-0001-CL38 |  | C | E | Permanent Core marking to be installed at both side | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Installed permanent core markings at both sides of the cable as per the approved wiring drawing | 2026-08-06T12:30:48.523 | Gawad, Mohamed | PS5 - Milestone A
PL-014016 | PS5-61-IK-0001-CL39 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-06T12:35:58.097 | Gawad, Mohamed | PS5 - Milestone A
PL-014017 | PS5-61-IK-0001-CL39 |  | C | E | Permanent Core marking to be installed at both side | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Installed permanent core markings at both sides of the cable as per the approved wiring drawing | 2026-08-06T12:36:21.990 | Gawad, Mohamed | PS5 - Milestone A
PL-014019 | PS5-61-IK-0001-CL40 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-06T12:39:31.177 | Gawad, Mohamed | PS5 - Milestone A
PL-014020 | PS5-61-IK-0001-CL40 |  | C | E | Permanent Core marking to be installed at both side | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Installed permanent core markings at both sides of the cable as per the approved wiring drawing | 2026-08-06T12:39:58.773 | Gawad, Mohamed | PS5 - Milestone A
PL-014021 | PS5-01-UB-6100_PIPING_OUTSIDE_BUILDING |  | B | P | The flange connection is resting directly on top of the pipe support. Normally, flange connections should remain free from any obstruction to allow access for future maintenance and flange opening activities. | EITS | PS5-01-09 - Inergen for EITS Building |  | Originated |  | The flange connection is resting directly on top of the pipe support. Need to adjust the pipe support. | 2026-08-06T12:41:35.000 | Kadyrgaliyevich, Nurlanbek | PS5 - Milestone A
PL-014022 | PS5-61-IK-0001-CL41 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-06T12:43:03.727 | Gawad, Mohamed | PS5 - Milestone A
PL-014023 | PS5-61-IK-0001-CL41 |  | C | E | Permanent Core marking to be installed at both side | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Installed permanent core markings at both sides of the cable as per the approved wiring drawing | 2026-08-06T12:43:26.640 | Gawad, Mohamed | PS5 - Milestone A
PL-014029 | PS5-61-IK-0001-CL42 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-06T12:48:11.393 | Gawad, Mohamed | PS5 - Milestone A
PL-014032 | PS5-61-IK-0001-CL42 |  | C | E | Permanent Core marking to be installed at both side | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Installed permanent core markings at both sides of the cable as per the approved wiring drawing | 2026-08-06T12:49:07.137 | Gawad, Mohamed | PS5 - Milestone A
PL-014039 | PS5-61-IK-0001-CL43 |  | B | E | INSULATION TESTER KEW 3125A W8501159 | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | MULTIMETER 15B MAX 64573532WS | 2026-08-06T12:52:48.180 | Gawad, Mohamed | PS5 - Milestone A
PL-014040 | PS5-61-IK-0001-CL43 |  | C | E | Permanent Core marking to be installed at both side | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Installed permanent core markings at both sides of the cable as per the approved wiring drawing | 2026-08-06T12:53:11.627 | Gawad, Mohamed | PS5 - Milestone A
PL-014053 | PS5-60-TG-0005F |  | B | I | Permanent tags and hanging tags to be installeds | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-08-06T13:14:35.417 | Gawad, Mohamed | PS5 - Milestone D
PL-014058 | PS5-60-TG-0006F |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-08-06T13:17:04.490 | Gawad, Mohamed | PS5 - Milestone D
PL-014060 | PS5-60-TG-0007F |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-08-06T13:18:22.073 | Gawad, Mohamed | PS5 - Milestone D
PL-014061 | PS5-60-TG-0008F |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-08-06T13:20:05.493 | Gawad, Mohamed | PS5 - Milestone D
PL-014087 | PS5-60-IE-0003A-CC01 |  | B | I | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-06T13:39:22.160 | Gawad, Mohamed | PS5 - Milestone B
PL-014088 | PS5-60-IE-0003A-CC01 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | internal grounding as per the approved drawing and project specification | 2026-08-06T13:39:44.780 | Gawad, Mohamed | PS5 - Milestone B
PL-014091 | PS5-60-IE-0003A-CC06 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | internal grounding as per the approved drawing and project specification | 2026-08-06T13:44:45.273 | Gawad, Mohamed | PS5 - Milestone B
PL-014092 | PS5-60-IE-0003A-CC07 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | internal grounding as per the approved drawing and project specification | 2026-08-06T13:46:33.220 | Gawad, Mohamed | PS5 - Milestone B
PL-014093 | PS5-60-IE-0003A-CC08 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | internal grounding as per the approved drawing and project specification | 2026-08-06T13:48:11.710 | Gawad, Mohamed | PS5 - Milestone B
PL-014094 | PS5-60-IE-0003A-CC05 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | internal grounding as per the approved drawing and project specification | 2026-08-06T13:54:28.457 | Gawad, Mohamed | PS5 - Milestone B
PL-014112 | PS5-60-BE-0007B-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T04:55:53.540 | Gawad, Mohamed | PS5 - Milestone B
PL-014113 | PS5-60-BE-0007B-CL01 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T04:56:14.687 | Gawad, Mohamed | PS5 - Milestone B
PL-014115 | PS5-60-BE-0007B-CL02 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T04:58:58.343 | Gawad, Mohamed | PS5 - Milestone B
PL-014116 | PS5-60-BE-0007B-CL02 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T05:04:59.680 | Gawad, Mohamed | PS5 - Milestone B
PL-014118 | PS5-60-BE-0007B-CL03 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T05:07:24.250 | Gawad, Mohamed | PS5 - Milestone B
PL-014119 | PS5-60-BE-0007B-CL03 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T05:07:46.783 | Gawad, Mohamed | PS5 - Milestone B
PL-014120 | PS5-60-BI-0006A-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T05:10:53.807 | Gawad, Mohamed | PS5 - Milestone B
PL-014121 | PS5-60-BI-0006A-CL01 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T05:11:16.477 | Gawad, Mohamed | PS5 - Milestone B
PL-014122 | PS5-60-BI-0006A-CL02 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T05:13:25.077 | Gawad, Mohamed | PS5 - Milestone B
PL-014125 | PS5-60-BI-0006A-CL03 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T05:16:27.600 | Gawad, Mohamed | PS5 - Milestone B
PL-014126 | PS5-60-BI-0006A-CL03 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T05:16:48.627 | Gawad, Mohamed | PS5 - Milestone B
PL-014128 | PS5-60-BI-0006A-CL04 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T05:20:10.770 | Gawad, Mohamed | PS5 - Milestone B
PL-014129 | PS5-60-BI-0006A-CL04 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T05:20:36.163 | Gawad, Mohamed | PS5 - Milestone B
PL-014131 | PS5-60-BI-0006A-CL05 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T05:23:07.390 | Gawad, Mohamed | PS5 - Milestone B
PL-014132 | PS5-60-BI-0006A-CL05 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T05:23:31.387 | Gawad, Mohamed | PS5 - Milestone B
PL-014134 |  | EACOP-PS5-60-42-0046 | B | P | 18:Collection Pot Connection & Installation to be done | CPP AGI | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A |  | Originated |  | Collection Pot Connection & Installation to be done | 2026-08-07T05:26:22.087 | Bhagavath, sangeeth | PS5 - Milestone B
PL-014135 | PS5-60-BI-0006A-CL06 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T05:26:24.287 | Gawad, Mohamed | PS5 - Milestone B
PL-014136 | PS5-60-BI-0006A-CL06 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T05:26:45.560 | Gawad, Mohamed | PS5 - Milestone B
PL-014137 |  | EACOP-PS5-60-42-0046 | B | P | 18.1:Paint touch up to be done | CPP AGI | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A |  | Originated |  | Paint touch up to be done | 2026-08-07T05:28:23.950 | Bhagavath, sangeeth | PS5 - Milestone B
PL-014138 | PS5-60-BI-0006A-CL07 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T05:28:41.753 | Gawad, Mohamed | PS5 - Milestone B
PL-014139 | PS5-60-BI-0006A-CL07 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T05:29:02.687 | Gawad, Mohamed | PS5 - Milestone B
PL-014140 | PS5-60-BI-0006A-CL08 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T05:32:01.977 | Gawad, Mohamed | PS5 - Milestone B
PL-014141 | PS5-60-BI-0006A-CL08 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T05:32:28.873 | Gawad, Mohamed | PS5 - Milestone B
PL-014142 |  | EACOP-PS5-60-43-0091 | B | P | 18:Collection Pot Connection & Installation to be done | CPP AGI | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B |  | Originated |  | Collection Pot Connection & Installation to be done | 2026-08-07T05:33:35.540 | Bhagavath, sangeeth | PS5 - Milestone B
PL-014143 | PS5-60-BI-0006A-CL09 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T05:34:26.520 | Gawad, Mohamed | PS5 - Milestone B
PL-014144 |  | EACOP-PS5-60-43-0091 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B |  | Originated |  | Paint touchup to be done in damaged area | 2026-08-07T05:34:44.663 | Bhagavath, sangeeth | PS5 - Milestone B
PL-014145 | PS5-60-BI-0006A-CL09 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T05:34:49.760 | Gawad, Mohamed | PS5 - Milestone B
PL-014146 | PS5-60-BI-0006A-CL10 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T05:37:08.783 | Gawad, Mohamed | PS5 - Milestone B
PL-014148 | PS5-60-BI-0006A-CL10 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T05:37:28.873 | Gawad, Mohamed | PS5 - Milestone B
PL-014150 | PS5-60-BI-0006A-CL11 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T05:39:29.070 | Gawad, Mohamed | PS5 - Milestone B
PL-014151 | PS5-60-BI-0006A-CL11 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T05:39:52.960 | Gawad, Mohamed | PS5 - Milestone B
PL-014152 | PS5-60-BI-0006B-CL04 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T05:42:24.643 | Gawad, Mohamed | PS5 - Milestone B
PL-014153 | PS5-60-BI-0006B-CL04 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T05:42:46.430 | Gawad, Mohamed | PS5 - Milestone B
PL-014154 | PS5-60-BI-0006B-CL05 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T05:44:31.283 | Gawad, Mohamed | PS5 - Milestone B
PL-014155 | PS5-60-BI-0006B-CL05 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T05:44:54.540 | Gawad, Mohamed | PS5 - Milestone B
PL-014157 | PS5-60-BI-0006B-CL06 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T05:47:25.343 | Gawad, Mohamed | PS5 - Milestone B
PL-014158 | PS5-60-BI-0006B-CL06 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T05:47:59.900 | Gawad, Mohamed | PS5 - Milestone B
PL-014159 | PS5-60-BI-0006B-CL10 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T05:56:21.013 | Gawad, Mohamed | PS5 - Milestone B
PL-014160 | PS5-60-BI-0006B-CL10 |  | C | E | SS Cables Tags not yet Install BOTH SIDE | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Installed SS cable tags on both sides of the cable as per the approved cable schedule and project | 2026-08-07T05:56:57.067 | Gawad, Mohamed | PS5 - Milestone B
PL-014199 |  | EACOP-PS5-60-48-0221 | B | P | 18:Paint touch up to be done | CPP AGI | PS5-60-48 - Oil Mist Separator Skid PS5-60-VS-9100G |  | Originated |  | Paint touchup to be done | 2026-08-07T11:38:05.833 | Bhagavath, sangeeth | PS5 - Milestone E
PL-014202 |  | EACOP-PS5-60-19-0169 | B | P | 18:PS5-60-UR-8100G-TP_1048 & TP_1049 - Equpiment joint Flange Management to be done | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | Equpiment joint Flange Management to be done | 2026-08-07T11:49:40.533 | Bhagavath, sangeeth | PS5 - Milestone E
PL-014203 |  | EACOP-PS5-60-19-0169 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-07T11:51:00.377 | Bhagavath, sangeeth | PS5 - Milestone E
PL-014204 |  | EACOP-PS5-60-19-0169 | B | P | 18.2:Paint touchup to be done | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | Paint touchup to be done in damaged area | 2026-08-07T11:51:36.647 | Bhagavath, sangeeth | PS5 - Milestone E
PL-014213 |  | EACOP-PS5-60-19-0170 | B | P | 18:PS5-60-UR-8100G-TP_1051 - Equpiment joint Flange Management to be done | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | Equpiment joint Flange Management to be done | 2026-08-07T12:05:49.303 | Bhagavath, sangeeth | PS5 - Milestone E
PL-014214 |  | EACOP-PS5-60-19-0170 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-07T12:06:36.590 | Bhagavath, sangeeth | PS5 - Milestone E
PL-014215 |  | EACOP-PS5-60-19-0170 | B | P | 18.2:Paint touchup to be done | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | Paint touchup to be done in damaged area | 2026-08-07T12:07:11.437 | Bhagavath, sangeeth | PS5 - Milestone E
PL-014217 |  | EACOP-PS5-60-19-0171 | B | P | 18:PS5-60-UR-8100G-TP_1050 - Equpiment joint Flange Management to be done | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | Equpiment joint Flange Management to be done | 2026-08-07T12:20:34.667 | Bhagavath, sangeeth | PS5 - Milestone E
PL-014218 |  | EACOP-PS5-60-19-0171 | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-07T12:21:39.993 | Bhagavath, sangeeth | PS5 - Milestone E
PL-014220 |  | EACOP-PS5-60-19-0171 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-07T12:22:29.980 | Bhagavath, sangeeth | PS5 - Milestone E
PL-014221 |  | EACOP-PS5-60-19-0171 | B | P | 18.3:Paint touchup to be done | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | Paint touchup to be done in damaged area | 2026-08-07T12:23:13.820 | Bhagavath, sangeeth | PS5 - Milestone E
PL-014235 |  | EACOP-PS5-60-34-0193 | B | P | 18:ITEM 14 / PS5-60-PG-0002G - Instrument joint Flange Management to be done | CPP AGI | PS5-60-34 - Air Receiver G & Air Regulator G |  | Originated |  | Instrument joint Flange Management to be done | 2026-08-07T12:36:47.357 | Bhagavath, sangeeth | PS5 - Milestone E
PL-014236 |  | EACOP-PS5-60-34-0193 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-34 - Air Receiver G & Air Regulator G |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-07T12:37:43.183 | Bhagavath, sangeeth | PS5 - Milestone E
PL-014237 |  | EACOP-PS5-60-34-0193 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-60-34 - Air Receiver G & Air Regulator G |  | Originated |  | Paint touch up to be done | 2026-08-07T12:38:29.123 | Bhagavath, sangeeth | PS5 - Milestone E
PL-014239 |  | EACOP-PS5-60-74-0275 | B | P | 18:PS5-60-UR-8100E_TP-875,TP-876 & TP-877 - Equpiment joint Flange Management to be done | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | Equpiment joint Flange Management to be done | 2026-08-07T12:49:17.913 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014240 |  | EACOP-PS5-60-74-0275 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-07T12:51:41.400 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:36:33.000
PL-014241 |  | EACOP-PS5-60-74-0275 | B | P | 18.2:Paint touch up to be done | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Completed |  | Paint touch up to be done | 2026-08-07T12:52:22.397 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:37:03.000
PL-014269 | PS5-60-BI-0006A-CC01 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | internal grounding as per the approved drawing and project specification | 2026-08-07T13:57:19.703 | Gawad, Mohamed | PS5 - Milestone B
PL-014272 | PS5-60-BI-0006A-CC02 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-57 - Fuel Conditioning Module PS5-60-UZ-8900A (UCP) |  | Originated |  | internal grounding as per the approved drawing and project specification | 2026-08-07T13:59:36.317 | Gawad, Mohamed | PS5 - Milestone B
PL-014273 | PS5-60-BI-0006A-CC03 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-57 - Fuel Conditioning Module PS5-60-UZ-8900A (UCP) |  | Originated |  | internal grounding as per the approved drawing and project specification | 2026-08-07T14:02:18.497 | Gawad, Mohamed | PS5 - Milestone B
PL-014274 | PS5-60-BI-0006A-CC04 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-57 - Fuel Conditioning Module PS5-60-UZ-8900A (UCP) |  | Originated |  | internal grounding as per the approved drawing and project specification | 2026-08-07T14:04:22.273 | Gawad, Mohamed | PS5 - Milestone B
PL-014276 | PS5-60-BI-0006A-CC05 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-57 - Fuel Conditioning Module PS5-60-UZ-8900A (UCP) |  | Originated |  | internal grounding as per the approved drawing and project specification | 2026-08-07T14:06:50.643 | Gawad, Mohamed | PS5 - Milestone B
PL-014277 | PS5-60-BI-0006A-CC06 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-57 - Fuel Conditioning Module PS5-60-UZ-8900A (UCP) |  | Originated |  | internal grounding as per the approved drawing and project specification | 2026-08-07T14:09:27.580 | Gawad, Mohamed | PS5 - Milestone B
PL-014278 | PS5-60-BI-0017A-CC02 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | internal grounding as per the approved drawing and project specification | 2026-08-07T14:11:34.440 | Gawad, Mohamed | PS5 - Milestone B
PL-014279 | PS5-60-VS-9101A-CC01 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A |  | Originated |  | internal grounding as per the approved drawing and project specification | 2026-08-07T14:13:49.963 | Gawad, Mohamed | PS5 - Milestone B
PL-014280 | PS5-60-VS-9101B-CC01 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B |  | Originated |  | internal grounding as per the approved drawing and project specification | 2026-08-07T14:17:18.833 | Gawad, Mohamed | PS5 - Milestone B
PL-014286 | PS5-05-IE-8100-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T16:08:48.237 | Gawad, Mohamed | PS5 - Milestone C
PL-014287 | PS5-05-IE-8100-CL02 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T16:11:11.413 | Gawad, Mohamed | PS5 - Milestone C
PL-014288 | PS5-60-BI-0005A-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T16:13:11.623 | Gawad, Mohamed | PS5 - Milestone B
PL-014289 | PS5-60-BI-0005B-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T16:20:14.520 | Gawad, Mohamed | PS5 - Milestone B
PL-014290 | PS5-60-IE-0002B-CL02 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T16:22:13.240 | Gawad, Mohamed | PS5 - Milestone B
PL-014291 | PS5-60-IE-0003A-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T16:24:06.327 | Gawad, Mohamed | PS5 - Milestone B
PL-014292 | PS5-60-IE-0003A-CL02 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T16:25:53.610 | Gawad, Mohamed | PS5 - Milestone B
PL-014293 | PS5-60-IE-0003B-CL02 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T16:27:40.420 | Gawad, Mohamed | PS5 - Milestone B
PL-014294 | PS5-60-IH-0001A-CL06 |  | A | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs |  | Completed |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T16:29:26.087 | Gawad, Mohamed | PS5 - Milestone B | 2026-08-27T08:57:23.000
PL-014295 | PS5-60-IH-0001B-CL06 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T16:31:08.713 | Gawad, Mohamed | PS5 - Milestone B
PL-014303 | PS5-05-IE-8100-CD09 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T17:28:18.073 | Gawad, Mohamed | PS5 - Milestone C
PL-014304 | PS5-05-IE-8100-CD22 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T17:34:47.037 | Gawad, Mohamed | PS5 - Milestone C
PL-014305 | PS5-05-IE-8100-CD24 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-05-02 - Emergency Diesel Generator Package (UCP) |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T17:37:12.923 | Gawad, Mohamed | PS5 - Milestone C
PL-014306 | PS5-60-BE-0024A-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-35 - Injector Tip Cooling Module A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T17:40:45.310 | Gawad, Mohamed | PS5 - Milestone B
PL-014307 | PS5-60-BE-0024A-CL02 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-35 - Injector Tip Cooling Module A |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T17:42:27.887 | Gawad, Mohamed | PS5 - Milestone B
PL-014308 | PS5-60-BE-0024B-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-36 - Injector Tip Cooling Module B |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T17:43:59.537 | Gawad, Mohamed | PS5 - Milestone B
PL-014309 | PS5-60-BE-0024B-CL02 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-36 - Injector Tip Cooling Module B |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-07T17:45:31.330 | Gawad, Mohamed | PS5 - Milestone B
PL-014311 | PS5-60-BI-0001A-CC01 |  |  | I | 14: | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2026-08-08T05:35:47.477 | Gawad, Mohamed | PS5 - Milestone B
PL-014314 | PS5-60-IE-0003A-CC09 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-08T06:07:45.567 | Gawad, Mohamed | PS5 - Milestone B
PL-014318 | PS5-60-IE-0003A-CC17 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-08T06:10:45.933 | Gawad, Mohamed | PS5 - Milestone B
PL-014319 | PS5-60-IE-0003A-CC23 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-08T06:22:26.640 | Gawad, Mohamed | PS5 - Milestone B
PL-014320 | PS5-60-IE-0003A-CC24 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-08T06:25:22.670 | Gawad, Mohamed | PS5 - Milestone B
PL-014399 | PS5-75-UI-6300 |  | B | M | 4:The nut for the 1/2-inch pipe U-clamp was missing. | EPS VENDOR | PS5-75-03 - Corrosion Inhibitor Injection Package |  | Originated |  |  | 2026-08-08T10:11:56.440 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-014400 | PS5-75-UI-6300 |  | B | M | 4.1:The U-clamp was found to be improperly installed | EPS VENDOR | PS5-75-03 - Corrosion Inhibitor Injection Package |  | Originated |  |  | 2026-08-08T10:13:29.630 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-014401 | PS5-75-UI-6300 |  | A | M | 4.2:"Oil leakage was observed from the diaphragm pump (PS5-75-PB-3100A)." | EPS VENDOR | PS5-75-03 - Corrosion Inhibitor Injection Package |  | Originated |  |  | 2026-08-08T10:14:35.137 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-014402 | PS5-75-UI-6300 |  | A | M | 4.3:"Oil leakage was observed from the diaphragm pump (PS5-75-PB-3100B)." | EPS VENDOR | PS5-75-03 - Corrosion Inhibitor Injection Package |  | Originated |  |  | 2026-08-08T10:15:23.737 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-014403 | PS5-75-UI-6300 |  | B | M | 4.4:The vent holes on the pad plate are not sealed | EPS VENDOR | PS5-75-03 - Corrosion Inhibitor Injection Package |  | Originated |  |  | 2026-08-08T10:16:24.557 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-014404 | PS5-75-UI-6300 |  | B | M | 4.5: 2" pipe U-clamp was found missing | EPS VENDOR | PS5-75-03 - Corrosion Inhibitor Injection Package |  | Originated |  |  | 2026-08-08T10:17:19.850 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-014405 | PS5-75-UI-6300 |  | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-75-03 - Corrosion Inhibitor Injection Package |  | Completed |  |  | 2026-08-08T10:22:45.963 | THANGARATHINAM, ajikumar | PS5 - Milestone G | 2026-08-08T10:23:28.000
PL-014421 | PS5-25-PA-3100A |  | B | M | "The material with Serial No. 104490004028 arrived without a packing list and is an overage item (Attach picture)" | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2026-08-08T11:33:16.000 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-014423 | PS5-25-PA-3100A |  | B | M | "The material with Serial No. 104490004028 arrived without a packing list and is an overage item (Attach picture)" | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Completed |  | vebdor to rectify | 2026-08-08T11:34:51.000 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-08-08T11:40:01.000
PL-014430 | PS5-25-PA-3100A |  | B | M | "The material with Serial No. 104490004028 arrived without a packing list and is an overage item (Attach picture)" | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Completed |  | VENDOR TO RECTIFY | 2026-08-08T11:45:37.000 | THANGARATHINAM, ajikumar | PS5 - Milestone H | 2026-08-08T11:46:59.000
PL-014433 | PS5-74-UB-5100 |  | A | M | The spool is not suitable for installation. The spool needs to be modified to fit properly and allow correct installation. | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Completed |  | VENDOR TO RECTIFY | 2026-08-08T11:48:10.000 | THANGARATHINAM, ajikumar | PS5 - Milestone F | 2026-08-08T11:52:39.000
PL-014444 | PS5-71-IN-0003-CC06 |  | C | I | Missing Indoor Cable Tag(Yellow Tag) | KENT | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP) |  | Originated |  | To be Provide Missing Indoor Cable Tag(Yellow Tag) | 2026-08-08T15:04:07.937 | Kumar, Senthil | PS5 - Milestone B
PL-014445 | PS5-71-IN-0003-CC06 |  | B | I | No Proper MCT Packing | KENT | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP) |  | Originated |  | To be Close the MCT proper | 2026-08-08T15:09:27.327 | Kumar, Senthil | PS5 - Milestone B
PL-014446 | PS5-71-IN-0003-CC06 |  | B | I | No Proper Earth clamp for Armour | KENT | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP) |  | Originated |  | To be arrange Proper Earth clamp for Armour | 2026-08-08T15:11:54.540 | Kumar, Senthil | PS5 - Milestone B
PL-014447 | PS5-71-IN-0003-CC06 |  | C | I | Missing Metal cable tag | CPP AGI | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP) |  | Originated |  | To be Arrange the Metal cable tag | 2026-08-08T15:13:41.930 | Kumar, Senthil | PS5 - Milestone B
PL-014458 | PS5-71-IN-0003-CC07 |  | C | I | Missing Indoor Cable Tag (Yellow Colour with Black font) | KENT | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP) |  | Originated |  | To be provide the Missing Indoor Cable Tag (Yellow Colour with Black font) | 2026-08-09T23:24:10.850 | Kumar, Senthil | PS5 - Milestone B
PL-014459 | PS5-71-IN-0003-CC07 |  | B | I | No Proper Earth Clamp for Armour Earth | KENT | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP) |  | Originated |  | To be Provide the Proper Earth Clamp for Armour Earth | 2026-08-09T23:25:19.680 | Kumar, Senthil | PS5 - Milestone B
PL-014460 | PS5-71-IN-0003-CC07 |  | B | I | The MCT is not closed properly. | KENT | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP) |  | Originated |  | To be Close the MCT properly. | 2026-08-09T23:26:41.257 | Kumar, Senthil | PS5 - Milestone B
PL-014461 | PS5-71-IN-0003-CC07 |  | C | I | Missing Metal Cable Tag (Out Door) | CPP AGI | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP) |  | Completed |  | To be Provide the Missing Metal Cable Tag (Out Door) | 2026-08-09T23:31:03.067 | Kumar, Senthil | PS5 - Milestone B | 2026-08-16T08:16:40.000
PL-014462 | PS5-25-BI-1301-CC01 |  | C | I | Missing Indoor Cable Tag (Yellow Colour With Black Font) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide the Missing Indoor Cable Tag (Yellow Colour With Black Font) | 2026-08-09T23:42:21.100 | Kumar, Senthil | PS5 - Milestone A
PL-014463 | PS5-25-BI-2301-CC01 |  | C | I | Missing Indoor Cable Tag (Yellow Colour With Black Font) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be provide the Missing Indoor Cable Tag (Yellow Colour With Black Font) | 2026-08-09T23:51:54.207 | Kumar, Senthil | PS5 - Milestone A
PL-014464 | PS5-25-BI-2301-CC01 |  | C | I | Missing Metal Cable Tag (Out Door) | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be provide the Missing Metal Cable Tag (Out Door) | 2026-08-09T23:53:19.617 | Kumar, Senthil | PS5 - Milestone A
PL-014465 | PS5-25-BI-2312-CC01 |  | C | I | Missing Indoor Cable Tag (Yellow Colour With Black Font) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide the Missing Indoor Cable Tag (Yellow Colour With Black Font) | 2026-08-09T23:59:41.450 | Kumar, Senthil | PS5 - Milestone A
PL-014466 | PS5-25-BI-2312-CC01 |  | B | I | No Proper Earth Clamp for Armour Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be provide the Proper Earth Clamp for Armour Earth | 2026-08-10T00:01:31.290 | Kumar, Senthil | PS5 - Milestone A
PL-014467 | PS5-25-BI-2312-CC01 |  | C | I | Missing the Metal Cable Tag (Outdoor) | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide the Metal Cable Tag (Outdoor) | 2026-08-10T00:02:57.627 | Kumar, Senthil | PS5 - Milestone A
PL-014468 | PS5-60-IE-0003A-CC21 |  | C | I | Missing Indoor Cable Tag (Yellow Colour with Black font) | KENT | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | To be Provide the Missing Indoor Cable Tag (Yellow Colour with Black font) | 2026-08-10T00:15:19.607 | Kumar, Senthil | PS5 - Milestone B
PL-014469 | PS5-60-IE-0003A-CC21 |  | B | I | No Proper Earth Clamp for Armour Earth | KENT | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | To be Provide the Proper Earth Clamp for Armour Earth | 2026-08-10T00:17:05.433 | Kumar, Senthil | PS5 - Milestone B
PL-014470 | PS5-60-IE-0003A-CC21 |  | B | I | MCT not Properly Closed | KENT | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | To be Close the MCT Properly | 2026-08-10T00:19:35.660 | Kumar, Senthil | PS5 - Milestone B
PL-014484 | PS5-61-IU-0001A |  |  | E | 22: | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2026-08-10T07:28:21.360 | Iriyanto, Edy | PS5 - Milestone B
PL-014504 |  | EACOP-PS5-28-03-0077 | B | P | 18:Paint touchup to be done | CPP AGI | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  | Paint touchup to be done in damaged area | 2026-08-10T11:21:30.960 | Bhagavath, sangeeth | PS5 - Milestone G
PL-014505 |  | EACOP-PS5-28-06-0292 | B | P | 18:Paint touchup to be done | CPP AGI | PS5-28-06 - Relief Drum and Pump |  | Originated |  | Paint touchup to be done in damaged area | 2026-08-10T11:25:20.587 | Bhagavath, sangeeth | PS5 - Milestone G
PL-014506 |  | EACOP-PS5-71-01-0356 | B | P | 18:Paint touchup to be done | CPP AGI | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  | Paint touchup to be done in damaged area | 2026-08-10T11:30:15.000 | Bhagavath, sangeeth | PS5 - Milestone H
PL-014507 |  | EACOP-PS5-01-02-0013 | B | P | 18:Pickling and passivation to be done | CPP AGI | PS5-01-02 - Fire Water Pump A |  | Originated |  | Pickling and passivation to be done in rusted area | 2026-08-10T11:52:54.103 | Bhagavath, sangeeth | PS5 - Milestone C
PL-014508 |  | EACOP-PS5-01-02-0013 | B | P | 18.1:Pickling and passivation to be done | CPP AGI | PS5-01-02 - Fire Water Pump A |  | Originated |  | Pickling and passivation to be done in rusted area | 2026-08-10T11:53:53.000 | Bhagavath, sangeeth | PS5 - Milestone C
PL-014509 |  | EACOP-PS5-28-07-0101 | B | P | 18:Paint touchup to be done | CPP AGI | PS5-28-07 - Open Drains (OD2) |  | Originated |  | Paint touchup to be done in damaged area | 2026-08-10T12:05:38.507 | Bhagavath, sangeeth | PS5 - Milestone G
PL-014514 |  | EACOP-PS5-71-15-0319 | B | P | 18:Pickling and passivation | CPP AGI | PS5-71-15 - Diesel Fuel Storage Tank |  | Originated |  | Pickling and passivation to be done in rusted area | 2026-08-10T12:15:46.380 | Bhagavath, sangeeth | PS5 - Milestone F
PL-014541 | PS5-25-BI-2305-CC01 |  | C | I | Missing Indoor Cable tag (Yellow tag With Black Font) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide the Missing Indoor Cable tag (Yellow tag With Black Font) | 2026-08-10T14:58:37.333 | Kumar, Senthil | PS5 - Milestone A
PL-014542 | PS5-25-BI-2305-CC01 |  | B | I | No Proper Earth Clamp for Armour Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be provide the Proper Earth Clamp for Armour Earth | 2026-08-10T15:04:47.630 | Kumar, Senthil | PS5 - Milestone A
PL-014543 | PS5-60-IE-0003B-CC21 |  | C | I | Missing Indoor Cable Tag (Yellow Colour with Black font) | KENT | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | To be Provide the Missing Indoor Cable Tag (Yellow Colour with Black font) | 2026-08-10T15:19:45.087 | Kumar, Senthil | PS5 - Milestone B
PL-014544 | PS5-60-IE-0003B-CC21 |  | B | I | MCT not Properly Closed | KENT | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | To be Close the MCT Properly | 2026-08-10T15:21:14.460 | Kumar, Senthil | PS5 - Milestone B
PL-014545 | PS5-60-IE-0003B-CC21 |  | B | I | No Proper Earth clamp for Armour | KENT | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | To be Provide the Proper Earth clamp for Armour | 2026-08-10T15:22:51.277 | Kumar, Senthil | PS5 - Milestone B
PL-014546 | PS5-60-IE-0003B-CC21 |  | C | I | Missing Outdoor Metal Cable Tag | KENT | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | To be Provide the Missing Outdoor Metal Cable Tag | 2026-08-10T15:24:51.693 | Kumar, Senthil | PS5 - Milestone B
PL-014552 | PS5-71-BI-1305-CC01 |  | C | I | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide the Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | 2026-08-10T16:10:39.313 | Kumar, Senthil | PS5 - Milestone A
PL-014553 | PS5-71-BI-1305-CC01 |  | B | I | No Proper Earth clamp for Armour | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide the Proper Earth clamp for Armour | 2026-08-10T16:12:31.210 | Kumar, Senthil | PS5 - Milestone A
PL-014554 | PS5-71-BI-1305-CC01 |  | C | I | Missing Outdoor Metal Cable Tag | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide the Missing Outdoor Metal Cable Tag | 2026-08-10T16:17:07.320 | Kumar, Senthil | PS5 - Milestone A
PL-014555 | PS5-71-BI-2317-CC01 |  | C | I | Missing Indoor Cable tag (Yellow tag With Black Font) | KENT | PS5-71-15 - Diesel Fuel Storage Tank |  | Originated |  | To be Provide the Missing Indoor Cable tag (Yellow tag With Black Font) | 2026-08-10T16:45:09.027 | Kumar, Senthil | PS5 - Milestone F
PL-014556 | PS5-71-BI-2317-CC01 |  | B | I | No Proper Earth Clamp for Armour Earth | KENT | PS5-71-15 - Diesel Fuel Storage Tank |  | Originated |  | To be Provide Proper Earth Clamp for Armour Earth | 2026-08-10T16:46:09.823 | Kumar, Senthil | PS5 - Milestone F
PL-014557 | PS5-71-BI-2317-CC01 |  | B | I | No Proper MCT Packing | KENT | PS5-71-15 - Diesel Fuel Storage Tank |  | Originated |  | To be Provide Proper MCT Packing | 2026-08-10T16:47:51.087 | Kumar, Senthil | PS5 - Milestone F
PL-014558 | PS5-71-BI-2317-CC01 |  | C | I | Missing Outdoor Metal Cable Tag | CPP AGI | PS5-71-15 - Diesel Fuel Storage Tank |  | Originated |  | To be Provide the Missing Outdoor Metal Cable Tag | 2026-08-10T16:49:02.690 | Kumar, Senthil | PS5 - Milestone F
PL-014590 |  | EACOP-PS5-60-72-0262 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-11T10:49:22.813 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014591 |  | EACOP-PS5-60-72-0262 | B | P | 18.1:PS5-60-UR-8100C_TP-821 & TP-823 - Equpiment joint Flange Management up to be done | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | Equpiment joint Flange Management up to be done | 2026-08-11T10:50:24.993 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014592 |  | EACOP-PS5-60-72-0262 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-11T10:52:01.280 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:58:49.000
PL-014593 |  | EACOP-PS5-60-72-0262 | B | P | 18.3:Paint touchup to be done | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-11T10:52:45.580 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T06:59:26.000
PL-014594 |  | EACOP-PS5-60-72-0264 | B | P | 18:PS5-60-UR-8100C_TP-824 - Equpiment joint Flange Management up to be done | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | Equpiment joint Flange Management up to be done | 2026-08-11T10:58:39.873 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014595 |  | EACOP-PS5-60-72-0264 | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-11T11:00:37.807 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014596 |  | EACOP-PS5-60-72-0264 | B | P | 18.2:TZ-MID-68-WPR2-207120 & TZ-MID-68-WPR2-207123 - Trunnion support to be welded to Structure | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | Trunnion support to be welded to Structure | 2026-08-11T11:01:41.553 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T07:01:49.000
PL-014597 |  | EACOP-PS5-60-72-0264 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-11T11:04:53.903 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T07:02:26.000
PL-014598 |  | EACOP-PS5-60-72-0264 | B | P | 18.4:Paint touch up to be done | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-11T11:05:36.177 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T07:03:49.000
PL-014601 |  | EACOP-PS5-60-72-0265 | B | P | 18:PS5-60-UR-8100C_TP-822 - Equpiment joint Flange Management up to be done | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | Equpiment joint Flange Management up to be done | 2026-08-11T11:13:57.793 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014602 |  | EACOP-PS5-60-72-0265 | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-11T11:14:52.267 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014603 |  | EACOP-PS5-60-72-0265 | B | P | 18.2:TZ-MID-68-WPR2-207128 & TZ-MID-68-WPR2-207131 - Trunnion to be welded to Structure | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | Trunnion to be welded to Structure | 2026-08-11T11:15:40.340 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T07:04:33.000
PL-014604 |  | EACOP-PS5-60-72-0265 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-11T11:17:03.130 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T07:05:26.000
PL-014605 |  | EACOP-PS5-60-72-0265 | B | P | 18.4:Paint touchup to be done | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-11T11:17:36.707 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T07:05:56.000
PL-014608 |  | EACOP-PS5-60-72-0266 | B | P | 18:1" V alve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-11T11:23:43.147 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014609 |  | EACOP-PS5-60-72-0266 | B | P | 18.1:TZ-MID-68-WPR2-207133 & TZ-MID-68-WPR2-207137 - Trunnion to be welded to Structure | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | As per Engineering concern, the trunnion is not welded to the structure. | 2026-08-11T11:24:23.100 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-17T12:59:35.000
PL-014610 |  | EACOP-PS5-60-72-0266 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-11T11:25:13.750 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-17T12:44:31.000
PL-014611 |  | EACOP-PS5-60-72-0266 | B | P | 18.3:Paint touchup to be done | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-11T11:25:43.830 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-17T13:00:48.000
PL-014612 |  | EACOP-PS5-60-72-0267 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-11T11:32:39.737 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014614 |  | EACOP-PS5-60-72-0267 | B | P | 18.1:TZ-MID-68-WPR2-207138 & TZ-MID-68-WPR2-207142 - Trunnion to be welded to Structure | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | Trunnion to be welded to Structure | 2026-08-11T11:33:55.030 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T07:06:30.000
PL-014615 |  | EACOP-PS5-60-72-0267 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-11T11:35:18.320 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T07:07:03.000
PL-014616 |  | EACOP-PS5-60-72-0267 | B | P | 18.3:Paint touch up to be done | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-11T11:36:04.650 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T07:07:37.000
PL-014618 |  | EACOP-PS5-60-73-0271 | B | P | 18:PS5-60-UR-8100D_TP-843 - F-1 Equpiment joint Flange Management up to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | F-1 Equpiment joint Flange Management up to be done | 2026-08-11T11:50:17.083 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014619 |  | EACOP-PS5-60-73-0271 | B | P | 18.1:1" valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-11T11:51:59.490 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014620 |  | EACOP-PS5-60-73-0271 | B | P | 18.2:TZ-MID-68-WPR2-207192 & TZ-MID-68-WPR2-207195 - Trunnion to be welded to Structure | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | Trunnion to be welded to Structure | 2026-08-11T11:53:07.067 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014621 |  | EACOP-PS5-60-73-0271 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-11T11:54:09.380 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:22:15.000
PL-014622 |  | EACOP-PS5-60-73-0271 | B | P | 18.4:Paint touchup to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-11T11:54:46.837 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:22:46.000
PL-014623 |  | EACOP-PS5-60-73-0270 | B | P | 18:PS5-60-UR-8100D_TP-845 - F-1 Equpiment joint Flange Management up to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | F-1 Equpiment joint Flange Management up to be done | 2026-08-11T12:04:43.570 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014624 |  | EACOP-PS5-60-73-0270 | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-11T12:05:40.073 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014625 |  | EACOP-PS5-60-73-0270 | B | P | 18.2:TZ-MID-68-WPR2-207184 & TZ-MID-68-WPR2-207187 - Trunnion to be welded to Structure | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | Trunnion to be welded to Structure | 2026-08-11T12:06:58.497 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014626 |  | EACOP-PS5-60-73-0270 | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-11T12:07:43.977 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:23:13.000
PL-014627 |  | EACOP-PS5-60-73-0270 | B | P | 18.4:Paint touchup to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-11T12:08:32.033 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:23:40.000
PL-014628 |  | EACOP-PS5-60-73-0273 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-11T12:16:50.677 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014629 |  | EACOP-PS5-60-73-0273 | B | P | 18.1:TZ-MID-68-WPR2-207202 & TZ-MID-68-WPR2-207206 - Trunnion to be welded to Structure | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Completed |  | Trunnion to be welded to Structure | 2026-08-11T12:17:27.620 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:38:22.000
PL-014630 |  | EACOP-PS5-60-73-0273 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-11T12:18:17.060 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:39:29.000
PL-014631 |  | EACOP-PS5-60-73-0273 | B | P | 18.3:Paint touchup to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-11T12:18:55.930 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:40:28.000
PL-014632 |  | EACOP-PS5-60-73-0272 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-11T12:27:23.550 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014633 |  | EACOP-PS5-60-73-0272 | B | P | 18.1:TZ-MID-68-WPR2-207197 & TZ-MID-68-WPR2-207201 - Trunnion to be welded to Structure | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | Trunnion to be welded to Structure | 2026-08-11T12:28:16.060 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014634 |  | EACOP-PS5-60-73-0272 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-11T12:30:03.320 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014635 |  | EACOP-PS5-60-73-0272 | B | P | 18.3:Paint touchup to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | Paint touchup to be done in damaged area | 2026-08-11T12:30:55.187 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014636 | PS5-01-UZ-610 |  | B | P | 8:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-01-11 - Inergen for Power Gen Building |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-08-11T12:41:13.213 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-014637 | PS5-01-UZ-610 |  | C | M | 8.1:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-01-11 - Inergen for Power Gen Building |  | Originated |  |  | 2026-08-11T12:44:09.793 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-014638 | PS5-01-UZ-610 |  | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-01-11 - Inergen for Power Gen Building |  | Originated |  |  | 2026-08-11T12:46:55.583 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-014639 |  | EACOP-PS5-60-73-0268 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-11T13:24:48.513 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014640 |  | EACOP-PS5-60-73-0268 | B | P | 18.1:TZ-MID-68-WPR2-208746 & TZ-MID-68-WPR2-208747 - Equpiment joint Flange Management up to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | Equpiment joint Flange Management up to be done | 2026-08-11T13:25:30.977 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014641 |  | EACOP-PS5-60-73-0268 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-11T13:26:22.890 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:24:27.000
PL-014642 |  | EACOP-PS5-60-73-0268 | C | P | 18.3:Paint touchup to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-11T13:26:59.350 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:25:02.000
PL-014643 | PS5-60-TG-0005D |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-08-11T14:19:15.410 | Gawad, Mohamed | PS5 - Milestone D
PL-014654 | PS5-60-TG-0006D |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-08-11T16:43:23.577 | Gawad, Mohamed | PS5 - Milestone D
PL-014655 | PS5-60-TG-0007D |  | B | I | Permanent tags and hanging tags to be installed | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | Permanent tag and hanging tag installed as per project specification | 2026-08-11T16:58:10.650 | Gawad, Mohamed | PS5 - Milestone D
PL-014656 | PS5-60-TG-0008D |  | B | I | Permanent tags and hanging tags to be installeds | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | Permanent tag and hanging tag installed as per project specificationPermanent tag and hanging tag installed as per project specification | 2026-08-11T17:10:24.700 | Gawad, Mohamed | PS5 - Milestone D
PL-014686 | PS5-60-IE-0002A-CC01 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-12T05:30:32.197 | Gawad, Mohamed | PS5 - Milestone B
PL-014688 | PS5-60-IE-0002A-CC03 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-12T05:43:04.397 | Gawad, Mohamed | PS5 - Milestone B
PL-014691 | PS5-60-IE-0003A-CC26 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-12T05:47:24.553 | Gawad, Mohamed | PS5 - Milestone B
PL-014693 | PS5-60-IN-0002A-CC04 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-57 - Fuel Conditioning Module PS5-60-UZ-8900A (UCP) |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-12T05:53:07.717 | Gawad, Mohamed | PS5 - Milestone B
PL-014694 | PS5-60-LA-0002A-CC01 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-12T05:57:43.890 | Gawad, Mohamed | PS5 - Milestone B
PL-014695 | PS5-60-LA-0002A-CC02 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-12T06:00:19.003 | Gawad, Mohamed | PS5 - Milestone B
PL-014696 | PS5-60-LA-0002A-CC03 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-12T06:01:52.617 | Gawad, Mohamed | PS5 - Milestone B
PL-014697 | PS5-60-BI-0006B-CC02 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP) |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-12T06:07:36.497 | Gawad, Mohamed | PS5 - Milestone B
PL-014698 | PS5-60-BI-0006B-CC03 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP) |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-12T06:09:53.733 | Gawad, Mohamed | PS5 - Milestone B
PL-014699 | PS5-60-BI-0006B-CC04 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP) |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-12T06:11:55.600 | Gawad, Mohamed | PS5 - Milestone B
PL-014700 | PS5-60-36_SS_ALL_LINES |  | C | P | 6:COLOUUR CODE AND MARKING TO BE DONE | CPP AGI | PS5-60-36 - Injector Tip Cooling Module B |  | Originated |  | COLOUUR CODE AND MARKING TO BE DONE | 2026-08-12T06:13:25.677 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-014701 | PS5-60-35_SS_ALL_LINES |  | C | P | 6:COLOUR CODE AND MARKING TO BE DONE | CPP AGI | PS5-60-35 - Injector Tip Cooling Module A |  | Originated |  | COLOUR CODE AND MARKING TO BE DONE | 2026-08-12T06:13:26.450 | arun, jabesteen | PS5 - Milestone B
PL-014702 | PS5-60-BI-0006B-CC05 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP) |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-12T06:13:33.610 | Gawad, Mohamed | PS5 - Milestone B
PL-014703 | PS5-60-BI-0006B-CC06 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP) |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-12T06:15:13.693 | Gawad, Mohamed | PS5 - Milestone B
PL-014704 | PS5-60-IE-0002B-CC05 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-12T06:16:56.027 | Gawad, Mohamed | PS5 - Milestone B
PL-014705 | PS5-60-IN-0002B-CC01 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP) |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-12T06:18:46.530 | Gawad, Mohamed | PS5 - Milestone B
PL-014706 | PS5-60-IN-0002B-CC02 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP) |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-12T06:20:43.923 | Gawad, Mohamed | PS5 - Milestone B
PL-014707 | PS5-60-IN-0002B-CC03 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP) |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-12T06:22:28.613 | Gawad, Mohamed | PS5 - Milestone B
PL-014708 | PS5-60-35_SS_ALL_LINES |  | B | P | 6:RING ISTALLED-WIRE MESH TO BE INSTALLED | CPP AGI | PS5-60-35 - Injector Tip Cooling Module A |  | Originated |  | RING ISTALLED-WIRE MESH TO BE INSTALLED | 2026-08-12T06:32:24.687 | arun, jabesteen | PS5 - Milestone B
PL-014709 | PS5-60-36_SS_ALL_LINES |  | B | P | 6:RING INSTALLED-WIREMESH TO BE INSTALLED | CPP AGI | PS5-60-36 - Injector Tip Cooling Module B |  | Originated |  | RING INSTALLED-WIREMESH TO BE INSTALLED | 2026-08-12T06:42:43.580 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-014710 | PS5-60-42_SS_ALL_LINES |  | C | P | 6:COLOUR CODING AND MARKING TO BE DONE | CPP AGI | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A |  | Originated |  | COLOUR CODING AND MARKING TO BE DONE | 2026-08-12T06:46:47.887 | arun, jabesteen | PS5 - Milestone B
PL-014711 | PS5-60-43_SS_ALL_LINES |  | C | P | 6:COLOUR CODE AND MARKING TO BE DONE | CPP AGI | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B |  | Originated |  | COLOUR CODE AND MARKING TO BE DONE | 2026-08-12T06:46:48.797 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-014713 | PS5-60-43_SS_ALL_LINES | EACOP-PS5-60-43-0211 | B | P | 6.1:TP-211- TOPCOAT TOUCHUP TO BE DONE | CPP AGI | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B |  | Originated |  | TP-211- TOP COAT TOUCHUP TO BE DONE | 2026-08-12T06:48:48.547 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-014714 | PS5-60-42_SS_ALL_LINES | EACOP-PS5-60-42-0209 | B | P | TOP COAT TOUCHUP TO BE DONE | CPP AGI | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A |  | Originated |  | TP - EACOP-PS5-60-42-0209-TOP COAT TOUCHUP TO BE DONE | 2026-08-12T06:48:50.383 | arun, jabesteen | PS5 - Milestone B
PL-014849 |  | EACOP-PS5-60-37-0198 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-37 - Injector Tip Cooling Module C |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-13T11:18:23.083 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T07:08:03.000
PL-014851 |  | EACOP-PS5-60-37-0198 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-60-37 - Injector Tip Cooling Module C |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-13T11:20:00.753 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T07:08:34.000
PL-014853 |  | EACOP-PS5-60-38-0200 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-38 - Injector Tip Cooling Module D |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-13T11:24:00.060 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:25:27.000
PL-014854 |  | EACOP-PS5-60-38-0200 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-60-38 - Injector Tip Cooling Module D |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-13T11:24:47.580 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:26:09.000
PL-014858 |  | EACOP-PS5-60-44-0212 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-13T11:29:07.157 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T07:09:07.000
PL-014859 |  | EACOP-PS5-60-44-0212 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-13T11:29:40.080 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T07:09:31.000
PL-014862 |  | EACOP-PS5-60-45-0214 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-13T11:35:04.143 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:26:35.000
PL-014864 |  | EACOP-PS5-60-45-0214 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-13T11:35:42.283 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:27:08.000
PL-014868 |  | EACOP-PS5-60-51-0226 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-13T11:42:10.660 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T07:09:55.000
PL-014869 |  | EACOP-PS5-60-51-0226 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-13T11:43:11.290 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-21T07:10:30.000
PL-014875 |  | EACOP-PS5-60-52-0228 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-13T11:48:51.607 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014877 |  | EACOP-PS5-60-52-0228 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D |  | Originated |  | Paint touchup to be done in damaged area | 2026-08-13T11:49:54.297 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014886 |  | EACOP-PS5-60-44-0213 | B | P | 18:Paint touchup to be done | CPP AGI | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-13T11:55:30.047 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-22T11:27:42.000
PL-014893 |  | EACOP-PS5-60-44-0421 | A | P | 18:Collection Pot Connection & Installation to be done | CPP AGI | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C |  | Originated |  | Collection Pot Connection & Installation to be done | 2026-08-13T11:59:14.250 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014894 |  | EACOP-PS5-60-44-0421 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C |  | Originated |  | Paint touchup to be done in damaged area | 2026-08-13T11:59:49.987 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014898 |  | EACOP-PS5-60-45-0422 | A | P | 18:Collection Pot Connection & Installation to be done | CPP AGI | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D |  | Originated |  | Collection Pot Connection & Installation to be done | 2026-08-13T12:05:15.320 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014901 |  | EACOP-PS5-60-45-0422 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D |  | Originated |  | Paint touchup to be done in damaged area | 2026-08-13T12:05:55.407 | Bhagavath, sangeeth | PS5 - Milestone D
PL-014904 | PS5-60-BE-0026B-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-13T12:22:18.323 | Gawad, Mohamed | PS5 - Milestone B
PL-014905 | PS5-60-BE-0027B-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-13T12:25:48.150 | Gawad, Mohamed | PS5 - Milestone B
PL-014906 | PS5-60-BE-0028B-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-13T12:28:48.557 | Gawad, Mohamed | PS5 - Milestone B
PL-014907 |  | EACOP-PS5-28-06-0354 | B | P | 18:Paint touchup to be done | CPP AGI | PS5-28-06 - Relief Drum and Pump |  | Originated |  | Paint touchup to be done in damaged area | 2026-08-13T12:29:57.553 | Bhagavath, sangeeth | PS5 - Milestone G
PL-014908 | PS5-60-IE-0002B-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-13T12:30:17.773 | Gawad, Mohamed | PS5 - Milestone B
PL-014909 | PS5-60-IE-0003B-CD14 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-13T12:31:51.423 | Gawad, Mohamed | PS5 - Milestone B
PL-014910 | PS5-60-IE-0003B-CL01 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-13T12:33:44.967 | Gawad, Mohamed | PS5 - Milestone B
PL-014911 | PS5-60-IH-0001A-CL05 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-13T12:44:15.630 | Gawad, Mohamed | PS5 - Milestone B
PL-014912 | PS5-60-IH-0001B-CL05 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-13T12:46:46.653 | Gawad, Mohamed | PS5 - Milestone B
PL-014913 |  | EACOP-PS5-71-04-0304 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-71-04 - CFO Storage Tank |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-13T12:48:02.633 | Bhagavath, sangeeth | PS5 - Milestone H
PL-014914 |  | EACOP-PS5-71-04-0304 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-71-04 - CFO Storage Tank |  | Originated |  | Paint touchup to be done in damaged area | 2026-08-13T12:48:57.890 | Bhagavath, sangeeth | PS5 - Milestone H
PL-014915 | PS5-60-IN-0002B-CL02 |  | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | CPP AGI | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP) |  | Originated |  | Connect the cable gland earthing tag to the earthing stud/bar at both ends | 2026-08-13T12:49:21.980 | Gawad, Mohamed | PS5 - Milestone B
PL-014918 |  | EACOP-PS5-71-04-0303 | B | P | 18:PS5-71-TR-4100_N1& N16, PS5-71-SPZQ-0069 - Flange Management to be done | CPP AGI | PS5-71-04 - CFO Storage Tank |  | Originated |  | Flange Management to be done | 2026-08-13T12:59:25.730 | Bhagavath, sangeeth | PS5 - Milestone H
PL-014919 |  | EACOP-PS5-71-04-0303 | B | P | 18.1:Paint touchup to be done | CPP AGI | PS5-71-04 - CFO Storage Tank |  | Originated |  | Paint touchup to be done in damaged area | 2026-08-13T13:01:45.500 | Bhagavath, sangeeth | PS5 - Milestone H
PL-014925 | PS5-60-BI-0008A-CC01 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-13T14:05:08.673 | Gawad, Mohamed | PS5 - Milestone B
PL-014926 | PS5-60-BI-0008A-CC02 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-13T14:06:41.723 | Gawad, Mohamed | PS5 - Milestone B
PL-014927 | PS5-60-BI-0008B-CC01 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-13T14:08:32.693 | Gawad, Mohamed | PS5 - Milestone B
PL-014931 | PS5-60-BI-0008B-CC02 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-13T14:10:47.247 | Gawad, Mohamed | PS5 - Milestone B
PL-014953 | PS5-60-IE-0003A-CC10 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-14T07:02:07.130 | Gawad, Mohamed | PS5 - Milestone B
PL-014954 | PS5-60-IE-0003A-CC11 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-14T07:03:45.137 | Gawad, Mohamed | PS5 - Milestone B
PL-014955 | PS5-60-IE-0003A-CC16 |  | B | I | internal Grounding not yet Done | CPP AGI | PS5-60-02 - Power Gen Package A (UCP) |  | Completed |  | Complete the internal grounding as per the approved drawing and project specification | 2026-08-14T07:05:17.693 | Gawad, Mohamed | PS5 - Milestone B | 2026-08-14T07:07:10.000
PL-015094 |  | EACOP-PS5-28-03-0075 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-15T14:13:53.173 | Bhagavath, sangeeth | PS5 - Milestone G
PL-015095 |  | EACOP-PS5-28-03-0082 | B | P | 18:TZ-MID-68-WPR2-206109 - Flange Insulation Set PS5-28-SPZZ-0023 Flange management to be done | CPP AGI | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  | Flange Insulation Set PS5-28-SPZZ-0023 Flange management to be done | 2026-08-15T14:16:45.140 | Bhagavath, sangeeth | PS5 - Milestone G
PL-015096 |  | EACOP-PS5-28-06-0097 | B | P | 18:TZ-MID-68-WPR2-206094 - Flange Insulation Set PS5-28-SPZZ-0024 Flange management to be done | CPP AGI | PS5-28-06 - Relief Drum and Pump |  | Originated |  | Flange Insulation Set PS5-28-SPZZ-0024 Flange management to be done | 2026-08-15T14:19:52.010 | Bhagavath, sangeeth | PS5 - Milestone G
PL-015097 |  | EACOP-PS5-28-17-0127 | B | P | 18:TZ-MID-68-WPR2-206304 - Pressure Instrument PS5-28-SDV-0045 Flange management to be done | CPP AGI | PS5-28-17 - Reinjection Pump |  | Originated |  | Pressure Instrument PS5-28-SDV-0045 Flange management to be done | 2026-08-15T14:24:41.877 | Bhagavath, sangeeth | PS5 - Milestone H
PL-015098 |  | EACOP-PS5-28-17-0127 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | CPP AGI | PS5-28-17 - Reinjection Pump |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed. | 2026-08-15T14:25:34.880 | Bhagavath, sangeeth | PS5 - Milestone H
PL-015099 |  | EACOP-PS5-71-12-0314 | B | P | 18:PS5-71--TR-4200_N2 - F15 Flange management to be done | CPP AGI | PS5-71-12 - CFO Service Tank |  | Originated |  | F15 Flange management to be done | 2026-08-15T14:30:03.817 | Bhagavath, sangeeth | PS5 - Milestone H
PL-015100 |  | EACOP-PS5-28-09-0108 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-28-09 - Observation Basin |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-15T14:35:54.190 | Bhagavath, sangeeth | PS5 - Milestone I
PL-015101 |  | EACOP-PS5-28-17-0387 | B | P | 18:TZ-MID-68-WPR2-208395 - Civil structure to be installed & GL02 welding to be done after structure instalation | CPP AGI | PS5-28-17 - Reinjection Pump |  | Originated |  | Civil structure to be installed & GL02 welding to be done after structure instalation | 2026-08-15T14:47:10.013 | Bhagavath, sangeeth | PS5 - Milestone H
PL-015148 | PS5-60-BE-0004A-CC01 |  | B | I | PS5-60-IN-0001A TB 100 X2 11, 12 NOT TERMINATED DWG ISSUE | CPP AGI | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A |  | Originated |  | Terminate TB100-X2 terminals 11 & 12 at PS5-60-IN-0001A. Resolve drawing issue prior to termination. | 2026-08-16T14:12:19.133 | Gawad, Mohamed | PS5 - Milestone B
PL-015149 | PS5-60-BI-0017B-CC02 |  | B | I | Grounding between Gland to Gland not yet Installed | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Install Equipotential Bonding Jumper Gland to Gland as per approved design drawing. | 2026-08-16T14:19:25.940 | Gawad, Mohamed | PS5 - Milestone B
PL-015150 | PS5-60-IE-0003B-CC05 |  | B | I | PS5-60-IE-0001B TB Numbers 25,8,0,1,4,5,14,49 NOT AVAILBUL IN THE PANEL | CPP AGI | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | Install missing Terminal Blocks (TB No. 25, 8, 0, 1, 4, 5, 14, 49) in the panel at PS5-60-IE-0001B as per approved design drawing. | 2026-08-16T14:30:26.620 | Gawad, Mohamed | PS5 - Milestone B
PL-015151 | PS5-60-IN-0001A-CC02 |  | B | I | JB - PS5-60-BE-0004A TB XI 3,4 NOT TERMINATED DWG ISSUE | CPP AGI | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A |  | Originated |  | Terminate JB - PS5-60-BE-0004A TB XI 3,4 . Resolve drawing issue prior to termination. | 2026-08-16T14:33:37.820 | Gawad, Mohamed | PS5 - Milestone B
PL-015152 | PS5-60-IN-0001A-CC04 |  | B | I | JB - PS5-60-BE-0004A TB XI 14,15,16 NOT TERMINATED DWG ISSUE | CPP AGI | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A |  | Originated |  | Terminate JB - PS5-60-BE-0004A TB XI 14,15,16. Resolve drawing issue prior to termination. | 2026-08-16T14:36:47.740 | Gawad, Mohamed | PS5 - Milestone B
PL-015206 |  | EACOP-PS5-60-25-0182 | B | P | 18: CONN. TO PS4-60-PA-3400/SN EQUIPMENT NOZZLE CONNECTION TO BE DONE AFTER GALT | CPP AGI | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | EQUIPMENT NOZZLE CONNECTION TO BE DONE AFTER GALT | 2026-08-17T10:30:23.203 | Kumar, Vijaya | PS5 - Milestone E
PL-015306 | PS5-01-BI-1118-CC01 |  | B | I | Grounding between Gland to Gland not yet Installed | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Originated |  | Install Equipotential Bonding Jumper Gland to Gland as per approved design drawing. | 2026-08-17T16:37:38.993 | Gawad, Mohamed | PS5 - Milestone A
PL-015307 | PS5-25-BI-1102-CC01 |  | B | I | Grounding between Gland to Gland not yet Installed | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Originated |  | Install Equipotential Bonding Jumper Gland to Gland as per approved design drawing. | 2026-08-17T16:46:19.243 | Gawad, Mohamed | PS5 - Milestone A
PL-015308 | PS5-25-BI-1115-CC01 |  | B | I | Grounding between Gland to Gland not yet Installed | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Originated |  | Install Equipotential Bonding Jumper Gland to Gland as per approved design drawing. | 2026-08-17T16:48:56.730 | Gawad, Mohamed | PS5 - Milestone A
PL-015309 | PS5-28-BI-1105-CC01 |  | B | I | Grounding between Gland to Gland not yet Installed | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Originated |  | Install Equipotential Bonding Jumper Gland to Gland as per approved design drawing. | 2026-08-17T16:52:47.170 | Gawad, Mohamed | PS5 - Milestone A
PL-015310 | PS5-50-BI-1107-CC01 |  | B | I | Grounding between Gland to Gland not yet Installed | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Originated |  | Install Equipotential Bonding Jumper Gland to Gland as per approved design drawing. | 2026-08-17T16:57:43.663 | Gawad, Mohamed | PS5 - Milestone A
PL-015311 | PS5-60-IE-0003B-CC06 |  | B | I | Grounding between Gland to Gland not yet Installed | CPP AGI | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | Install Equipotential Bonding Jumper Gland to Gland as per approved design drawing. | 2026-08-17T17:06:03.570 | Gawad, Mohamed | PS5 - Milestone B
PL-015312 | PS5-60-IE-0003B-CC07 |  | B | I | Grounding between Gland to Gland not yet Installed | CPP AGI | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | Install Equipotential Bonding Jumper Gland to Gland as per approved design drawing. | 2026-08-17T17:09:15.640 | Gawad, Mohamed | PS5 - Milestone B
PL-015313 | PS5-60-IE-0003B-CC08 |  | B | I | Grounding between Gland to Gland not yet Installed | CPP AGI | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | Install Equipotential Bonding Jumper Gland to Gland as per approved design drawing. | 2026-08-17T17:12:44.787 | Gawad, Mohamed | PS5 - Milestone B
PL-015314 | PS5-60-IE-0003B-CC08 |  | B | I | TB X1101 - TB 31,32,33,34 CORE NOT TERMIANTED | CPP AGI | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | Review the drawing and rectify to match the latest approved drawing | 2026-08-17T17:13:20.293 | Gawad, Mohamed | PS5 - Milestone B
PL-015315 | PS5-60-IE-0003B-CC09 |  | B | I | Grounding between Gland to Gland not yet Installed | CPP AGI | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | Install Equipotential Bonding Jumper Gland to Gland as per approved design drawing. | 2026-08-17T17:17:41.927 | Gawad, Mohamed | PS5 - Milestone B
PL-015316 | PS5-60-IE-0003B-CC15 |  | B | I | Grounding between Gland to Gland not yet Installed | CPP AGI | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | Install Equipotential Bonding Jumper Gland to Gland as per approved design drawing. | 2026-08-17T17:19:50.690 | Gawad, Mohamed | PS5 - Milestone B
PL-015317 | PS5-60-IE-0003B-CC16 |  | B | I | Grounding between Gland to Gland not yet Installed | CPP AGI | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | Install Equipotential Bonding Jumper Gland to Gland as per approved design drawing. | 2026-08-17T17:22:04.317 | Gawad, Mohamed | PS5 - Milestone B
PL-015335 | PS5-60-DM-3400-CL01 |  | B | E | Tags are not available ( Ferrule ) | KENT | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | CTR to rectify | 2026-08-18T04:48:58.473 | Galang, Angelo | PS5 - Milestone E
PL-015336 | PS5-60-IES-3400-CD01 |  | B | E | Tags are not available ( Ferrule ) | KENT | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | CTR to rectify | 2026-08-18T05:00:56.353 | Galang, Angelo | PS5 - Milestone E
PL-015341 | PS5-03-BI-1512-CC01 |  | B | I | Tags are not available ( Ferrule ) | KENT | PS5-03-09 - FZ-09 - Power Generation Building - Engine Bay 1 |  | Originated |  | CTR to rectify | 2026-08-18T05:09:41.307 | Galang, Angelo | PS5 - Milestone E
PL-015345 | PS5-60-IE-0003B-CC23 |  | B | I | Tags are not available ( Ferrule ) | KENT | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | CTR to rectify | 2026-08-18T05:11:57.710 | Galang, Angelo | PS5 - Milestone B
PL-015346 | PS5-60-IE-0003B-CC24 |  | B | I | Tags are not available ( Ferrule ) | KENT | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | CTR to rectify | 2026-08-18T05:13:51.000 | Galang, Angelo | PS5 - Milestone B
PL-015347 | PS5-71-IN-0003-CC05 |  | B | I | Tags are not available ( Ferrule ) | KENT | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP) |  | Originated |  | CTR to rectify | 2026-08-18T05:15:56.500 | Galang, Angelo | PS5 - Milestone B
PL-015354 | PS5-01-BI-1515-CC01 |  | B | I | Tags are not available ( Ferrule ) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-18T05:42:37.710 | Galang, Angelo | PS5 - Milestone A
PL-015355 | PS5-01-BI-1520-CC01 |  | B | I | Tags are not available ( Ferrule ) | KENT | PS5-01-10 - Water Mist Package |  | Originated |  | CTR to rectify | 2026-08-18T05:44:20.817 | Galang, Angelo | PS5 - Milestone E
PL-015357 | PS5-60-IE-0003B-CC23 |  | B | I | No proper earth clamp for armour | KENT | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | CTR to rectify | 2026-08-18T07:32:22.737 | Galang, Angelo | PS5 - Milestone B
PL-015358 | PS5-60-IE-0003B-CC24 |  | B | I | No proper earth clamp in the armour | KENT | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | CTR to rectify | 2026-08-18T07:35:40.590 | Galang, Angelo | PS5 - Milestone B
PL-015380 | PS5-02-SAS-0003 |  | B | M | 4:The clamp is not properly installed | EPS VENDOR | PS5-02-01 - Miscellaneous Safety equipment |  | Originated |  |  | 2026-08-18T14:21:38.500 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-015381 | PS5-02-SAS-0004 |  | B | M | 4:The clamp is not properly installed | EPS VENDOR | PS5-02-01 - Miscellaneous Safety equipment |  | Originated |  |  | 2026-08-18T14:24:27.013 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-015382 | PS5-02-SAS-0006 |  | B | M | 4:During inspection, the clamp support was found broken. | EPS VENDOR | PS5-02-01 - Miscellaneous Safety equipment |  | Originated |  |  | 2026-08-18T14:26:08.843 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-015383 | PS5-02-SCA-0001 |  | C | M | 4:During inspection, it was found that the packing list specifies 1 No. of 7 kg portable carbon dioxide fire extinguisher with cabinet, but 6 Nos. were received. ( 5 nos overage). | EPS VENDOR | PS5-02-02 - Portable Fire Fighting Equipments |  | Originated |  |  | 2026-08-18T14:28:23.560 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-015384 | PS5-02-SCA-0001 |  | C | M | 4.1:During inspection, 4 Nos. of 9 L foam fire extinguishers were found inside the box; they are not listed in the packing list. | EPS VENDOR | PS5-02-02 - Portable Fire Fighting Equipments |  | Originated |  |  | 2026-08-18T14:29:08.607 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-015386 | PS5-28-HE-2200 |  | C | M | 4:AS PER THE PACKING LIST 4 nos BUT RECEIVED 7 Nos (OVERAGE 3 nos) | CPP AGI | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  |  | 2026-08-18T14:33:16.577 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-015387 | PS5-28-HE-2200 |  | C | M | 4.1:FOUND 1 no KNOB WHICH IS NOT SHOWING IN PACKING LIST (1 no OVERAGE) | EPS VENDOR | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  |  | 2026-08-18T14:34:18.677 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-015402 | PS5-01-BI-2520-CC01 |  | B | I | Ferulle tags missing | KENT | PS5-01-10 - Water Mist Package |  | Originated |  | CTR need to rectify | 2026-08-19T05:22:52.813 | Galang, Angelo | PS5 - Milestone E
PL-015403 | PS5-01-BI-2520-CC01 |  | B | I | Clamp for screen shield not installed | KENT | PS5-01-10 - Water Mist Package |  | Originated |  | CTR need to rectify | 2026-08-19T05:26:21.713 | Galang, Angelo | PS5 - Milestone E
PL-015492 |  | EACOP-PS5-25-01-0049 | B | P | 18:PS5--25-PIT-1102 - TZ-MID-68-WPR2-206085, Pressure Instrument Flange management to be done | CPP AGI | PS5-25-01 - Export Pipeline Pig Receiver |  | Originated |  | PS5--25-PIT-1102 - Pressure Instrument Flange management to be done | 2026-08-19T12:51:27.200 | Bhagavath, sangeeth | PS5 - Milestone H
PL-015504 |  | EACOP-PS5-25-07-0067 | B | P | 18:PS5--25-ZS-1201 - TZ-MID-68-WPR2-206088, Pressure Instrument Flange management to be done | CPP AGI | PS5-25-07 - Export Pipeline Pig Launcher |  | Originated |  | Pressure Instrument Flange management to be done | 2026-08-19T13:04:03.290 | Bhagavath, sangeeth | PS5 - Milestone H
PL-015508 |  | EACOP-PS5-25-07-0071 | B | P | 18:TZ-MID-68-WPR2-206157 - Valve handle orientation not as per ISO Drawing RLMU to be done | CPP AGI | PS5-25-07 - Export Pipeline Pig Launcher |  | Originated |  | Valve handle orientation not as per ISO Drawing RLMU to be Done | 2026-08-19T13:19:11.070 | Bhagavath, sangeeth | PS5 - Milestone H
PL-015509 |  | EACOP-PS5-60-39-0203 | B | P | 18:PS5-60-UR-8100E_TP-869 & TP_870 - Hose connection joint FM to be done | CPP AGI | PS5-60-39 - Injector Tip Cooling Module E |  | Originated |  | Hose connection joint FM to be done | 2026-08-19T13:45:07.870 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015510 |  | EACOP-PS5-60-39-0203 | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-39 - Injector Tip Cooling Module E |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-19T13:46:15.293 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015511 |  | EACOP-PS5-60-39-0203 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-39 - Injector Tip Cooling Module E |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-19T13:47:53.557 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:41:09.000
PL-015514 |  | EACOP-PS5-60-66-0247 | B | P | 18:PS5-60-UR-8100F_TP-888 & TP_890 - Equpiment connection Flange Management to be done | CPP AGI | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Originated |  | Equpiment connection Flange Management to be done | 2026-08-19T14:02:12.090 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015515 |  | EACOP-PS5-60-66-0247 | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-19T14:03:50.243 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015516 |  | EACOP-PS5-60-66-0247 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-19T14:04:44.250 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:41:29.000
PL-015517 |  | EACOP-PS5-71-05-0305 | B | P | 18:PS5-71-TR-4100_N5 - F1 Flange Management to be done after GALT test | CPP AGI | PS5-71-05 - CFO Transfer Pump A/B |  | Originated |  | F1 Flange Management to be done after GALT test | 2026-08-19T14:16:25.307 | Bhagavath, sangeeth | PS5 - Milestone H
PL-015518 |  | EACOP-PS5-71-05-0305 | B | P | 18.1: PS5-71-SPXA-0002 - Bund wall Pipe penetration seal to be fixed | CPP AGI | PS5-71-05 - CFO Transfer Pump A/B |  | Originated |  | PS5-71-SPXA-0002 - Bund wall Pipe penetration seal to be fixed | 2026-08-19T14:17:51.943 | Bhagavath, sangeeth | PS5 - Milestone H
PL-015519 |  | EACOP-PS5-71-05-0305 | B | P | 18.2:PS5-71-PA-3300A & 3300B - Pump connection Flange Management to be done | CPP AGI | PS5-71-05 - CFO Transfer Pump A/B |  | Originated |  | PS5-71-PA-3300A & 3300B - Pump connection Flange Management to be done | 2026-08-19T14:19:17.243 | Bhagavath, sangeeth | PS5 - Milestone H
PL-015521 |  | EACOP-PS5-28-03-0079 | A | P | 18:PS5-28-TIT-1104 & PS5-28-TIT-1105 - Temperature instrument to be install & Flange Management to be done | CPP AGI | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  | PS5-28-TIT-1104 & PS5-28-TIT-1105 - Temperature instrument to be install & Flange Management to be done | 2026-08-19T14:28:31.003 | Bhagavath, sangeeth | PS5 - Milestone G
PL-015522 |  | EACOP-PS5-28-03-0084 | B | P | 18:TZ-MID-68-WPR2-206309 - Lever/Handl wheel OR I= South, RLMU to be done | CPP AGI | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  | TZ-MID-68-WPR2-206309 - Lever/Handl wheel OR I= South, RLMU to be done | 2026-08-19T14:43:33.987 | Bhagavath, sangeeth | PS5 - Milestone G
PL-015523 |  | EACOP-PS5-28-03-0084 | B | P | 18.1:TZ-MID-68-WPR2-206202 - Lever/Handl wheel OR I= UP, RLMU to be done | CPP AGI | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  | TZ-MID-68-WPR2-206202 - Lever/Handl wheel OR I= UP, RLMU to be done | 2026-08-19T14:44:34.877 | Bhagavath, sangeeth | PS5 - Milestone G
PL-015551 | PS5-01-BI-1117-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR To rectify | 2026-08-20T06:50:58.493 | Galang, Angelo | PS5 - Milestone A
PL-015553 | PS5-01-BI-1117-CC01 |  | B | I | Screen armour clamp not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-20T06:53:00.987 | Galang, Angelo | PS5 - Milestone A
PL-015555 | PS5-71-DM-3500A-CL01 |  | B | E | Ferrule tags not available | KENT | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | CTR to rectify | 2026-08-20T07:03:38.580 | Galang, Angelo | PS5 - Milestone B
PL-015570 |  | EACOP-PS5-25-07-0066 | B | P | 18:Paint touchup to be done in damaged area | CPP AGI | PS5-25-07 - Export Pipeline Pig Launcher |  | Completed |  | Paint touchup to be done in damaged area | 2026-08-20T11:34:21.380 | Bhagavath, sangeeth | PS5 - Milestone H | 2026-08-21T13:52:30.000
PL-015571 |  | EACOP-PS5-60-74-0278 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-20T11:46:15.900 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015572 |  | EACOP-PS5-60-74-0278 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-20T11:47:05.250 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:41:59.000
PL-015573 |  | EACOP-PS5-60-75-0280 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-20T11:50:07.170 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015574 |  | EACOP-PS5-60-75-0280 | B | P | 18.1:PS5-60-UR-8100F_TP-884 & 886 - Equpiment joint Flange Management up to be done | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | Equpiment joint Flange Management up to be done | 2026-08-20T11:50:58.223 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015575 |  | EACOP-PS5-60-75-0280 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-20T11:52:04.780 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:42:27.000
PL-015577 | PS5-71-IES-3500A-CD01 |  | B | E | FERULLE TAGS MISSING | KENT | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | CRT to rectify | 2026-08-20T12:05:24.850 | Galang, Angelo | PS5 - Milestone B
PL-015580 | PS5-71-IES-3500B-CD01 |  | B | E | FERULLE TAGS NOT AVAILABLE | KENT | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | CTR need to rectify | 2026-08-20T12:13:36.987 | Galang, Angelo | PS5 - Milestone B
PL-015581 | PS5-71-DM-3500B-CL01 |  | B | E | FERRULE TAGS NOT AVAILABLE | KENT | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | CTR to rectify | 2026-08-20T12:20:43.163 | Galang, Angelo | PS5 - Milestone B
PL-015584 |  | EACOP-PS5-60-75-0282 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-20T12:41:47.437 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015585 |  | EACOP-PS5-60-75-0282 | B | P | 18.1:PS5-60-UR-8100F_TP-887 - Equpiment joint Flange Management up to be done | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | Equpiment joint Flange Management up to be done | 2026-08-20T12:42:32.527 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015586 |  | EACOP-PS5-60-75-0282 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-20T12:43:17.120 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:42:59.000
PL-015587 |  | EACOP-PS5-60-75-0283 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-20T12:57:54.587 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015588 |  | EACOP-PS5-60-75-0283 | B | P | 18.1:PS5-60-UR-8100F_TP-885 - Equpiment joint Flange Management up to be done | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | Equpiment joint Flange Management up to be done | 2026-08-20T12:58:38.583 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015589 |  | EACOP-PS5-60-75-0283 | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-20T12:59:53.837 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:43:18.000
PL-015592 |  | EACOP-PS5-60-75-0284 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-20T13:08:44.910 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015594 |  | EACOP-PS5-60-75-0284 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-20T13:10:25.000 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015595 |  | EACOP-PS5-60-75-0285 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-20T13:24:28.507 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015596 |  | EACOP-PS5-60-75-0285 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-20T13:25:33.893 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:43:39.000
PL-015597 |  | EACOP-PS5-71-17-0324 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-71-17 - Diesel Fuel Distribution Header |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-20T13:30:48.303 | Bhagavath, sangeeth | PS5 - Milestone F
PL-015598 |  | EACOP-PS5-71-17-0324 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-71-17 - Diesel Fuel Distribution Header |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-20T13:33:09.417 | Bhagavath, sangeeth | PS5 - Milestone F
PL-015603 | PS5-01-BI-2110-CC01 |  | B | I | FERRULE TAGS NOT AVAILABLE | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR need to rectify | 2026-08-20T14:12:29.993 | Galang, Angelo | PS5 - Milestone A
PL-015604 | PS5-01-BI-2110-CC01 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | Ctr need to rectify | 2026-08-20T14:13:48.980 | Galang, Angelo | PS5 - Milestone A
PL-015656 | PS5-03-BI-2514-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-21T10:04:14.317 | Galang, Angelo | PS5 - Milestone A
PL-015657 | PS5-03-BI-2514-CC01 |  | B | I | Clamp support not available for screen shield | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-21T10:06:50.483 | Galang, Angelo | PS5 - Milestone A
PL-015658 | PS5-71-IN-0001-CC10 |  | B | I | Ferrule tags not available | KENT | PS5-71-19 - Diesel Separator Module (UCP) |  | Originated |  | CTR to rectify | 2026-08-21T10:13:59.747 | Galang, Angelo | PS5 - Milestone F
PL-015659 | PS5-71-IN-0001-CC10 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-71-19 - Diesel Separator Module (UCP) |  | Originated |  | CTR to rectify | 2026-08-21T10:16:08.210 | Galang, Angelo | PS5 - Milestone F
PL-015660 | PS5-71-IN-0001-CC08 |  | B | I | Ferrule tags not available | KENT | PS5-71-19 - Diesel Separator Module (UCP) |  | Originated |  | CTR to rectify | 2026-08-21T10:25:04.283 | Galang, Angelo | PS5 - Milestone F
PL-015661 | PS5-71-IN-0001-CC08 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-71-19 - Diesel Separator Module (UCP) |  | Originated |  | CTR to rectify | 2026-08-21T10:26:13.427 | Galang, Angelo | PS5 - Milestone F
PL-015662 | PS5-60-49_SS_ALL_LINES |  | B | P | 6:WIRE MESH TO BE INSTALLED | CPP AGI | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A |  | Originated |  | WIRE MESH TO BE INSTALLED | 2026-08-21T10:31:14.563 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-015663 | PS5-60-50_SS_ALL_LINES |  | B | P | 6:WIRE MESH TO BE INSTALLED | CPP AGI | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B |  | Originated |  | WIRE MESH TO BE INSTALLED | 2026-08-21T10:52:09.590 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-015664 | PS5-60-70_SS_ALL_LINES |  | B | P | 6:WIRE MESH TO BE INSTALLED | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | WIRE MESH TO BE INSTALLED | 2026-08-21T10:55:36.100 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-015665 | PS5-60-71_SS_ALL_LINES |  | B | P | 6:WIRE MESH TO BE INSTALLED | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | WIRE MESH TO BE INSTALLED | 2026-08-21T10:57:01.240 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-015696 | PS5-60-IE-0003A-CC23 |  | B | I | Ferrule tags not available | KENT | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | CTR to rectify | 2026-08-21T12:31:48.633 | Galang, Angelo | PS5 - Milestone B
PL-015697 | PS5-60-IE-0003A-CC23 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | CTR need to rectify | 2026-08-21T12:32:46.510 | Galang, Angelo | PS5 - Milestone B
PL-015698 | PS5-60-IE-0003A-CC24 |  | B | I | Ferrule tags not available | KENT | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | CTR need to rectify | 2026-08-21T12:38:55.890 | Galang, Angelo | PS5 - Milestone B
PL-015699 | PS5-60-IE-0003A-CC24 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | CTR need to rectify | 2026-08-21T12:40:15.343 | Galang, Angelo | PS5 - Milestone B
PL-015701 | PS5-01-UZ-610 |  | A | M | 10.1:Nitrogen (N₂) cylinders received with low filling pressure. As per the packing list, the required pressure is 200 bar, but two cylinders were received at only 1300 psi (89.6 bar).Replace or refill the cylinders to the specified 200 bar pressure. | EPS VENDOR | PS5-01-11 - Inergen for Power Gen Building |  | Originated |  | Nitrogen (N₂) cylinders received with low filling pressure. As per the packing list, the required pressure is 200 bar, but two cylinders were received at only 1300 psi (89.6 bar).Replace or refill the cylinders to the specified 200 bar pressure. | 2026-08-21T13:18:50.387 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-015705 | PS5-60-IE-0003B-CC23 |  | B | I | Ferrule tags are not available | KENT | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | CTR to rectify | 2026-08-21T13:53:53.033 | Galang, Angelo | PS5 - Milestone B
PL-015706 | PS5-60-IE-0003B-CC23 |  | B | I | Clamp and support for screen shiled not available | KENT | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | CTR to rectify | 2026-08-21T13:54:46.887 | Galang, Angelo | PS5 - Milestone B
PL-015714 |  | EACOP-PS5-60-24-0176 | B | P | 18:PS5-60-PA-3300/SN - Flange Management to be done after pump alignment | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Completed |  | PS5-60-PA-3300/SN - Flange Management to be done after pump alignment | 2026-08-21T14:50:55.127 | Bhagavath, sangeeth | PS5 - Milestone E | 2026-08-30T14:46:20.000
PL-015715 |  | EACOP-PS5-60-24-0176 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-21T14:51:43.160 | Bhagavath, sangeeth | PS5 - Milestone E | 2026-08-30T14:44:24.000
PL-015727 | PS5-60-DM-3300-CL01 |  | B | E | Ferrule tags not available | KENT | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  | CTR to rectify | 2026-08-22T08:09:21.257 | Galang, Angelo | PS5 - Milestone E
PL-015728 | PS5-60-IES-3300-CD01 |  | B | E | Ferrule tags not available | KENT | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  | CTR to rectify | 2026-08-22T08:14:34.880 | Galang, Angelo | PS5 - Milestone E
PL-015729 |  | EACOP-PS5-60-24-0177 | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-22T08:45:02.770 | Bhagavath, sangeeth | PS5 - Milestone E
PL-015730 |  | EACOP-PS5-60-24-0177 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-22T08:45:50.990 | Bhagavath, sangeeth | PS5 - Milestone E | 2026-08-30T14:44:48.000
PL-015731 |  | EACOP-PS5-60-74-0279 | B | P | 18:TZ-MID-68-WPR2-206949 - PS5-SPS-A550-401, Support to be installed | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | PS5-SPS-A550-401, Support to be installed | 2026-08-22T08:55:56.110 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015732 |  | EACOP-PS5-60-74-0279 | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-22T08:56:46.023 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:46:53.000
PL-015733 |  | EACOP-PS5-01-02-0348 | B | P | 18:Valve Lever/Handle Wheel ORI=W, RLMU to be done | CPP AGI | PS5-01-02 - Fire Water Pump A |  | Originated |  | Valve Lever/Handle Wheel ORI=W, RLMU to be done | 2026-08-22T09:01:37.663 | Bhagavath, sangeeth | PS5 - Milestone C
PL-015734 |  | EACOP-PS5-01-03-0350 | B | P | 18:Valve Lever/Handle Wheel ORI=W, RLMU to be done | CPP AGI | PS5-01-03 - Fire Water Pump B |  | Originated |  | Valve Lever/Handle Wheel ORI=W, RLMU to be done | 2026-08-22T09:05:40.870 | Bhagavath, sangeeth | PS5 - Milestone C
PL-015736 | PS5-03-SEA-0003-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room |  | Originated |  | CTR to recticfy | 2026-08-22T11:38:51.440 | Galang, Angelo | PS5 - Milestone E
PL-015738 | PS5-03-SEA-0003-CC01 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room |  | Originated |  | CTR to rectify | 2026-08-22T11:40:57.633 | Galang, Angelo | PS5 - Milestone E
PL-015741 | PS5-60-SEA-0001-CC18 |  | B | I | Ferrule tgas not available | KENT | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room |  | Originated |  | CTR need to rectify | 2026-08-22T12:14:38.730 | Galang, Angelo | PS5 - Milestone E
PL-015742 | PS5-60-SEA-0001-CC18 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room |  | Originated |  | CTR to rectify | 2026-08-22T12:15:38.857 | Galang, Angelo | PS5 - Milestone E
PL-015743 | PS5-03-SFMC-0006-CC01 |  | C | I | Missing core marker | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Need to install the core marker | 2026-08-22T12:16:33.000 | Shirima, Frank | PS5 - Milestone A
PL-015744 | PS5-04-PMC-0002-CS03 |  | C | E | Missing cable tag | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Install cable tag | 2026-08-22T12:21:46.000 | Shirima, Frank | PS5 - Milestone A
PL-015745 | PS5-04-PMC-0008-CC26 |  | C | I | Missing core marker PS5-04-PMC-0008-CC26/TBA12/5/PR01/WH at PMC-0008 side | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Install core marker | 2026-08-22T12:23:41.000 | Shirima, Frank | PS5 - Milestone A
PL-015746 | PS5-04-PMC-0008-CC26 (Reconnection) |  | C | I | Missing core marker PS5-04-PMC-0008-CC26/TBA12/5/PR01/WH at PMC-0008 side | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Install core marker | 2026-08-22T12:25:44.000 | Shirima, Frank | PS5 - Milestone A
PL-015747 | PS5-61-IK-0001-CC29 (Reconnection) |  | C | I | Missing core marker PS5-61-IK-0001-CC29/TBD09/5/PR03/WH at PMC-0007 side | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Install core marker | 2026-08-22T12:27:04.000 | Shirima, Frank | PS5 - Milestone A
PL-015748 | PS5-61-IK-0001-CC64 (Reconnection) |  | B | I | To changed terminal block name following interconnection drawing | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Change terminal block name following interconnection drawing | 2026-08-22T12:29:00.000 | Shirima, Frank | PS5 - Milestone A
PL-015749 | PS5-61-IK-0001-CC65 (Reconnection) |  | B | I | To changed terminal block name following interconnection drawing | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Change terminal block name following interconnection drawing | 2026-08-22T12:30:40.000 | Shirima, Frank | PS5 - Milestone A
PL-015756 | PS5-03-SEA-0003-CJ01 |  | B | I | Ferrule tags not available | KENT | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room |  | Originated |  | CTR to rectify | 2026-08-22T14:04:02.023 | Galang, Angelo | PS5 - Milestone E
PL-015757 | PS5-03-SEA-0003-CJ01 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room |  | Originated |  | CTR to rectify | 2026-08-22T14:05:28.890 | Galang, Angelo | PS5 - Milestone E
PL-015783 | PS5-60-IE-0003A-CC22 |  | B | I | Ferrule tags not available | KENT | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | CTR to rectify | 2026-08-24T05:05:56.657 | Galang, Angelo | PS5 - Milestone B
PL-015784 | PS5-60-IE-0003A-CC22 |  | B | I | Clamp and support for screen shield are not available | KENT | PS5-60-02 - Power Gen Package A (UCP) |  | Originated |  | CTR to rectify | 2026-08-24T05:08:23.710 | Galang, Angelo | PS5 - Milestone B
PL-015786 | PS5-71-IN-0001-CC09 |  | B | I | Ferrule tags are not available | KENT | PS5-71-19 - Diesel Separator Module (UCP) |  | Originated |  | Ctr to modify | 2026-08-24T06:08:53.820 | Galang, Angelo | PS5 - Milestone F
PL-015787 | PS5-71-IN-0001-CC09 |  | B | I | Clamp and support for screen shield are not available | KENT | PS5-71-19 - Diesel Separator Module (UCP) |  | Originated |  | CTR need to rectify | 2026-08-24T06:10:07.070 | Galang, Angelo | PS5 - Milestone F
PL-015839 | PS5-06-GU-0003A-CD01 |  | B | E | Ferrule tags not available | KENT | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | CTR to rectify | 2026-08-24T11:38:02.067 | Galang, Angelo | PS5 - Milestone B
PL-015840 | PS5-06-IG-0004A-CD01 |  | B | E | Ferrule tags not available | KENT | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | CTR to rectify | 2026-08-24T13:04:14.393 | Galang, Angelo | PS5 - Milestone B
PL-015841 |  | EACOP-PS5-60-25-0182 | B | P | 18.1:TZ-MID-68-WPR2-2073653 - ITEM 03, LEVER/HANDWHEEL ORI = W,RLMU to be done | CPP AGI | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | LEVER/HANDWHEEL ORI = W,RLMU to be done | 2026-08-24T13:12:38.047 | Bhagavath, sangeeth | PS5 - Milestone E
PL-015842 |  | EACOP-PS5-60-25-0182 | B | P | 18.2:Pickling & Passivation to be done in affected area | CPP AGI | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | Pickling & Passivation to be done in affected area | 2026-08-24T13:13:44.390 | Bhagavath, sangeeth | PS5 - Milestone E
PL-015843 | PS5-06-GU-0003B-CD01 |  | B | E | Ferrule tag not available | KENT | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | CTR to rectify | 2026-08-24T13:14:04.470 | Galang, Angelo | PS5 - Milestone B
PL-015844 | PS5-06-IG-0004B-CD01 |  | B | E | Ferrule tags not available | KENT | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | CTR to rectify | 2026-08-24T13:18:58.943 | Galang, Angelo | PS5 - Milestone B
PL-015845 |  | EACOP-PS5-60-40-0204 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-40 - Injector Tip Cooling Module F |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-24T13:24:37.640 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:47:12.000
PL-015846 |  | EACOP-PS5-60-46-0216 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-46 - Oil Mist Separator Skid PS5-60-VS-9100E |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-24T13:30:37.823 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:47:27.000
PL-015847 |  | EACOP-PS5-60-47-0218 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-47 - Oil Mist Separator Skid PS5-60-VS-9100F |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-24T13:37:02.807 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:47:46.000
PL-015848 | PS5-06-GU-0003B-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | CTR to rectify | 2026-08-24T13:43:49.113 | Galang, Angelo | PS5 - Milestone B
PL-015849 |  | EACOP-PS5-60-54-0232 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-54 - Lube Oil Separator Module PS5-60-UO-81100F |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-24T13:47:18.620 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:48:21.000
PL-015850 |  | EACOP-PS5-60-25-0389 | B | P | 18:PS5-60-PPA-3400/DN - F1 & F2 Flange management to be done after pump alignment | CPP AGI | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | F1 & F2 Flange management to be done after pump alignment | 2026-08-24T13:55:42.000 | Bhagavath, sangeeth | PS5 - Milestone E
PL-015851 |  | EACOP-PS5-60-25-0389 | B | P | 18.1:Pickling & Passivation to be done in affected area | CPP AGI | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | Pickling & Passivation to be done in affected area | 2026-08-24T13:57:33.790 | Bhagavath, sangeeth | PS5 - Milestone E
PL-015852 | PS5-06-GU-0003A-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | CTR to rectify | 2026-08-24T14:00:35.270 | Galang, Angelo | PS5 - Milestone B
PL-015864 | PS5-71-IN-0002-CC07 |  | B | I | Ferrule tags not available | KENT | PS5-71-09 - CFO Pre-Pressure Modules (UCP) |  | Originated |  | CTR to rectify | 2026-08-25T05:00:04.727 | Galang, Angelo | PS5 - Milestone H
PL-015865 | PS5-09-ACU-0007_OUTDOOR_INSTALLATION |  | B | M | 10:STRUCTURAL UNCOATED BOLTS TO BE REPLACED | CPP AGI | PS5-09-05 - HVAC for EITS Building |  | Completed |  | STRUCTURAL UNCOATED BOLTS TO BE REPLACED | 2026-08-25T06:46:30.033 | THANGARATHINAM, ajikumar | PS5 - Milestone A | 2026-08-25T06:49:12.000
PL-015866 | PS5-09-ACU-0007_OUTDOOR_INSTALLATION |  | B | H | 17:STRUCTURAL UNCOATED BOLTS TO BE REPLACED | CPP AGI | PS5-09-05 - HVAC for EITS Building |  | Originated |  | STRUCTURAL UNCOATED BOLTS TO BE REPLACED | 2026-08-25T06:52:27.540 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-015887 | PS5-60-26_SS_ALL_LINES |  | C | P | 6:COLOUR CODE AND MARKING TO BE DONE | CPP AGI | PS5-60-26 - Instrument Air Compressor Skid |  | Originated |  | COLOUR CODE AND MARKING TO BE DONE | 2026-08-25T08:52:22.363 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-015923 |  | EACOP-PS5-25-02-0053 | B | P | 18:Pickling & Passivation to be done in affected area | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Pickling & Passivation to be done in affected area | 2026-08-25T12:46:37.210 | Bhagavath, sangeeth | PS5 - Milestone H
PL-015924 | PS5-01-BI-0002-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-01-10 - Water Mist Package |  | Originated |  | CTR to rectify | 2026-08-25T12:57:06.470 | Galang, Angelo | PS5 - Milestone E
PL-015925 | PS5-01-BI-0002-CC01 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-01-10 - Water Mist Package |  | Originated |  | CTR to rectify | 2026-08-25T12:59:23.653 | Galang, Angelo | PS5 - Milestone E
PL-015926 |  | EACOP-PS5-60-74-0274 | B | P | 18:PS5-60-UR-8100E_TP-863 & 865 - Hose connection joint FM to be done | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | Hose connection joint FM to be done | 2026-08-25T13:06:14.540 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015927 |  | EACOP-PS5-60-74-0274 | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-25T13:07:28.803 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015928 | PS5-01-BI-0003-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-01-10 - Water Mist Package |  | Originated |  | CTR to rectify | 2026-08-25T13:07:44.323 | Galang, Angelo | PS5 - Milestone E
PL-015929 | PS5-01-BI-0003-CC01 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-01-10 - Water Mist Package |  | Originated |  | CTR to rectify | 2026-08-25T13:12:07.340 | Galang, Angelo | PS5 - Milestone E
PL-015930 | PS5-01-BI-0004-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-01-10 - Water Mist Package |  | Originated |  | CTR to rectify | 2026-08-25T13:17:25.567 | Galang, Angelo | PS5 - Milestone E
PL-015931 |  | EACOP-PS5-60-74-0276 | B | P | 18:PS5-60-UR-8100E_TP-866 - Hose connection joint FM to be done | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | Hose connection joint FM to be done | 2026-08-25T13:17:39.117 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015932 |  | EACOP-PS5-60-74-0276 | B | P | 18.1:CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-25T13:18:33.500 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015933 | PS5-01-BI-0004-CC01 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-01-10 - Water Mist Package |  | Originated |  | CTR to rectify | 2026-08-25T13:21:04.547 | Galang, Angelo | PS5 - Milestone E
PL-015935 |  | EACOP-PS5-60-74-0277 | B | P | 18:PS5-60-UR-8100E_TP-864 - Hose connection joint FM to be done | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | Hose connection joint FM to be done | 2026-08-25T13:27:53.687 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015936 |  | EACOP-PS5-60-74-0277 | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | CTR commodity code to be add. RLMU to be done | 2026-08-25T13:28:45.687 | Bhagavath, sangeeth | PS5 - Milestone D
PL-015937 | PS5-01-LIT-4201-CJ01 |  | B | I | ferulle tags not available | KENT | PS5-01-10 - Water Mist Package |  | Originated |  | CTR to rectify | 2026-08-25T13:36:39.703 | Galang, Angelo | PS5 - Milestone E
PL-015938 | PS5-01-LIT-4201-CJ01 |  | B | I | Clamp and support arenot available | KENT | PS5-01-10 - Water Mist Package |  | Originated |  |  | 2026-08-25T13:37:34.730 | Galang, Angelo | PS5 - Milestone E
PL-015939 |  | EACOP-PS5-71-13-0316 | B | P | 18:PS5-71-TR-4200_N3 - Tank joint F1 Flange Management to be done | CPP AGI | PS5-71-13 - CFO Service Pump A/B |  | Originated |  | Tank joint Flange Management to be done | 2026-08-25T13:39:19.857 | Bhagavath, sangeeth | PS5 - Milestone H
PL-015940 |  | EACOP-PS5-71-13-0316 | B | P | 18.1:PS5-71-PA-3400A_SN & PS5-71-PA-3400B_SN - Pump connection Flange Management to be done | CPP AGI | PS5-71-13 - CFO Service Pump A/B |  | Originated |  | Pump connection Flange Management to be done | 2026-08-25T13:40:30.187 | Bhagavath, sangeeth | PS5 - Milestone H
PL-015941 | PS5-60-IE-0003B-CC22 |  | B | I | Ferrule tags not available | KENT | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | CTR to rectify | 2026-08-25T13:53:44.610 | Galang, Angelo | PS5 - Milestone B
PL-015942 | PS5-60-IE-0003B-CC22 |  | B | I | Clamp and support are not available | KENT | PS5-60-05 - Power Gen Package B (UCP) |  | Originated |  | CTR to rectify | 2026-08-25T13:54:32.997 | Galang, Angelo | PS5 - Milestone B
PL-015943 |  | EACOP-PS5-28-04-0086 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-25T13:58:33.313 | Bhagavath, sangeeth | PS5 - Milestone E
PL-015946 |  | EACOP-PS5-60-39-0202 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-39 - Injector Tip Cooling Module E |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-25T14:12:43.917 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:48:45.000
PL-015947 |  | EACOP-PS5-60-53-0230 | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | CPP AGI | PS5-60-53 - Lube Oil Separator Module PS5-60-UO-81100E |  | Completed |  | GL01 PTFE Isolation Pad to be Fixed | 2026-08-25T14:19:20.643 | Bhagavath, sangeeth | PS5 - Milestone D | 2026-08-30T14:49:22.000
PL-015948 | PS5-61-IV-0002A |  | A | E | Cables to be connected after the gland plate change | CPP AGI | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Reconnect and properly terminate all cables after completion of the gland plate replacement, as per the approved wiring drawings. | 2026-08-25T15:31:44.360 | Gawad, Mohamed | PS5 - Milestone D
PL-015949 | PS5-61-IV-0002B |  | A | E | Cables to be connected after the gland plate change | CPP AGI | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Reconnect and properly terminate all cables after completion of the gland plate replacement, as per the approved wiring drawings. | 2026-08-25T15:40:41.267 | Gawad, Mohamed | PS5 - Milestone D
PL-015952 | PS5-71-BI-2306-CC01 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-26T06:19:04.040 | Galang, Angelo | PS5 - Milestone A
PL-015955 | PS5-71-BI-2314-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-26T06:47:18.530 | Galang, Angelo | PS5 - Milestone A
PL-015956 | PS5-71-BI-2314-CC01 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-26T06:48:11.350 | Galang, Angelo | PS5 - Milestone A
PL-015960 | PS5-71-BI-1306-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-26T07:09:20.610 | Galang, Angelo | PS5 - Milestone A
PL-015961 | PS5-71-BI-1306-CC01 |  | B | I | Clamp and support not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-26T07:10:09.650 | Galang, Angelo | PS5 - Milestone A
PL-015964 | PS5-71-BI-1116-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-26T10:56:56.187 | Galang, Angelo | PS5 - Milestone A
PL-015965 | PS5-03-SEA-0003-CC01 |  | C | I | WIRE MARKER MISSING | KENT | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room |  | Originated |  | WIRE MARKER TO INSTALLS | 2026-08-26T10:57:26.000 | Iriyanto, Edy | PS5 - Milestone E
PL-015966 | PS5-71-BI-1116-CC01 |  | B | I | Clamp and support not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-26T10:57:37.500 | Galang, Angelo | PS5 - Milestone A
PL-015999 | PS5-71-BI-2107-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-26T12:14:43.693 | Galang, Angelo | PS5 - Milestone A
PL-016000 | PS5-71-BI-2107-CC01 |  | B | I | Clamp and support not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-26T12:15:51.417 | Galang, Angelo | PS5 - Milestone A
PL-016005 | PS5-71-BI-1109-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-26T12:47:39.220 | Galang, Angelo | PS5 - Milestone A
PL-016007 | PS5-71-BI-1109-CC01 |  | B | I | Clamp and support not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-26T12:49:06.777 | Galang, Angelo | PS5 - Milestone A
PL-016029 | PS5-60-UZ-8200A |  | B | M | PRESSURE GAUGE TO BE FIXED | CPP AGI | PS5-60-35 - Injector Tip Cooling Module A |  | Originated |  | PRESSURE GAUGE TO BE FIXED | 2026-08-26T13:26:28.000 | arun, jabesteen | PS5 - Milestone B
PL-016031 | PS5-25-BI-2105-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-26T14:29:20.933 | Galang, Angelo | PS5 - Milestone A
PL-016032 | PS5-25-BI-2105-CC01 |  | B | I | Clamp and support not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-26T14:30:46.740 | Galang, Angelo | PS5 - Milestone A
PL-016033 | PS5-25-BI-1115-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-26T14:37:57.620 | Galang, Angelo | PS5 - Milestone A
PL-016034 | PS5-25-BI-1115-CC01 |  | B | I | Clamp and support not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-26T14:38:49.713 | Galang, Angelo | PS5 - Milestone A
PL-016045 | PS5-60-TR-4300 |  | C | M | 3:FINAL TOUCH UP PAINT TO BE CARRIED OUT | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  | 3:FINAL TOUCH UP PAINT TO BE CARRIED OUT | 2026-08-27T04:38:03.293 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-016046 | PS5-60-TR-4400 |  | C | M | 3:FINAL TOUCH UP PAINT TO BE CARRIED OUT | CPP AGI | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | 3:FINAL TOUCH UP PAINT TO BE CARRIED OUT | 2026-08-27T04:44:23.057 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-016115 | PS5-60-PA-3400 |  | B | M | 21:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO- RUN | EACOP | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | 21:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO- RUN by commissioning team | 2026-08-27T12:49:55.397 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-016116 | PS5-60-PA-3300 |  | B | M | 21:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO- RUN | EACOP | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  | 21:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO- RUN by commisioning team | 2026-08-27T12:57:32.000 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-016120 | PS5-01-PA-3200A |  | B | M | 21 COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO- RUN | EACOP | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  | 21:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO- RUN by commissioning team | 2026-08-27T14:14:46.290 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-016121 | PS5-01-PA-3200B |  | B | M | 21:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO- RUN | EACOP | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  | 21:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO- RUN by commissioning | 2026-08-27T14:19:08.237 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-016122 | PS5-28-PA-3700A |  | C | M | 14:TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | CPP AGI | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  | TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | 2026-08-27T14:35:48.937 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-016123 | PS5-28-PA-3700B |  | C | M | 14:TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | CPP AGI | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  | TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | 2026-08-27T14:39:22.127 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-016124 | PS5-60-51_SS_ALL_LINES |  | B | P | 6: Wire Mesh to be installed | CPP AGI | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C |  | Originated |  | Wire Mesh to be installed | 2026-08-27T14:42:06.840 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-016125 | PS5-60-52_SS_ALL_LINES |  | B | P | 6:wire mesh to be installed | CPP AGI | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D |  | Originated |  | Wire mesh to be installed | 2026-08-27T14:45:01.323 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-016126 | PS5-28-PA-3400 |  | C | M | 21:TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | CPP AGI | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  | TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | 2026-08-27T14:49:18.713 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-016129 | PS5-25-BI-2201-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-27T16:44:10.707 | Galang, Angelo | PS5 - Milestone A
PL-016130 | PS5-25-BI-2201-CC01 |  | B | I | Clamp ang support not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-27T16:45:14.147 | Galang, Angelo | PS5 - Milestone A
PL-016131 | PS5-25-BI-2203-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-27T17:01:23.910 | Galang, Angelo | PS5 - Milestone A
PL-016132 | PS5-25-BI-2203-CC01 |  | B | I | Clamp and support not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-27T17:02:23.060 | Galang, Angelo | PS5 - Milestone A
PL-016133 | PS5-25-BI-2205-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-25-01 - Export Pipeline Pig Receiver |  | Originated |  | CTR to rectify | 2026-08-27T17:08:20.080 | Galang, Angelo | PS5 - Milestone H
PL-016134 | PS5-25-BI-2205-CC01 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-25-01 - Export Pipeline Pig Receiver |  | Originated |  | CTR to rectify | 2026-08-27T17:09:10.583 | Galang, Angelo | PS5 - Milestone H
PL-016135 | PS5-25-BI-2309-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-27T17:15:38.517 | Galang, Angelo | PS5 - Milestone A
PL-016136 | PS5-25-BI-2309-CC01 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-27T17:17:20.457 | Galang, Angelo | PS5 - Milestone A
PL-016137 | PS5-25-BI-2106-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-27T17:29:00.043 | Galang, Angelo | PS5 - Milestone A
PL-016138 | PS5-25-BI-2106-CC01 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-27T17:29:45.720 | Galang, Angelo | PS5 - Milestone A
PL-016139 | PS5-25-BI-2308-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-27T17:35:48.527 | Galang, Angelo | PS5 - Milestone A
PL-016140 | PS5-25-BI-2308-CC01 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-27T17:36:33.570 | Galang, Angelo | PS5 - Milestone A
PL-016141 | PS5-25-BI-2316-CC01 |  | B | I | Ferrule tags not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-27T17:42:14.410 | Galang, Angelo | PS5 - Milestone A
PL-016142 | PS5-25-BI-2316-CC01 |  | B | I | Clamp and support for screen shield not available | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | CTR to rectify | 2026-08-27T17:43:03.787 | Galang, Angelo | PS5 - Milestone A
PL-016251 | PS5-60-UZ-8200B |  | B | M | PRESSURE GAUGE TO BE FIXED | CPP AGI | PS5-60-36 - Injector Tip Cooling Module B |  | Originated |  | PRESSURE GAUGE TO BE FIXED | 2026-08-28T12:38:49.000 | arun, jabesteen | PS5 - Milestone B
PL-016307 | PS5-28-PA-3700A |  | B | M | 14.1:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN BY COMMISSIONING | EACOP | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  | COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN BY COMMISSIONING | 2026-08-28T14:20:03.630 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-016309 | PS5-28-PA-3700B |  | B | M | 14.1:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN BY COMMISSIONING | EACOP | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  | COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN BY COMMISSIONING | 2026-08-28T14:21:26.803 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-016516 | PS5-60-TR-4300 |  | B | M | NAME PLATE TO BE INSTALLED | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  | NAME PLATE TO BE INSTALLED | 2026-08-29T08:03:45.000 | arun, jabesteen | PS5 - Milestone E
PL-016517 | PS5-60-TR-4400 |  | B | M | NAME PLATE TO BE INSTALLED | CPP AGI | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | NAME PLATE TO BE INSTALLED | 2026-08-29T08:06:55.000 | arun, jabesteen | PS5 - Milestone E
PL-016518 | PS5-60-UZ-8200A |  | B | M | SKID DRAINS NEED TO BE INSTALLED ELBOW | EACOP | PS5-60-35 - Injector Tip Cooling Module A |  | Originated |  | SKID DRAINS NEED TO BE INSTALLED ELBOW | 2026-08-29T08:11:06.000 | arun, jabesteen | PS5 - Milestone B
PL-016519 | PS5-60-UZ-8200B |  | B | M | SKID DRAINS NEED TO BE INSTALLED ELBOW | EACOP | PS5-60-36 - Injector Tip Cooling Module B |  | Originated |  | SKID DRAINS NEED TO BE INSTALLED ELBOW | 2026-08-29T08:13:50.000 | arun, jabesteen | PS5 - Milestone B
PL-016541 | PS5-28-02_SS_ALL_LINES |  | B | P | 6:WIRE MESH TO BE INSTALLED | CPP AGI | PS5-28-02 - Closed Drain Header 2 |  | Originated |  | WIRE MESH TO BE INSTALLED | 2026-08-29T11:31:53.507 | Chinnathambi, Prasanth | PS5 - Milestone E
PL-016542 | PS5-60-37_SS_ALL_LINES |  | B | P | 6:WIRE MESH TO BE INSTALLED | CPP AGI | PS5-60-37 - Injector Tip Cooling Module C |  | Originated |  | WIRE MESH TO BE INSTALLED | 2026-08-29T11:35:06.903 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-016543 | PS5-60-38_SS_ALL_LINES |  | B | P | 6:WIRE MESH TO BE INSTALLED | CPP AGI | PS5-60-38 - Injector Tip Cooling Module D |  | Originated |  | WIRE MESH TO BE INSTALLED | 2026-08-29T11:37:32.460 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-016545 | PS5-60-72_SS_ALL_LINES |  | B | P | 6:WIRE MESH TO BE INSTALLED | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | WIRE MESH TO BE INSTALLED | 2026-08-29T11:39:17.633 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-016546 | PS5-60-73_SS_ALL_LINES |  | B | P | 6:WIRE MESH TO BE INSTALLED | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | WIRE MESH TO BE INSTALLED | 2026-08-29T11:41:26.013 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-016568 | PS5-06-GU-0003A |  | B | E | 'CH1+A2 - 2 extract fan metallic covers on top of cubicle are missing | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | 2 fan cover to be provided | 2026-08-29T15:07:07.000 | Shirima, Frank | PS5 - Milestone B
PL-016569 | PS5-06-GU-0003A |  | B | E | 'CH1+A2 - Fan M8 not working | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | Fan to be replaced | 2026-08-29T15:16:36.000 | Shirima, Frank | PS5 - Milestone B
PL-016573 | PS5-06-GU-0003A |  | C | E | 'CH1+A2 - terminal bloc number and terminal number for T40_1 missing | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | Terminal Block and terminal number to be provided | 2026-08-30T06:50:47.000 | Shirima, Frank | PS5 - Milestone B
PL-016574 | PS5-06-GU-0003A |  | B | E | 'INP1+A1 - 2 canbus Cat6 RJ45 cable betwwen UPS and Battery are missing - refer to SLD TZ-MID-60-RME2-150011 | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | RJ45 cables to be provided | 2026-08-30T06:55:57.000 | Shirima, Frank | PS5 - Milestone B
PL-016576 | PS5-06-GU-0003A |  | C | E | 'CH1+A2 - terminal block number for T40_2 missing | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | Terminal Block number to be provided | 2026-08-30T07:09:46.000 | Shirima, Frank | PS5 - Milestone B
PL-016577 | PS5-06-GU-0003A |  | C | E | 'CH1+A2 - X943 not shown in wiring diagram | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | Wiring to be updated | 2026-08-30T07:13:14.000 | Shirima, Frank | PS5 - Milestone B
PL-016578 | PS5-60-01_SS_ALL_LINES |  | C | P | 6.1:Colour code and marking to be done | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Colour code and marking to be done | 2026-08-30T07:23:08.480 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016579 | PS5-06-GU-0003B |  | C | E | 'CH2+A7 - terminal block number for T40_2 interface missing | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | Terminal Block number to be provided | 2026-08-30T07:25:08.000 | Shirima, Frank | PS5 - Milestone B
PL-016580 | PS5-06-GU-0003A |  | C | E | 'CH2+A7 - terminal block number for T40_2 interface missing | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | Terminal Block number to be provided | 2026-08-30T07:27:21.000 | Shirima, Frank | PS5 - Milestone B
PL-016581 | PS5-60-04_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-08-30T07:31:44.517 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016582 | PS5-60-04_SS_ALL_LINES |  | C | P | 6.1: Stenciling to be done | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Stenciling to be done | 2026-08-30T07:32:46.730 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016584 | PS5-60-27_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-08-30T07:43:29.963 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016585 | PS5-60-27_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  | Stenciling to be done | 2026-08-30T07:44:24.790 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016587 | PS5-60-49_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-08-30T07:51:02.527 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016588 | PS5-60-49_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A |  | Originated |  | Stenciling to be done | 2026-08-30T07:52:43.930 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016589 | PS5-60-50_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-08-30T07:57:47.740 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016590 | PS5-60-50_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B |  | Originated |  | Stenciling to be done | 2026-08-30T07:59:27.840 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016591 | PS5-60-56_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-08-30T08:05:19.040 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016592 | PS5-60-56_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | Stenciling to be done | 2026-08-30T08:06:08.747 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016596 | PS5-60-58_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-08-30T10:14:59.630 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016597 | PS5-60-58_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | Stenciling to be done | 2026-08-30T10:18:01.990 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016598 | PS5-60-70_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-08-30T10:21:41.680 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016599 | PS5-60-70_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  | Stenciling to be done | 2026-08-30T10:22:17.470 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016600 | PS5-60-71_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-08-30T10:27:22.423 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016601 | PS5-60-71_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  | Stenciling to be done | 2026-08-30T10:27:55.890 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016603 | PS5-71-20_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-08-30T10:32:19.550 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016604 | PS5-71-20_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank |  | Originated |  | Stenciling to be done | 2026-08-30T10:33:49.380 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016606 | PS5-71-21_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-08-30T10:38:00.433 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016607 | PS5-71-21_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  | Stenciling to be done | 2026-08-30T10:38:46.790 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016608 | PS5-71-22_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-08-30T10:44:36.050 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016610 | PS5-71-22_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | Stenciling to be done | 2026-08-30T10:48:59.700 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016614 |  | EACOP-PS5-60-24-0344 | B | P | 18:TZ-MID-68-WPR2-208480 - ITEM 05, BALL VALVE , 316/316L SS A182-F316/F316L , CL300 RLMU to be done | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  | RLMU to be done | 2026-08-30T12:48:15.697 | Bhagavath, sangeeth | PS5 - Milestone E
PL-016615 |  | EACOP-PS5-60-24-0344 | B | P | 18.1:TZ-MID-68-WPR2-208480 - Item 06 / PS5 60 LIT-4301, LEVEL INSTRUMENT to be install | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  | LEVEL INSTRUMENT to be install | 2026-08-30T12:49:59.977 | Bhagavath, sangeeth | PS5 - Milestone E
PL-016616 |  | EACOP-PS5-60-25-0345 | B | P | 18:TZ-MID-68-WPR2-208483 - ITEM 05, Ball Valve, CL300 RLMU tobe done | CPP AGI | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | RLMU tobe done | 2026-08-30T12:57:34.097 | Bhagavath, sangeeth | PS5 - Milestone E
PL-016617 |  | EACOP-PS5-60-25-0345 | B | P | 18.1:TZ-MID-68-WPR2-208483 - Item 06 / PS5 60 LIT-4401 , LEVEL INSTRUMENT to be install | CPP AGI | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | LEVEL INSTRUMENT to be install | 2026-08-30T12:58:41.597 | Bhagavath, sangeeth | PS5 - Milestone E
PL-016620 | PS5-06-GU-0003A |  | B | E | 'INV1+A3 - Resistor -R11 & R14 are damaged - precharge xircuit not working | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | Resistor to be provided | 2026-08-30T14:22:42.000 | Shirima, Frank | PS5 - Milestone B
PL-016621 | PS5-06-GU-0003B |  | B | E | 'INV2+A8 - Resistor -R11 & R14 are damaged - precharge xircuit not working | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | Resistor to be provided | 2026-08-30T14:27:06.000 | Shirima, Frank | PS5 - Milestone B
PL-016622 | PS5-06-GU-0003B |  | B | E | 'INV2+A8 - internal wiring from X981 to A89 missing along with the connector at A89 | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | internal wiring and connector to be provided | 2026-08-30T14:30:27.000 | Shirima, Frank | PS5 - Milestone B
PL-016623 | PS5-06-GU-0003A |  | B | E | 'INV1+A3 - interpanel wiring to link X990 in INV1 to X990 in CH2 is missing | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | Internal wiring to be provided | 2026-08-30T14:32:56.000 | Shirima, Frank | PS5 - Milestone B
PL-016624 | PS5-06-GU-0003A |  | B | E | 'CH1+A2 - interpanel wiring to link T40_2 from CH1 to CH2 is missing | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | Internal wiring to be provided | 2026-08-30T14:36:40.000 | Shirima, Frank | PS5 - Milestone B
PL-016625 | PS5-28-PA-3400 |  | B | M | 14: COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN BY COMMISSIONING | EACOP | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  | COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN BY COMMISSIONING | 2026-08-30T14:36:51.797 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-016626 | PS5-28-PA-3400 |  | C | M | 14.1:TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | CPP AGI | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  | TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | 2026-08-30T14:38:46.503 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-016627 | PS5-06-GU-0003A |  | B | E | 'CH1+A2 - Relay settings for DC Earth Fault to be provided | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | Setting to be provided | 2026-08-30T14:40:10.000 | Shirima, Frank | PS5 - Milestone B
PL-016628 | PS5-06-GU-0003B |  | B | E | 'CH2+A7 - Relay settings for DC Earth Fault to be privided | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | setting to be provided | 2026-08-30T14:41:58.000 | Shirima, Frank | PS5 - Milestone B
PL-016629 | PS5-06-GU-0003A |  | C | E | 'Load Bank breaker Q8 is connected at -Q6 UPS side and not battery side | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | SLD TZ-MID-60-RME2-150013 To be updated | 2026-08-30T14:44:21.000 | Shirima, Frank | PS5 - Milestone B
PL-016630 | PS5-06-GU-0003A |  | C | E | 'Wiring diagram rev 7 from factory has been submitted to EACOP whereas Vendor is having rev 10 available | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | Latest TZ-MID-60-RME2-150015 To be updated | 2026-08-30T14:45:53.000 | Shirima, Frank | PS5 - Milestone B
PL-016631 | PS5-06-GU-0003A |  | B | E | 'Wiring TZ-MID-60-RME2-150013 To be updated | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | Drawing to be updated | 2026-08-30T14:47:18.000 | Shirima, Frank | PS5 - Milestone B
PL-016632 | PS5-06-GU-0003B |  | B | E | 'INV2+A8 - door closing mechanism damaged | EACOP | PS5-06-02 - AC UPS - Power Generator Building |  | Originated |  | door mechanism to be replaced | 2026-08-30T14:48:55.000 | Shirima, Frank | PS5 - Milestone B
PL-016633 | PS5-28-PA-3400 |  | C | M | 14.2:EARTHING TO BE DONE | CPP AGI | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  | EARTHING TO BE DONE | 2026-08-31T07:07:59.300 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-016643 | PS5-60-VA-5100B |  | B | M | SKID DRAINS NEED TO BE INSTALLED ELBOW | EACOP | PS5-60-29 - Air Receiver B & Air Regulator B |  | Originated |  | SKID DRAINS NEED TO BE INSTALLED ELBOW | 2026-08-31T08:09:00.000 | arun, jabesteen | PS5 - Milestone B
PL-016644 | PS5-60-VA-5100C |  | C | M | SKID DRAINS NEED TO BE INSTALLED ELBOW | EACOP | PS5-60-30 - Air Receiver C & Air Regulator C |  | Originated |  | SKID DRAINS NEED TO BE INSTALLED ELBOW | 2026-08-31T08:22:22.000 | arun, jabesteen | PS5 - Milestone D
PL-016645 | PS5-60-VA-5100D |  | C | P | SKID DRAINS NEED TO BE INSTALLED ELBOW | EACOP | PS5-60-31 - Air Receiver D & Air Regulator D |  | Originated |  |  | 2026-08-31T08:27:21.000 | arun, jabesteen | PS5 - Milestone D
PL-016646 | PS5-71-18_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-08-31T08:40:29.797 | Chinnathambi, Prasanth | PS5 - Milestone F
PL-016647 | PS5-71-18_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Originated |  | Stenciling to be done | 2026-08-31T08:41:11.970 | Chinnathambi, Prasanth | PS5 - Milestone F
PL-016649 | PS5-60-29_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-29 - Air Receiver B & Air Regulator B |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-08-31T08:45:22.707 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016650 | PS5-60-29_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-29 - Air Receiver B & Air Regulator B |  | Completed |  | Stenciling to be done | 2026-08-31T08:46:14.143 | Chinnathambi, Prasanth | PS5 - Milestone B | 2026-08-31T08:46:30.000
PL-016651 | PS5-60-28_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-28 - Air Receiver A & Air Regulator A |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-08-31T08:50:45.243 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016652 | PS5-60-28_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-28 - Air Receiver A & Air Regulator A |  | Originated |  | Stenciling to be done | 2026-08-31T08:51:40.420 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016658 | PS5-01-PA-3100A |  | C | M | 21:TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | CPP AGI | PS5-01-02 - Fire Water Pump A |  | Originated |  | TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | 2026-08-31T10:45:40.957 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-016670 | PS5-01-PA-3100B |  | C | M | 21:TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQIUPMENT | CPP AGI | PS5-01-03 - Fire Water Pump B |  | Originated |  | OUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQIUPMENT | 2026-08-31T11:03:43.963 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-016671 | PS5-01-PA-3100B |  | A | P | 21.1:PRESSURE SENCING LINE TO BE INSTALLED | CPP AGI | PS5-01-03 - Fire Water Pump B |  | Originated |  | PRESSURE SENCING LINE TO BE INSTALLED | 2026-08-31T11:09:56.603 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-016673 | PS5-01-PA-3100B |  | A | M | 21.2:PRESSURE GAUGE TO BE RE-INSTALLED | CPP AGI | PS5-01-03 - Fire Water Pump B |  | Originated |  | PRESSURE GAUGE TO BE RE-INSTALLED | 2026-08-31T11:11:43.303 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-016675 | PS5-01-PA-3100A |  | A | P | 21.1:PRESSURE SENCING LINE TO BE INSTALLED | CPP AGI | PS5-01-02 - Fire Water Pump A |  | Originated |  | PRESSURE SENCING LINE TO BE INSTALLED | 2026-08-31T11:27:51.070 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-016676 | PS5-01-PA-3100A |  | A | M | 21.2:PRESSURE GAUGE TO BE RE-INSTALLED | CPP AGI | PS5-01-02 - Fire Water Pump A |  | Originated |  | PRESSURE GAUGE TO BE RE-INSTALLED | 2026-08-31T11:28:42.137 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-016740 | PS5-03-BI-2506-CC01 |  | C | I | No Indoor Cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable tag (Yellow Black) | 2026-08-31T18:02:52.117 | Kumar, Senthil | PS5 - Milestone A
PL-016743 | PS5-03-BI-2506-CC01 |  | B | I | No Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange the Core Marker | 2026-08-31T18:06:48.690 | Kumar, Senthil | PS5 - Milestone A
PL-016747 | PS5-03-BI-2506-CC01 |  | B | I | MCT packing is not Proper | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Close the MCT Packing | 2026-08-31T18:10:38.887 | Kumar, Senthil | PS5 - Milestone A
PL-016749 | PS5-03-BI-2506-CC01 |  | B | I | No Proper Screen Earthing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange the proper Screen Earthing | 2026-08-31T18:12:15.667 | Kumar, Senthil | PS5 - Milestone A
PL-016751 | PS5-03-BI-2506-CC01 |  | C | I | No Outdoor Metal Cable Tag | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be provide the Outdoor Cable tag | 2026-08-31T18:14:18.407 | Kumar, Senthil | PS5 - Milestone A
PL-016758 | PS5-03-BI-2515-CC01 |  | C | I | No indoor Cable Tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be provide Indoor Cable tag (Yellow Black) | 2026-08-31T18:24:57.720 | Kumar, Senthil | PS5 - Milestone A
PL-016761 | PS5-03-BI-2515-CC01 |  | B | I | No Core Markers | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Core Markers | 2026-08-31T18:27:12.270 | Kumar, Senthil | PS5 - Milestone A
PL-016763 | PS5-03-BI-2515-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange proper Screen Earth | 2026-08-31T18:29:21.913 | Kumar, Senthil | PS5 - Milestone A
PL-016767 | PS5-03-BI-2515-CC01 |  | B | I | No proper MCT packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange proper MCT Packing | 2026-08-31T18:33:16.850 | Kumar, Senthil | PS5 - Milestone A
PL-016770 | PS5-03-BI-2515-CC01 |  | C | I | No outdoor Metal Cable Tag | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange the Outdoor Metal Cable tag | 2026-08-31T18:36:52.337 | Kumar, Senthil | PS5 - Milestone A
PL-016780 | PS5-25-BI-1302-CC01 |  | C | I | No Indoor Cable Tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-08-31T18:51:09.740 | Kumar, Senthil | PS5 - Milestone A
PL-016782 | PS5-25-BI-1302-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange the Proper Screen Earth | 2026-08-31T18:52:50.917 | Kumar, Senthil | PS5 - Milestone A
PL-016784 | PS5-25-BI-1302-CC01 |  | B | I | No Proper MCT packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange the Proper MCT Packing | 2026-08-31T18:54:49.843 | Kumar, Senthil | PS5 - Milestone A
PL-016788 | PS5-25-BI-1302-CC01 |  | B | I | No core Markers | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange the Core Markers | 2026-08-31T18:57:57.427 | Kumar, Senthil | PS5 - Milestone A
PL-016789 | PS5-25-BI-1302-CC01 |  | C | I | No outdoor Metal Cable Tag | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange the Outdoor Metal Cable tag | 2026-08-31T18:59:11.167 | Kumar, Senthil | PS5 - Milestone A
PL-016794 | PS5-25-BI-1310-CC01 |  | C | I | No Indoor Cable Tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-08-31T19:06:13.893 | Kumar, Senthil | PS5 - Milestone A
PL-016795 | PS5-25-BI-1310-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-08-31T19:15:53.673 | Kumar, Senthil | PS5 - Milestone A
PL-016796 | PS5-25-BI-1310-CC01 |  | B | I | No Proper MCT Packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Proper MCT Packing | 2026-08-31T19:17:08.710 | Kumar, Senthil | PS5 - Milestone A
PL-016797 | PS5-25-BI-1310-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-08-31T19:18:13.227 | Kumar, Senthil | PS5 - Milestone A
PL-016798 | PS5-25-BI-2104-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-08-31T19:24:11.047 | Kumar, Senthil | PS5 - Milestone A
PL-016799 | PS5-25-BI-2104-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-08-31T19:25:57.847 | Kumar, Senthil | PS5 - Milestone A
PL-016800 | PS5-25-BI-2104-CC01 |  | B | I | No Proper MCT Packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Proper MCT Packing | 2026-08-31T19:26:55.980 | Kumar, Senthil | PS5 - Milestone A
PL-016801 | PS5-25-BI-2108-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T04:47:17.547 | Kumar, Senthil | PS5 - Milestone A
PL-016802 | PS5-25-BI-2108-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T04:47:55.080 | Kumar, Senthil | PS5 - Milestone A
PL-016803 | PS5-25-BI-2109-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T04:52:55.443 | Kumar, Senthil | PS5 - Milestone A
PL-016804 | PS5-25-BI-2109-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T04:54:02.500 | Kumar, Senthil | PS5 - Milestone A
PL-016805 | PS5-25-BI-2109-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-01T04:54:54.613 | Kumar, Senthil | PS5 - Milestone A
PL-016806 | PS5-28-BI-1307-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T05:00:10.513 | Kumar, Senthil | PS5 - Milestone A
PL-016807 | PS5-28-BI-1307-CC01 |  | B | I | No Core Markers | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-01T05:00:53.140 | Kumar, Senthil | PS5 - Milestone A
PL-016808 | PS5-71-BI-1110-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T05:11:24.707 | Kumar, Senthil | PS5 - Milestone A
PL-016809 | PS5-71-BI-1110-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T05:13:51.727 | Kumar, Senthil | PS5 - Milestone A
PL-016810 | PS5-71-BI-1110-CC01 |  | B | I | Missing Cable’s some Core Markers | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-01T05:15:36.630 | Kumar, Senthil | PS5 - Milestone A
PL-016811 | PS5-71-BI-1113-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T05:22:50.103 | Kumar, Senthil | PS5 - Milestone A
PL-016813 | PS5-71-BI-1113-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T05:24:44.737 | Kumar, Senthil | PS5 - Milestone A
PL-016814 | PS5-71-BI-1113-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-01T05:25:41.907 | Kumar, Senthil | PS5 - Milestone A
PL-016815 | PS5-71-BI-1117-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T05:30:35.980 | Kumar, Senthil | PS5 - Milestone A
PL-016816 | PS5-71-BI-1117-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T05:32:06.833 | Kumar, Senthil | PS5 - Milestone A
PL-016817 | PS5-71-BI-2113-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T05:36:27.993 | Kumar, Senthil | PS5 - Milestone A
PL-016818 | PS5-71-BI-2113-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T05:37:38.917 | Kumar, Senthil | PS5 - Milestone A
PL-016819 | PS5-71-BI-2114-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T05:43:15.900 | Kumar, Senthil | PS5 - Milestone A
PL-016820 | PS5-71-BI-2114-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T05:44:15.357 | Kumar, Senthil | PS5 - Milestone A
PL-016821 | PS5-71-BI-2114-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-01T05:45:23.347 | Kumar, Senthil | PS5 - Milestone A
PL-016831 | PS5-71-BI-2115-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T07:13:57.650 | Kumar, Senthil | PS5 - Milestone A
PL-016832 | PS5-60-24_SS_ALL_LINES |  | C | P | 6:Stenciling to be done | CPP AGI | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  | Stenciling to be done | 2026-09-01T07:15:40.073 | Chinnathambi, Prasanth | PS5 - Milestone E
PL-016833 | PS5-71-BI-2115-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T07:17:31.923 | Kumar, Senthil | PS5 - Milestone A
PL-016834 | PS5-60-25_SS_ALL_LINES |  | C | P | 6:Stenciling to be done | CPP AGI | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  | Stenciling to be done | 2026-09-01T07:17:39.100 | Chinnathambi, Prasanth | PS5 - Milestone E
PL-016835 | PS5-60-56_SS_ALL_LINES |  | B | P | 16:VALVE,FLANGE AND PENETRATION LOCATION TO BE DONE | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | VALVE,FLANGE AND PENETRATION LOCATION TO BE DONE | 2026-09-01T07:22:44.030 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016836 | PS5-71-BI-2118-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T07:22:55.230 | Kumar, Senthil | PS5 - Milestone A
PL-016837 | PS5-71-BI-2118-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T07:23:32.887 | Kumar, Senthil | PS5 - Milestone A
PL-016838 | PS5-71-BI-2118-CC01 |  | B | I | No Proper MCT Packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Proper MCT Packing | 2026-09-01T07:24:05.310 | Kumar, Senthil | PS5 - Milestone A
PL-016839 | PS5-71-BI-2118-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-01T07:25:15.667 | Kumar, Senthil | PS5 - Milestone A
PL-016841 | PS5-71-BI-2118-CC01 |  | C | I | No Outdoor Metal Cable Tag | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Outdoor Metal Cable Tag | 2026-09-01T07:26:02.303 | Kumar, Senthil | PS5 - Milestone A
PL-016844 | PS5-71-BI-2119-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T07:30:36.843 | Kumar, Senthil | PS5 - Milestone A
PL-016846 | PS5-71-BI-2119-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T07:32:12.003 | Kumar, Senthil | PS5 - Milestone A
PL-016848 | PS5-71-BI-2120-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T07:36:55.803 | Kumar, Senthil | PS5 - Milestone A
PL-016849 | PS5-71-BI-2120-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T07:38:18.900 | Kumar, Senthil | PS5 - Milestone A
PL-016850 | PS5-71-BI-2120-CC01 |  | B | I | No Proper MCT Packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Proper MCT Packing | 2026-09-01T07:39:08.443 | Kumar, Senthil | PS5 - Milestone A
PL-016852 | PS5-71-BI-2120-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-01T07:39:54.187 | Kumar, Senthil | PS5 - Milestone A
PL-016853 | PS5-71-BI-2120-CC01 |  | C | I | No Outdoor Metal Cable Tag | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Outdoor Metal Cable Tag | 2026-09-01T07:40:42.310 | Kumar, Senthil | PS5 - Milestone A
PL-016855 | PS5-71-BI-2121-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T07:45:45.897 | Kumar, Senthil | PS5 - Milestone A
PL-016856 | PS5-71-BI-2121-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T07:46:27.327 | Kumar, Senthil | PS5 - Milestone A
PL-016857 | PS5-71-BI-2121-CC01 |  | B | I | No Proper MCT Packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Proper MCT Packing | 2026-09-01T07:47:19.540 | Kumar, Senthil | PS5 - Milestone A
PL-016858 | PS5-71-BI-2121-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-01T07:47:58.867 | Kumar, Senthil | PS5 - Milestone A
PL-016859 | PS5-71-BI-2121-CC01 |  | C | I | No Outdoor Metal Cable Tag | CPP AGI | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Outdoor Metal Cable Tag | 2026-09-01T07:48:39.000 | Kumar, Senthil | PS5 - Milestone A
PL-016861 | PS5-71-BI-2121-CC01 |  | B | I | No Proper Cable Dressing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange proper Cable Dressing | 2026-09-01T07:49:30.260 | Kumar, Senthil | PS5 - Milestone A
PL-016862 | PS5-71-BI-2122-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T07:54:25.817 | Kumar, Senthil | PS5 - Milestone A
PL-016864 | PS5-71-BI-2122-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T07:55:50.220 | Kumar, Senthil | PS5 - Milestone A
PL-016865 | PS5-71-BI-2122-CC01 |  | B | I | No proper Cable Dressing (Below Unistrut channel Missing) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange proper Cable Dressing | 2026-09-01T07:56:54.347 | Kumar, Senthil | PS5 - Milestone A
PL-016875 | PS5-60-23_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-23 - Instrument Air Distribution lines |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-09-01T08:24:52.810 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016876 | PS5-60-23_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-23 - Instrument Air Distribution lines |  | Originated |  | Stenciling to be done | 2026-09-01T08:25:35.797 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016900 | PS5-60-58_SS_ALL_LINES |  | B | P | 16: VALVE,FLANGE TO BE DONE | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | VALVE,FLANGE TO BE DONE | 2026-09-01T11:15:35.960 | Chinnathambi, Prasanth | PS5 - Milestone B
PL-016901 |  | EACOP-PS5-01-01-0001 | B | P | 18:TZ-MID-68-WPR2-207154 - F15 Flange management to be done after Vendor installing PG | CPP AGI | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  | F15 Flange management to be done after Vendor installing PG | 2026-09-01T11:16:11.490 | Bhagavath, sangeeth | PS5 - Milestone C
PL-016906 |  | EACOP-PS5-01-03-0004 | C | P | 18:TZ-MID-68-WPR2-206319 - ITEM 14, Bolt projection threads are at the same level | CPP AGI | PS5-01-03 - Fire Water Pump B |  | Originated |  | TZ-MID-68-WPR2-206319 - ITEM 14, Bolt projection threads are at the same level | 2026-09-01T11:35:33.507 | Bhagavath, sangeeth | PS5 - Milestone C
PL-016925 |  | EACOP-PS5-01-01-0006 | B | P | 18:TZ-MID-68-WPR2-207153 - F15 Flange management to be done after PG installed by vendor | CPP AGI | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  | F15 Flange management to be done after PG installed by vendor | 2026-09-01T12:01:54.780 | Bhagavath, sangeeth | PS5 - Milestone C
PL-016936 |  | EACOP-PS5-01-02-0007 | C | P | 18:TZ-MID-68-WPR2-206318 - Item 14, Bolt projection threads are at the same level | CPP AGI | PS5-01-02 - Fire Water Pump A |  | Originated |  | Item 14, Bolt projection threads are at the same level | 2026-09-01T12:07:20.153 | Bhagavath, sangeeth | PS5 - Milestone C
PL-016946 | PS5-71-BI-2123-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T12:23:09.703 | Kumar, Senthil | PS5 - Milestone A
PL-016948 | PS5-71-BI-2123-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T12:24:25.477 | Kumar, Senthil | PS5 - Milestone A
PL-016954 | PS5-71-BI-2124-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T12:28:22.707 | Kumar, Senthil | PS5 - Milestone A
PL-016955 | PS5-71-BI-2124-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T12:29:20.693 | Kumar, Senthil | PS5 - Milestone A
PL-016956 | PS5-71-BI-2125-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T12:33:03.267 | Kumar, Senthil | PS5 - Milestone A
PL-016957 |  | EACOP-PS5-01-04-0019 | B | P | 18:TZ-MID-68-WPR2-206265 - Item 14, LEVER/HANDWHEEL ORI= E, RLMU tobe done | CPP AGI | PS5-01-04 - Fire Water Pump Mini Flow Recycle |  | Originated |  | LEVER/HANDWHEEL ORI= E, RLMU tobe done | 2026-09-01T12:34:12.877 | Bhagavath, sangeeth | PS5 - Milestone C
PL-016959 | PS5-71-BI-2125-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T12:34:59.150 | Kumar, Senthil | PS5 - Milestone A
PL-016960 |  | EACOP-PS5-01-04-0019 | B | P | 18.1:TZ-MID-68-WPR2-206288 - ITEM 14, LEVER/HANDWHEEL ORI= E, RLMU tobe done | CPP AGI | PS5-01-04 - Fire Water Pump Mini Flow Recycle |  | Originated |  | LEVER/HANDWHEEL ORI= E, RLMU tobe done | 2026-09-01T12:35:19.240 | Bhagavath, sangeeth | PS5 - Milestone C
PL-016961 | PS5-71-BI-2125-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-01T12:35:41.990 | Kumar, Senthil | PS5 - Milestone A
PL-016984 |  | EACOP-PS5-01-03-0014 | B | P | 18: TZ-MID-68-WPR2-206288 - Item 14, LEVER/HANDWHEEL ORI= E, RLMU tobe done | CPP AGI | PS5-01-03 - Fire Water Pump B |  | Originated |  | TZ-MID-68-WPR2-206288 - Item 14, LEVER/HANDWHEEL ORI= E, RLMU tobe done | 2026-09-01T13:07:41.000 | Bhagavath, sangeeth | PS5 - Milestone C
PL-016985 | PS5-01-TR-4100A |  | C | M | 23:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-01-02 - Fire Water Pump A |  | Originated |  | TOUCH UP PAINTING TO BE DONE | 2026-09-01T13:27:03.020 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-016987 | PS5-01-TR-4100A |  | B | E | 23.1:EARTHING TO BE DONE | CPP AGI | PS5-01-02 - Fire Water Pump A |  | Originated |  | EARTHING TO BE DONE | 2026-09-01T13:28:04.437 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-016990 |  | EACOP-PS5-01-01-0002 | B | P | 18:TZ-MID-68-WPR2-207026 & TZ-MID-68-WPR2-207027 - F15 Flange Management to be done(PG in vender Scope) | CPP AGI | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  | F15 Flange Management to be done(PG in vender Scope) | 2026-09-01T13:30:21.213 | Bhagavath, sangeeth | PS5 - Milestone C
PL-016992 | PS5-01-TR-4100B |  | C | M | 23:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-01-03 - Fire Water Pump B |  | Originated |  | TOUCH UP PAINTING TO BE DONE | 2026-09-01T13:30:50.760 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-016993 | PS5-01-TR-4100B |  | B | E | 23.1:EARTHING TO BE DONE | CPP AGI | PS5-01-03 - Fire Water Pump B |  | Originated |  | EARTHING TO BE DONE | 2026-09-01T13:31:59.710 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-017017 |  | EACOP-PS5-01-07-0021 | B | P | 18:TZ-MID-68-WPR2-206382 & TZ-MID-68-WPR2-206382 - Item 14, LEVER/HANDWHEEL ORI= N, RLMU tobe done | CPP AGI | PS5-01-07 - Fire Water Ring Main & Distribution |  | Originated |  | TZ-MID-68-WPR2-206382 & TZ-MID-68-WPR2-206382 - Item 14, LEVER/HANDWHEEL ORI= N, RLMU tobe done | 2026-09-01T14:17:22.213 | Bhagavath, sangeeth | PS5 - Milestone C
PL-017018 | PS5-03-BI-2503-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T14:17:49.190 | Kumar, Senthil | PS5 - Milestone A
PL-017019 | PS5-03-BI-2503-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T14:19:42.417 | Kumar, Senthil | PS5 - Milestone A
PL-017020 | PS5-03-BI-2503-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-01T14:21:25.793 | Kumar, Senthil | PS5 - Milestone A
PL-017025 | PS5-28-VDC-1400 |  | C | M | 18:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  | TOUCH UP PAINTING TO BE DONE | 2026-09-01T14:57:38.443 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-017026 | PS5-28-VDC-1400 |  | B | E | 18.1:EARTHING TO BE DONE | CPP AGI | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  | EARTHING TO BE DONE | 2026-09-01T14:58:20.953 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-017044 | PS5-03-BI-2509-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T17:42:15.480 | Kumar, Senthil | PS5 - Milestone A
PL-017045 | PS5-03-BI-2509-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T17:44:44.657 | Kumar, Senthil | PS5 - Milestone A
PL-017046 | PS5-03-BI-2509-CC01 |  | B | I | No Proper MCT Packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Proper MCT Packing | 2026-09-01T17:45:40.620 | Kumar, Senthil | PS5 - Milestone A
PL-017047 | PS5-03-BI-2509-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-01T17:46:49.837 | Kumar, Senthil | PS5 - Milestone A
PL-017048 | PS5-25-BI-1101-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T17:51:30.280 | Kumar, Senthil | PS5 - Milestone A
PL-017049 | PS5-25-BI-1101-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T17:52:42.613 | Kumar, Senthil | PS5 - Milestone A
PL-017050 | PS5-25-BI-1101-CC01 |  | B | I | No Proper MCT Packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Proper MCT Packing | 2026-09-01T17:53:50.430 | Kumar, Senthil | PS5 - Milestone A
PL-017051 | PS5-25-BI-1102-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T17:58:15.047 | Kumar, Senthil | PS5 - Milestone A
PL-017052 | PS5-25-BI-1102-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T17:59:23.143 | Kumar, Senthil | PS5 - Milestone A
PL-017053 | PS5-25-BI-1102-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-01T18:00:44.517 | Kumar, Senthil | PS5 - Milestone A
PL-017054 | PS5-25-BI-1103-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T18:05:11.470 | Kumar, Senthil | PS5 - Milestone A
PL-017055 | PS5-25-BI-1103-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T18:06:03.817 | Kumar, Senthil | PS5 - Milestone A
PL-017056 | PS5-25-BI-1103-CC01 |  | B | I | No Proper MCT Packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Proper MCT Packing | 2026-09-01T18:07:26.163 | Kumar, Senthil | PS5 - Milestone A
PL-017057 | PS5-25-BI-1104-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T18:13:06.540 | Kumar, Senthil | PS5 - Milestone A
PL-017058 | PS5-25-BI-1104-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T18:14:06.313 | Kumar, Senthil | PS5 - Milestone A
PL-017059 | PS5-25-BI-1104-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-01T18:15:36.147 | Kumar, Senthil | PS5 - Milestone A
PL-017060 | PS5-25-BI-1201-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T18:20:28.640 | Kumar, Senthil | PS5 - Milestone A
PL-017061 | PS5-25-BI-1201-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-01T18:21:14.413 | Kumar, Senthil | PS5 - Milestone A
PL-017062 | PS5-25-BI-1201-CC01 |  | B | I | No Proper MCT Packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Proper MCT Packing | 2026-09-01T18:21:51.033 | Kumar, Senthil | PS5 - Milestone A
PL-017063 | PS5-25-BI-1201-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-01T18:23:04.167 | Kumar, Senthil | PS5 - Milestone A
PL-017066 | PS5-01-IE-0009A-CL01 |  | C | E | No indoor cable tag (Yellow Black) | KENT | PS5-01-02 - Fire Water Pump A |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-01T18:44:59.727 | Kumar, Senthil | PS5 - Milestone C
PL-017067 | PS5-01-IE-0009A-CL01 |  | B | E | No Proper Earth | KENT | PS5-01-02 - Fire Water Pump A |  | Originated |  | To be Provide Proper Earth | 2026-09-01T18:48:21.530 | Kumar, Senthil | PS5 - Milestone C
PL-017068 | PS5-01-IE-0009A-CL01 |  | B | E | No Cable’s Core Marker | KENT | PS5-01-02 - Fire Water Pump A |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-01T18:50:25.543 | Kumar, Senthil | PS5 - Milestone C
PL-017071 | PS5-60-TX-41500A |  | C | M | 23:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | TOUCH UP PAINTING TO BE DONE | 2026-09-02T04:15:32.733 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017072 | PS5-60-TX-41500A |  | B | E | 23.1:EARTHING TO BE DONE | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | EARTHING TO BE DONE | 2026-09-02T04:16:08.807 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017110 | PS5-60-TX-41500B |  | B | E | 23:EARTHING TO BE DONE | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | EARTHING TO BE DONE | 2026-09-02T06:27:33.810 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017111 | PS5-60-TX-41500B |  | C | M | 23.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | TOUCH UP PAINTING TO BE DONE | 2026-09-02T06:28:27.877 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017115 | PS5-60-TX-41600A |  | C | M | 23:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | TOUCH UP PAINTING TO BE DONE | 2026-09-02T06:31:57.020 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017116 | PS5-60-TX-41600A |  | B | E | 23.1:EARTHING TO BE DONE | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | EARTHING TO BE DONE | 2026-09-02T06:33:05.160 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017117 | PS5-60-TX-41600B |  | B | E | 23:EARTHING TO BE DONE | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | EARTHING TO BE DONE | 2026-09-02T06:36:53.373 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017118 | PS5-60-TX-41600B |  | C | P | 23.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  | TOUCH UP PAINTING TO BE DONE | 2026-09-02T06:37:27.327 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017122 | PS5-60-TX-41700A |  | C | M | 23TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-76 - Engine G Cooling system |  | Originated |  | TOUCH UP PAINTING TO BE DONE | 2026-09-02T06:40:01.767 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-017124 | PS5-60-TX-41700A |  | B | E | 23.1: EARTHING TO BE DONE | CPP AGI | PS5-60-76 - Engine G Cooling system |  | Originated |  | 23.1: EARTHING TO BE DONE | 2026-09-02T06:41:01.640 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-017126 | PS5-60-TX-41700B |  | B | E | 23: EARTHING TO BE DONE | CPP AGI | PS5-60-76 - Engine G Cooling system |  | Originated |  | 23: EARTHING TO BE DONE | 2026-09-02T06:46:48.903 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-017127 | PS5-60-TX-41700B |  | C | M | 23.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-76 - Engine G Cooling system |  | Originated |  | TOUCH UP PAINTING TO BE DON | 2026-09-02T06:48:02.067 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-017161 | PS5-28-VDC-1100 |  | B | M | 18:TOUCH UP PAINTING & INSULATION TO BE DONE | CPP AGI | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  |  | 2026-09-02T10:17:13.323 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-017162 | PS5-28-VDC-1100 |  | B | E | 18.1:EARTHING TO BE DONE | CPP AGI | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  | EARTHING TO BE DONE | 2026-09-02T10:19:03.737 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-017164 | PS5-01-BI-1118-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-02T10:27:17.937 | Kumar, Senthil | PS5 - Milestone A
PL-017165 | PS5-01-BI-1118-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-02T10:29:08.760 | Kumar, Senthil | PS5 - Milestone A
PL-017166 | PS5-01-BI-1118-CC01 |  | B | I | No Proper MCT Packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Proper MCT Packing | 2026-09-02T10:29:57.100 | Kumar, Senthil | PS5 - Milestone A
PL-017172 | PS5-25-BI-2103-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-02T10:41:29.187 | Kumar, Senthil | PS5 - Milestone A
PL-017173 | PS5-25-BI-2103-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-02T10:43:09.143 | Kumar, Senthil | PS5 - Milestone A
PL-017174 | PS5-25-BI-2103-CC01 |  | B | I | No Proper MCT Packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Proper MCT Packing | 2026-09-02T10:43:48.583 | Kumar, Senthil | PS5 - Milestone A
PL-017175 | PS5-28-BI-1303-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-02T10:46:58.177 | Kumar, Senthil | PS5 - Milestone A
PL-017177 | PS5-28-BI-1303-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-02T10:48:03.430 | Kumar, Senthil | PS5 - Milestone A
PL-017178 | PS5-28-BI-1303-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-02T10:48:41.267 | Kumar, Senthil | PS5 - Milestone A
PL-017182 | PS5-50-BI-1107-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-02T10:52:47.593 | Kumar, Senthil | PS5 - Milestone A
PL-017184 | PS5-50-BI-1107-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-02T10:53:37.310 | Kumar, Senthil | PS5 - Milestone A
PL-017186 | PS5-50-BI-1107-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-02T10:56:48.187 | Kumar, Senthil | PS5 - Milestone A
PL-017256 | PS5-53-BI-1108-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-02T12:49:04.267 | Kumar, Senthil | PS5 - Milestone A
PL-017257 | PS5-53-BI-1108-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-02T12:50:04.100 | Kumar, Senthil | PS5 - Milestone A
PL-017258 | PS5-53-BI-1108-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-02T12:51:07.083 | Kumar, Senthil | PS5 - Milestone A
PL-017259 | PS5-53-BI-1108-CC01 |  | B | I | No Proper Cable Dressing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arange proper Cable Dressing | 2026-09-02T12:52:01.323 | Kumar, Senthil | PS5 - Milestone A
PL-017260 | PS5-71-BI-1111-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-02T13:00:08.290 | Kumar, Senthil | PS5 - Milestone A
PL-017261 | PS5-71-BI-1111-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-02T13:00:56.340 | Kumar, Senthil | PS5 - Milestone A
PL-017262 | PS5-71-BI-1111-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-02T13:02:27.390 | Kumar, Senthil | PS5 - Milestone A
PL-017263 | PS5-71-BI-2116-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-02T13:09:46.173 | Kumar, Senthil | PS5 - Milestone A
PL-017265 | PS5-71-BI-2116-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-02T13:10:50.897 | Kumar, Senthil | PS5 - Milestone A
PL-017266 | PS5-71-BI-2116-CC01 |  | B | I | No Proper MCT Packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Proper MCT Packing | 2026-09-02T13:11:57.890 | Kumar, Senthil | PS5 - Milestone A
PL-017268 | PS5-71-BI-2310-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-02T13:17:26.357 | Kumar, Senthil | PS5 - Milestone A
PL-017269 | PS5-71-BI-2310-CC01 |  | C | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-02T13:18:44.647 | Kumar, Senthil | PS5 - Milestone A
PL-017270 | PS5-71-BI-2310-CC01 |  | B | I | No Proper MCT Packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Proper MCT Packing | 2026-09-02T13:20:07.393 | Kumar, Senthil | PS5 - Milestone A
PL-017271 | PS5-71-BI-2310-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-02T13:21:30.857 | Kumar, Senthil | PS5 - Milestone A
PL-017276 | PS5-60-30_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-30 - Air Receiver C & Air Regulator C |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-09-02T14:07:24.013 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017277 | PS5-60-30_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-30 - Air Receiver C & Air Regulator C |  | Originated |  | Stenciling to be done | 2026-09-02T14:07:48.880 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017278 | PS5-60-31_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-31 - Air Receiver D & Air Regulator D |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-09-02T14:11:00.667 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017279 | PS5-60-31_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-31 - Air Receiver D & Air Regulator D |  | Originated |  | Stenciling to be done | 2026-09-02T14:11:30.427 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017280 | PS5-60-IE-0004-CC08 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  |  | 2026-09-02T14:28:44.480 | Kumar, Senthil | PS5 - Milestone B
PL-017281 | PS5-60-IE-0004-CC08 |  | B | I | No Proper Screen Earth | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-02T14:29:24.713 | Kumar, Senthil | PS5 - Milestone B
PL-017282 | PS5-60-IE-0004-CC08 |  | B | I | No Proper MCT Packing | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be Arrange Proper MCT Packing | 2026-09-02T14:30:10.830 | Kumar, Senthil | PS5 - Milestone B
PL-017354 | PS5-71-08_SS_ALL_LINES |  | B | P | 6:TP-309 -Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-71-08 - CFO Pre-Pressure Modules |  | Originated |  | TP-309 -Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-09-03T07:56:43.770 | Chinnathambi, Prasanth | PS5 - Milestone H
PL-017355 | PS5-71-08_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-71-08 - CFO Pre-Pressure Modules |  | Originated |  | Stenciling to be done | 2026-09-03T07:57:38.420 | Chinnathambi, Prasanth | PS5 - Milestone H
PL-017358 | PS5-60-07_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-09-03T08:03:14.550 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017360 | PS5-60-07_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | Stenciling to be done | 2026-09-03T08:03:56.923 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017366 | PS5-60-73_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-09-03T08:09:09.123 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017367 | PS5-60-73_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  | Stenciling to be done | 2026-09-03T08:09:35.743 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017369 | PS5-60-72_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-09-03T08:16:43.103 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017370 | PS5-60-72_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | Stenciling to be done | 2026-09-03T08:17:15.837 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017371 | PS5-60-10_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-09-03T08:19:31.393 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017372 | PS5-60-10_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | Stenciling to be done | 2026-09-03T08:19:50.490 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017373 | PS5-60-IE-0004-CC11 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | No indoor cable tag (Yellow Black) | 2026-09-03T08:20:16.453 | Kumar, Senthil | PS5 - Milestone B
PL-017374 | PS5-60-IE-0004-CC11 |  | B | I | No Proper Screen Earth | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-03T08:21:03.823 | Kumar, Senthil | PS5 - Milestone B
PL-017375 | PS5-60-IE-0004-CC11 |  | B | I | No Proper MCT Packing | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be Arrange Proper MCT Packing | 2026-09-03T08:22:03.707 | Kumar, Senthil | PS5 - Milestone B
PL-017376 | PS5-60-IE-0004-CC11 |  | B | I | Wrong Cable’s Core Marker | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be Arrange Correct Cable’s Core Marker | 2026-09-03T08:22:39.783 | Kumar, Senthil | PS5 - Milestone B
PL-017377 | PS5-60-IE-0004-CC12 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-03T08:27:19.970 | Kumar, Senthil | PS5 - Milestone B
PL-017378 | PS5-60-IE-0004-CC12 |  | B | I | No Proper Screen Earth | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-03T08:28:11.230 | Kumar, Senthil | PS5 - Milestone B
PL-017379 | PS5-60-IE-0004-CC12 |  | B | I | No Proper MCT Packing | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be Arrange Proper MCT Packing | 2026-09-03T08:28:45.880 | Kumar, Senthil | PS5 - Milestone B
PL-017380 | PS5-60-IE-0004-CC12 |  | B | I | No Cable’s Core Marker | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-03T08:29:27.377 | Kumar, Senthil | PS5 - Milestone B
PL-017381 | PS5-60-TX-41500A |  | B | M | 23.2:Blind flange to be installed downstream of the drain valve Engineering / Vendor | EACOP | PS5-60-74 - Engine E Cooling system |  | Originated |  | Blind flange to be installed downstream of the drain valve Engineering / Vendor | 2026-09-03T08:52:48.510 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017403 | PS5-60-TX-41500B |  | B | M | 23.2:Blind flange to be installed downstream of the drain valve . (Engineering / Vendor) | EACOP | PS5-60-74 - Engine E Cooling system |  | Originated |  | Blind flange to be installed downstream of the drain valve . (Engineering / Vendor) | 2026-09-03T10:52:01.463 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017404 | PS5-60-TX-41600A |  | B | P | 23.2:Blind flange to be installed downstream of the drain valve . (Engineering / Vendor) | EACOP | PS5-60-75 - Engine F Cooling system |  | Originated |  | Blind flange to be installed downstream of the drain valve . (Engineering / Vendor) | 2026-09-03T10:53:42.100 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017405 | PS5-60-TX-41600B |  | B | M | 23.2:Blind flange to be installed downstream of the drain valve . (Engineering / Vendor) | EACOP | PS5-60-75 - Engine F Cooling system |  | Originated |  | Blind flange to be installed downstream of the drain valve . (Engineering / Vendor) | 2026-09-03T10:54:43.340 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017406 | PS5-60-TX-41700A |  | B | M | 23.2:Blind flange to be installed downstream of the drain valve . (Engineering / Vendor) | EACOP | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2026-09-03T10:55:38.327 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-017407 | PS5-60-TX-41700B |  | B | M | 23.2:Blind flange to be installed downstream of the drain valve . (Engineering / Vendor) | EACOP | PS5-60-76 - Engine G Cooling system |  | Originated |  | Blind flange to be installed downstream of the drain valve . (Engineering / Vendor) | 2026-09-03T10:56:36.947 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-017472 |  | EACOP-PS5-28-05-0093 | B | P | 18:TZ-MID-68-WPR2-206380 - Item 07 & 08, WN FLG & Gasket, CL300 RLMU to be done | CPP AGI | PS5-28-05 - HP Relief Header |  | Originated |  | WN FLG & Gasket, CL300 RLMU to be done | 2026-09-03T13:15:54.673 | Bhagavath, sangeeth | PS5 - Milestone G
PL-017473 |  | EACOP-PS5-28-05-0093 | B | P | 18.1:TZ-MID-68-WPR2-206380 - F4 & F5 Flange Management to be done | CPP AGI | PS5-28-05 - HP Relief Header |  | Originated |  | F4 & F5 Flange Management to be done | 2026-09-03T13:17:52.630 | Bhagavath, sangeeth | PS5 - Milestone G
PL-017480 | PS5-28-VK-1200 |  | B | E | 18: Electrical heating cable to be installed | CPP AGI | PS5-28-06 - Relief Drum and Pump |  | Originated |  | Electrical heating cable to be installed | 2026-09-03T14:09:34.177 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-017481 | PS5-28-VK-1200 |  | B | P | 18.1:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-28-06 - Relief Drum and Pump |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-09-03T14:10:42.547 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-017483 | PS5-28-VK-1200 |  | C | M | 18.2: Hot insulation to be done by Insulation team | CPP AGI | PS5-28-06 - Relief Drum and Pump |  | Originated |  | Hot insulation to be done by Insulation team | 2026-09-03T14:12:42.690 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-017485 | PS5-74-VA-1100 |  | C | M | 18:TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | CPP AGI | PS5-74-03 - Nitrogen Receiver |  | Originated |  | TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | 2026-09-03T14:36:28.963 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-017486 | PS5-74-VA-1100 |  | B | E | 18.1: EARTHING TO BE DONE | CPP AGI | PS5-74-03 - Nitrogen Receiver |  | Originated |  | EARTHING TO BE DONE | 2026-09-03T14:38:00.717 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-017487 | PS5-53-TR-4100 |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-53-01 - Utility Water / Storage Tank |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-09-03T14:49:00.403 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-017488 |  | EACOP-PS5-01-10-0445 | B | P | 18: UB02 Clamp support to be install 1 nos | CPP AGI | PS5-01-10 - Water Mist Package |  | Originated |  | UB02 Clamp support to be install | 2026-09-03T14:49:06.223 | Bhagavath, sangeeth | PS5 - Milestone E
PL-017528 | PS5-25-BI-2302-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-03T17:51:29.650 | Kumar, Senthil | PS5 - Milestone A
PL-017529 | PS5-25-BI-2302-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-03T17:52:49.390 | Kumar, Senthil | PS5 - Milestone A
PL-017530 | PS5-25-BI-2302-CC01 |  | B | I | No Cable’s Core Marker | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-03T17:54:40.483 | Kumar, Senthil | PS5 - Milestone A
PL-017531 | PS5-25-BI-2302-CC01 |  | B | I | No Proper MCT Packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Proper MCT Packing | 2026-09-03T17:55:47.430 | Kumar, Senthil | PS5 - Milestone A
PL-017532 | PS5-28-BI-1105-CC01 |  | C | I | No indoor cable tag (Yellow Black) | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-03T18:10:25.947 | Kumar, Senthil | PS5 - Milestone A
PL-017533 | PS5-28-BI-1105-CC01 |  | B | I | No Proper Screen Earth | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Provide Proper Screen Earth | 2026-09-03T18:12:15.493 | Kumar, Senthil | PS5 - Milestone A
PL-017534 | PS5-28-BI-1105-CC01 |  | B | I | No Proper MCT Packing | KENT | PS5-91-01 - Multicore cables & JB |  | Originated |  | To be Arrange Proper MCT Packing | 2026-09-03T18:13:26.880 | Kumar, Senthil | PS5 - Milestone A
PL-017554 | PS5-60-IE-0003B-CD06 |  | C | E | No Indoor Cable Tag (Yellow Black) | KENT | PS5-60-04 - Power Generation Package B |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-04T05:01:56.437 | Kumar, Senthil | PS5 - Milestone B
PL-017557 | PS5-60-IE-0003B-CD08 |  | C | E | No indoor cable tag (Yellow Black) | KENT | PS5-60-04 - Power Generation Package B |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-04T05:09:56.337 | Kumar, Senthil | PS5 - Milestone B
PL-017558 | PS5-60-IE-0003B-CD08 |  | B | E | No Cable’s Core Marker for Blue Core | KENT | PS5-60-04 - Power Generation Package B |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-04T05:11:37.033 | Kumar, Senthil | PS5 - Milestone B
PL-017560 | PS5-60-IE-0003B-CD12 |  | C | E | No indoor cable tag (Yellow Black) | KENT | PS5-60-04 - Power Generation Package B |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-04T05:57:09.630 | Kumar, Senthil | PS5 - Milestone B
PL-017561 | PS5-60-IE-0003B-CD12 |  | B | E | Earh core not connected | KENT | PS5-60-04 - Power Generation Package B |  | Originated |  | To be Connect the Earh core | 2026-09-04T05:58:50.903 | Kumar, Senthil | PS5 - Milestone B
PL-017563 | PS5-60-IE-0003C-CD08 |  | C | E | No indoor cable tag (Yellow Black) | KENT | PS5-60-07 - Power Generation Package C |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-04T06:07:32.653 | Kumar, Senthil | PS5 - Milestone D
PL-017574 | PS5-60-IE-0004-CD01 |  | B | E | Earth core not connected | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be connected the Earth core | 2026-09-04T06:25:40.000 | Kumar, Senthil | PS5 - Milestone B
PL-017578 | PS5-60-IE-0004-CD01 |  | C | E | No indoor cable tag (Yellow Black) | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-04T06:29:26.000 | Kumar, Senthil | PS5 - Milestone B
PL-017582 | PS5-60-IE-0004-CD02 |  | C | E | No indoor cable tag (Yellow Black) | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-04T06:43:03.050 | Kumar, Senthil | PS5 - Milestone B
PL-017583 | PS5-60-IE-0004-CD02 |  | B | E | Earth Core is not Connected | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be Connect the Earth Core | 2026-09-04T06:44:03.083 | Kumar, Senthil | PS5 - Milestone B
PL-017587 | PS5-60-IE-0004-CD14 |  | C | E | No indoor cable tag (Yellow Black) | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-04T08:30:31.720 | Kumar, Senthil | PS5 - Milestone B
PL-017588 | PS5-60-IE-0004-CD14 |  | B | E | No Cable’s Core Marker | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-04T08:31:11.553 | Kumar, Senthil | PS5 - Milestone B
PL-017591 | PS5-78-JC-9100D |  | B | E | 17:PUNCH LIST ID PL-001470,PL-001475,PL-004419,PL-004420,PL-004426 TO BE CLOSED | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | PUNCH LIST ID PL-001470,PL-001475,PL-004419,PL-004420,PL-004426 TO BE CLOSED | 2026-09-04T08:57:03.647 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-017592 | PS5-78-JC-9100D |  | C | M | 17.1: PUNCH LIST ID PL-001469,PL-004343 TO BE CLOSED | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | PUNCH LIST ID PL-001469,PL-004343 TO BE CLOSED | 2026-09-04T08:59:04.387 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-017600 | PS5-28-VDC-1100 |  | B | P | 18.2:Thermowells (Nozzle K1, K2) to be installed after GALT test | CPP AGI | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  | Thermowells (Nozzle K1, K2) to be installed after GALT test | 2026-09-04T10:18:16.693 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-017603 | PS5-25-SPZS-0002A |  | C | M | 16:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-09-04T10:30:33.147 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-017605 | PS5-25-SPZS-0002B |  | C | M | 16:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-09-04T10:35:03.487 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-017606 | PS5-25-SPZS-0002C |  | C | M | 16:Touch up / painting to be completed wherever required on the equipment | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Touch up / painting to be completed wherever required on the equipment | 2026-09-04T10:38:01.730 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-017630 | PS5-60-37_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-37 - Injector Tip Cooling Module C |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-09-04T11:18:38.630 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017636 | PS5-60-37_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-37 - Injector Tip Cooling Module C |  | Originated |  | Stenciling to be done | 2026-09-04T11:29:46.270 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017642 | PS5-60-38_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-38 - Injector Tip Cooling Module D |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-09-04T11:35:42.897 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017644 | PS5-60-38_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-38 - Injector Tip Cooling Module D |  | Originated |  | Stenciling to be done | 2026-09-04T11:36:21.043 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017652 | PS5-60-52_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-09-04T11:43:40.013 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017655 | PS5-60-52_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D |  | Originated |  | Stenciling to be done | 2026-09-04T11:44:30.480 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017664 | PS5-60-62_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-09-04T11:55:10.467 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017665 | PS5-60-62_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D |  | Originated |  | Stenciling to be done | 2026-09-04T11:56:03.833 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017668 | PS5-60-60_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-09-04T11:59:02.333 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017669 | PS5-60-60_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C |  | Originated |  | Stenciling to be done | 2026-09-04T11:59:43.877 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017680 | PS5-60-IE-0004-CD15 |  | C | E | No indoor cable tag (Yellow Black) | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  |  | 2026-09-04T12:24:05.703 | Kumar, Senthil | PS5 - Milestone B
PL-017682 | PS5-60-IE-0004-CD15 |  | B | E | No Cable’s Core Marker | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-04T12:24:38.560 | Kumar, Senthil | PS5 - Milestone B
PL-017684 | PS5-60-IE-0004-CD15 |  | B | E | Unused cores not properly protected (Including screen & Earth) | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be protect properly the Unused cores (Including screen & Earth) | 2026-09-04T12:25:37.983 | Kumar, Senthil | PS5 - Milestone B
PL-017685 | PS5-60-BE-0021A-CL01 |  | B | E | TERMINTION NOT COMPLET Chimney Aviation Lights JB PS5-60-BE-0021A | CPP AGI | PS5-60-22 - Power Gen Master UCP |  | Originated |  | TERMINTION NOT COMPLET Chimney Aviation Lights JB PS5-60-BE-0021A | 2026-09-04T12:26:45.287 | Gawad, Mohamed | PS5 - Milestone B
PL-017686 | PS5-60-IE-0004-CD15 |  | B | E | No Earthing for Gland's Earth tag | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be provide the Gland's Earth tag earthing | 2026-09-04T12:28:17.930 | Kumar, Senthil | PS5 - Milestone B
PL-017688 | PS5-60-IE-0004-CD15 |  | C | E | No outdoor Cable Tag | CPP AGI | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be provide out door Metal Cable tag | 2026-09-04T12:30:08.573 | Kumar, Senthil | PS5 - Milestone B
PL-017689 | PS5-60-BE-0021B-CL01 |  | B | E | TERMINTION NOT COMPLET Chimney Aviation Lights JB PS5-60-BE-0021B | CPP AGI | PS5-60-22 - Power Gen Master UCP |  | Originated |  | TERMINTION NOT COMPLET Chimney Aviation Lights JB PS5-60-BE-0021B | 2026-09-04T12:30:23.120 | Gawad, Mohamed | PS5 - Milestone B
PL-017693 | PS5-60-IE-0004-CD16 |  | C | E | No indoor cable tag (Yellow Black) | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be arrange Indoor Cable Tag (Yellow Black) | 2026-09-04T12:40:44.700 | Kumar, Senthil | PS5 - Milestone B
PL-017694 | PS5-60-IE-0004-CD16 |  | B | E | No Cable’s Core Marker | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be Arrange Cable’s Core Marker | 2026-09-04T12:41:25.677 | Kumar, Senthil | PS5 - Milestone B
PL-017695 | PS5-60-IE-0004-CD16 |  | B | E | No Earthing for Gland's Earth tag | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be provide the Gland's earth tag Earthing | 2026-09-04T12:42:06.050 | Kumar, Senthil | PS5 - Milestone B
PL-017696 | PS5-60-IE-0004-CD16 |  | B | E | Unused cores not properly protected (Including screen & Earth) | KENT | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be protect properly the Unused cores (Including screen & Earth) | 2026-09-04T12:43:54.687 | Kumar, Senthil | PS5 - Milestone B
PL-017697 | PS5-60-IE-0004-CD16 |  | C | E | No outdoor Metal cable tag | CPP AGI | PS5-60-22 - Power Gen Master UCP |  | Originated |  | To be provide outdoor Metal Cable tag | 2026-09-04T12:45:48.783 | Kumar, Senthil | PS5 - Milestone B
PL-017698 | PS5-60-BI-0001C-CC02 |  | B | I | TERMINTION NOT COMPLET 60-IE-0001C TB 24,31,15 | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | TERMINTION NOT COMPLET 60-IE-0001C TB 24,31,15 | 2026-09-04T12:48:28.457 | Gawad, Mohamed | PS5 - Milestone D
PL-017699 | PS5-60-BI-0010A-CC01 |  | B | I | TERMINAL BLOCK ISSUE / in complet DWG ISSUE | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | TERMINAL BLOCK ISSUE / in complet DWG ISSUE | 2026-09-04T12:55:40.980 | Gawad, Mohamed | PS5 - Milestone D
PL-017700 | PS5-09-QX-8451A |  | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-09-03 - HVAC for Generator Building |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-09-04T13:03:54.390 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017701 | PS5-60-IE-0002C-CC01 |  | B | I | 60-IE-0002C SIDE LDP SIDE NOT TERMINTED | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | 60-IE-0002C SIDE LDP SIDE NOT TERMINTED | 2026-09-04T13:04:55.330 | Gawad, Mohamed | PS5 - Milestone D
PL-017702 | PS5-09-QX-8451A |  | B | H | 16.1: HVAC ducting installation to be done | CPP AGI | PS5-09-03 - HVAC for Generator Building |  | Originated |  | HVAC ducting installation to be done | 2026-09-04T13:06:20.497 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017703 | PS5-60-IE-0002C-CC02 |  | B | I | TERMINTION NOT COMPLET 60-IE-0002C TB 1,2,3 | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | TERMINTION NOT COMPLET 60-IE-0002C TB 1,2,3 | 2026-09-04T13:06:50.800 | Gawad, Mohamed | PS5 - Milestone D
PL-017705 | PS5-09-QX-8451A |  | B | E | 16.2:Earthing to be done | CPP AGI | PS5-09-03 - HVAC for Generator Building |  | Originated |  | Earthing to be done | 2026-09-04T13:09:05.473 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017706 | PS5-09-QX-8451B |  | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-09-03 - HVAC for Generator Building |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-09-04T13:12:16.807 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017707 | PS5-09-QX-8451B |  | B | H | 16.1:HVAC ducting installation to be done | CPP AGI | PS5-09-03 - HVAC for Generator Building |  | Originated |  | HVAC ducting installation to be done | 2026-09-04T13:12:52.943 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017708 | PS5-60-IE-0003C-CC16 |  | B | I | TERMINATION WRONG DWG ISSUE | CPP AGI | PS5-60-08 - Power Gen Package C (UCP) |  | Originated |  | TERMINATION WRONG DWG ISSUE | 2026-09-04T13:13:14.710 | Gawad, Mohamed | PS5 - Milestone D
PL-017709 | PS5-09-QX-8451B |  | B | E | 16.2: Earthing to be done | CPP AGI | PS5-09-03 - HVAC for Generator Building |  | Originated |  | Earthing to be done | 2026-09-04T13:14:25.047 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-017710 | PS5-61-BI-0003-CC01 |  | B | I | TERMINATION WRONG DWG ISSUE | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | TERMINATION WRONG DWG ISSUE | 2026-09-04T13:18:54.967 | Gawad, Mohamed | PS5 - Milestone D
PL-017711 | PS5-71-IN-0001-CC06 |  | B | I | PS5 -60-IE-0004 TBX1501-5,6 Termination DWG ISSUE | CPP AGI | PS5-71-19 - Diesel Separator Module (UCP) |  | Originated |  | PS5 -60-IE-0004 TBX1501-5,6 Termination DWG ISSUE | 2026-09-04T13:33:56.967 | Gawad, Mohamed | PS5 - Milestone F
PL-017714 |  | EACOP-PS5-28-07-0373 | B | P | 18:Manhole cover to be installed and properly closed. | CPP AGI | PS5-28-07 - Open Drains (OD2) |  | Originated |  | Manhole cover to be installed and properly closed. | 2026-09-04T14:05:55.457 | Bhagavath, sangeeth | PS5 - Milestone G
PL-017719 |  | EACOP-PS5-28-07-0375 | B | P | 18:Manhole cover to be installed and properly closed. | CPP AGI | PS5-28-07 - Open Drains (OD2) |  | Originated |  | Manhole cover to be installed and properly closed. | 2026-09-04T14:30:44.340 | Bhagavath, sangeeth | PS5 - Milestone G
PL-017775 | PS5-60-44_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-09-05T07:47:20.590 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017776 | PS5-60-44_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C |  | Originated |  | Stenciling to be done | 2026-09-05T07:47:59.803 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017779 | PS5-60-45_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-09-05T07:53:09.757 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017780 | PS5-60-45_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D |  | Originated |  | Stenciling to be done | 2026-09-05T07:53:39.930 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017781 | PS5-60-51_SS_ALL_LINES |  | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | CPP AGI | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C |  | Originated |  | Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | 2026-09-05T07:57:43.743 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017782 | PS5-60-51_SS_ALL_LINES |  | C | P | 6.1:Stenciling to be done | CPP AGI | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C |  | Originated |  | Stenciling to be done | 2026-09-05T07:58:16.057 | Chinnathambi, Prasanth | PS5 - Milestone D
PL-017863 | PS5-50-SPZQ-0027 |  | B | P | 8:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-50-03 - Water Pre-Treatment Package |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-09-05T14:00:41.343 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-017864 | PS5-71-SPZQ-0026 |  | B | P | 8:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-16 - Diesel Fuel Supply Pump A/B |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-09-05T14:04:45.477 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-017865 | PS5-28-UO-8200 |  | B | P | 8:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-28-11 - Open Drain Interceptor |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-09-05T14:14:06.487 | THANGARATHINAM, ajikumar | PS5 - Milestone I