## Exported from SC
Punchlist ID | Asset (Name/Tag) | Asset Pack | Punchlist Category (Name) | Discipline (Name) | Description | Scheduling - Responsible Company (Name) | Systemization - Subsystem (Summary) | Workflow - Closing Date | Status | Comment | Action Required | Originated Date | Originated By | Priority
PL-000073 | PS5-60-UR-8100A |  | C | M | Gen-Set nameplate and equipment tagging not complete. | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2024-03-21T11:08:57.000 | Thao-my, Alexandre | PS5 - Milestone B
PL-000074 | PS5-60-UR-8100B |  | C | M | Gen-Set nameplate and equipment tagging not complete. | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2024-03-21T11:58:13.000 | Thao-my, Alexandre | PS5 - Milestone B
PL-000075 | PS5-60-UR-8100C |  | C | M | Gen-Set nameplate and equipment tagging not complete. | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  |  | 2024-03-21T12:01:18.000 | Thao-my, Alexandre | PS5 - Milestone D
PL-000076 | PS5-60-UR-8100D |  | C | M | Gen-Set nameplate and equipment tagging not complete. | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2024-03-21T12:02:50.000 | Thao-my, Alexandre | PS5 - Milestone D
PL-000077 | PS5-60-UR-8100E |  | C | M | Gen-Set nameplate and equipment tagging not complete. | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2024-03-21T12:04:20.000 | Thao-my, Alexandre | PS5 - Milestone D
PL-000078 | PS5-60-UR-8100F |  | C | M | Gen-Set nameplate and equipment tagging not complete. | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2024-03-21T12:07:26.000 | Thao-my, Alexandre | PS5 - Milestone D
PL-000079 | PS5-60-UR-8100G |  | C | M | Gen-Set nameplate and equipment tagging not complete. | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2024-03-21T12:08:59.000 | Thao-my, Alexandre | PS5 - Milestone E
PL-000170 | PS5-25-PA-3100A |  | C | M | CE mark not present on pump skid. | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Acquire CE marking on pump skid. New CE marked nameplate to supply and fit. | 2024-04-25T12:07:16.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000171 | PS5-25-PA-3100B |  | C | M | CE mark not present on pump skid. | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Acquire CE marking on pump skid. Carry Over Work confirmed as supplying and fitting new CE marked nameplate. | 2024-04-25T12:11:13.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000172 | PS5-25-PA-3100C |  | C | M | CE mark not present on pump skid. | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Acquire CE marking on pump skid. | 2024-04-25T12:12:40.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000173 | PS5-25-PA-3100A |  | A | M | Thermowells are to be replaced. | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Thermowells to be replaced on site. | 2024-04-25T12:18:16.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000174 | PS5-25-PA-3100B |  | A | M | Thermowells are to be replaced. | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Thermowells to be replaced on site. | 2024-04-25T12:19:34.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000175 | PS5-25-PA-3100C |  | A | M | Thermowells are to be replaced. | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Thermowells to be replaced on site. | 2024-04-25T12:20:30.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000176 | PS5-25-PA-3100A |  | B | M | PS5-25-LIT-3101A: Sunshade is damaged. | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Sunshade to be replaced. Sunshield has been removed for repair and is packed separately. Carry Over Work action is to confirm availability and condition of this sunshade. | 2024-04-25T12:22:28.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000177 | PS5-25-PA-3100C |  | B | M | Sunshade has chips and appears to be damaged - Local to PS5-25-BI-1274C. | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Replace or repair sun shade. Confirmed carry Over Work is to inspect during installation/commissioning and confirm availability and condition. | 2024-04-25T12:24:05.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000178 | PS5-25-PA-3100C |  | 0 | M | PS5-25-BE-0001C: Stopping plugs installed into side of MTB frame do not have legible Ex markings | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C | 2025-05-27T07:12:26.000 | Closed |  | Ensure stopping plugs installed can be verified for suitability at point of visual inspection as per IEC 60079-17. | 2024-04-25T12:24:59.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-000327 | PS5-60-UR-8100D |  | A | M | 2: DAMAGED AIR FILTERS. | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  | Replace the air inlet filters . | 2024-08-29T05:37:27.130 | khan, mojammil | PS5 - Milestone D
PL-000329 | PS5-60-UR-8100D |  | A | M | 4:OIL LEAKAGE FROM GENERATOR BEARING LUBRICATION PUMP TUBING. | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  | CHECK TUBING JOINTS AND TIGHT PROPERLY. | 2024-09-03T05:55:00.923 | khan, mojammil | PS5 - Milestone D
PL-000330 | PS5-60-UR-8100D |  | B | M | 4.1:CABLE PROTECTION IS DAMAGED | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  | FIX THE CABLE PROTECTION | 2024-09-03T06:04:57.720 | khan, mojammil | PS5 - Milestone D
PL-000331 | PS5-60-UR-8100D |  | A | M | 4.2:OIL LEAKAGE FROM DRAINING POINT | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  | TIGHT PROPERLY THE DRAINING POINT | 2024-09-03T06:05:33.963 | khan, mojammil | PS5 - Milestone D
PL-000332 | PS5-60-UR-8100D |  | A | M | 4.3: RUST IN SEVERAL AREAS OF GENSET AND PRESENCE OF PIN HOLES IN WELDING. | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  | CLEAN IT WITH SAND PAPER AND APPLY GREASE. | 2024-09-03T06:05:41.210 | khan, mojammil | PS5 - Milestone D
PL-000333 | PS5-60-UR-8100D |  | C | M | 4.4:PAINT DAMAGED FROM LIFTING POINTS | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  | TOUCH-UP PAINTING OF LIFTING POINTS. | 2024-09-03T06:10:52.070 | khan, mojammil | PS5 - Milestone D
PL-000334 | PS5-60-UR-8100C |  | A | M | 4:LEAKAGE FROM FUEL FILTER. | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | TIGHT PROPERLY . | 2024-09-03T08:01:52.957 | khan, mojammil | PS5 - Milestone D
PL-000335 | PS5-60-UR-8100C |  | C | M | 4.1:THE FUEL FILTER CONNECTING THREAD IS CORRODED | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | CHANGE THE CORRODED PART. | 2024-09-03T08:09:29.060 | khan, mojammil | PS5 - Milestone D
PL-000336 | PS5-60-UR-8100C |  | A | M | 4.2:THE BOTTOM HOLE ASSESORY IS DAMAGED | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | REPLACE THE PART | 2024-09-03T08:15:02.330 | khan, mojammil | PS5 - Milestone D
PL-000337 | PS5-60-UR-8100C |  | A | M | 4.3: TRANSMITTER ROD IS BEND AND OIL LEAKING | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | CLEAN THE OIL AND TIGHT PROPERLY FOR LEAKING . | 2024-09-03T08:19:23.150 | khan, mojammil | PS5 - Milestone D
PL-000338 | PS5-60-UR-8100C |  | A | M | 4.4:OIL LEAKAGE FROM DRAINING POINT | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | TIGHT PROPERLY | 2024-09-03T08:31:44.377 | khan, mojammil | PS5 - Milestone D
PL-000339 | PS5-60-UR-8100C |  | C | M | 4.5:GENERATOR PAINT IRREGULARITY. | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | TOUCH UP PAINTING REQUIRED | 2024-09-03T08:36:39.730 | khan, mojammil | PS5 - Milestone D
PL-000340 | PS5-60-UR-8100C |  | C | M | 4.6:BENDING OF THE HEAD CONNECTING PIPE IN ENGINE. | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | INSTALL PROPERLY. | 2024-09-03T08:41:24.890 | khan, mojammil | PS5 - Milestone D
PL-000341 | PS5-60-UR-8100C |  | C | M | 4.7: RUST IN MULTIPLE LOCATIONS | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | CLEAN IT WITH SAND PAPER AND APPLY GREASE. | 2024-09-03T08:44:33.457 | khan, mojammil | PS5 - Milestone D
PL-000342 | PS5-60-UR-8100C |  | C | M | 4.8:LIFTING POINT PAINT DAMAGE | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | TOUCH UP PAINTING REQUIRED. | 2024-09-03T08:52:28.897 | khan, mojammil | PS5 - Milestone D
PL-000343 | PS5-60-UR-8100B |  | A | M | 4:OIL LEAKAGE FROM SEVERAL PLACES OF GENERATOR.(TUBINGS,JOINTS) | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  | TIGHT PROPERLY THE JOINTS. | 2024-09-03T10:09:54.410 | khan, mojammil | PS5 - Milestone B
PL-000344 | PS5-60-UR-8100B |  | C | M | 4.1: RUST IN MULTIPLE AREAS | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  | CLEAN IT WITH SAND PAPER AND APPLY GREASE | 2024-09-03T10:17:18.007 | khan, mojammil | PS5 - Milestone B
PL-000345 | PS5-60-UR-8100B |  | C | M | 4.2:PAINT DAMAGED AT LIFTING POINT | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  | PAINT TOUCH UP REQUIRED | 2024-09-03T10:24:01.873 | khan, mojammil | PS5 - Milestone B
PL-000346 | PS5-60-UR-8100A |  | A | E | 4: A BUTTON ON GENERATOR CONTROL PANEL IS BROKEN | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  | REPLACE THE BUTTON IN CONTROL PANEL | 2024-09-03T10:35:16.897 | khan, mojammil | PS5 - Milestone B
PL-000347 | PS5-60-UR-8100A |  | C | M | 4.1:RUST IN COUPLING AND OTHER PLACES. | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  | CLEAN IT WITH SAND PAPER AND APPLY GREASE | 2024-09-03T10:43:20.693 | khan, mojammil | PS5 - Milestone B
PL-000348 | PS5-60-UR-8100A |  | A | M | 4.2:GENERATOR HAS MULTIPLE LEAKING POINTS.(JOINTS AND CONNECTIONS) | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  | TIGHT PROPERLY. | 2024-09-03T10:50:44.327 | khan, mojammil | PS5 - Milestone B
PL-000349 | PS5-60-UR-8100A |  | C | M | 4.3:LIFTING POINTS PAINT DAMAGED | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  | TOUCH UP PAINT REQUIRED | 2024-09-03T11:09:04.780 | khan, mojammil | PS5 - Milestone B
PL-000350 | PS5-60-UR-8100G |  | A | M | 4:LEAKAGE FROM MULTIPLE POINTS(JOINTS AND CONNECTIONS) | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  | TIGHT PROPERLY ALL THE LEAKING PARTS | 2024-09-03T11:20:14.057 | khan, mojammil | PS5 - Milestone E
PL-000351 | PS5-60-UR-8100G |  | C | M | 4.1:RUST IN MULTIPLE PLACES | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  | CLEAN IT WITH SAND PAPER AND APPLY GREASE | 2024-09-03T11:29:17.363 | khan, mojammil | PS5 - Milestone E
PL-000352 | PS5-60-UR-8100G |  | C | M | 4.2:LIFTING POINTS PAINT ARE DAMAGED | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  | TOUCH UP PAINT REQUIRED | 2024-09-03T11:33:31.003 | khan, mojammil | PS5 - Milestone E
PL-000353 | PS5-60-UR-8100A |  | A | E | 4.4: A jumper has been installed to short the CT at the alternator JB – Jumper to be removed once CTs will be connected and shorted at the CRO GCP via permanent cable. | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  | Jumper to be removed once permanent cable is connected. | 2024-09-03T13:19:51.893 | Thao-my, Alexandre | PS5 - Milestone B
PL-000354 | PS5-60-UR-8100A |  | A | E | 4.5: During preservation, VTs are disconnected in the cable terminal box to perform Insulation Resistance test. | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  | Any cable disconnected to be insulated and to be reconnected prior commissioning activities. | 2024-09-03T13:24:53.493 | Thao-my, Alexandre | PS5 - Milestone B
PL-000355 | PS5-60-UR-8100B |  | A | E | 4.3: A jumper has been installed to short the CT at the alternator JB – Jumper to be removed once CTs will be connected and shorted at the CRO GCP via permanent cable. | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  | Jumper to be removed once permanent cable is connected. | 2024-09-04T04:55:04.100 | Thao-my, Alexandre | PS5 - Milestone B
PL-000356 | PS5-60-UR-8100B |  | A | E | 4.4: During preservation, VTs are disconnected in the cable terminal box to perform Insulation Resistance test. | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  | Any cable disconnected to be insulated and to be reconnected prior commissioning activities. | 2024-09-04T04:56:48.277 | Thao-my, Alexandre | PS5 - Milestone B
PL-000357 | PS5-60-UR-8100C |  | A | E | 4.9: A jumper has been installed to short the CT at the alternator JB – Jumper to be removed once CTs will be connected and shorted at the CRO GCP via permanent cable. | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | Jumper to be removed once permanent cable is connected. | 2024-09-04T05:01:26.570 | Thao-my, Alexandre | PS5 - Milestone D
PL-000358 | PS5-60-UR-8100C |  | A | E | 4.10: During preservation, VTs are disconnected in the cable terminal box to perform Insulation Resistance test. | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | Any cable disconnected to be insulated and to be reconnected prior commissioning activities. | 2024-09-04T05:03:15.050 | Thao-my, Alexandre | PS5 - Milestone D
PL-000359 | PS5-60-UR-8100D |  | A | E | 4.5: A jumper has been installed to short the CT at the alternator JB – Jumper to be removed once CTs will be connected and shorted at the CRO GCP via permanent cable. | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  | Jumper to be removed once permanent cable is connected. | 2024-09-04T05:08:59.090 | Thao-my, Alexandre | PS5 - Milestone D
PL-000360 | PS5-60-UR-8100D |  | A | E | 4.6: During preservation, VTs are disconnected in the cable terminal box to perform Insulation Resistance test. | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  | Any cable disconnected to be insulated and to be reconnected prior commissioning activities. | 2024-09-04T05:10:13.133 | Thao-my, Alexandre | PS5 - Milestone D
PL-000361 | PS5-60-UR-8100G |  | A | E | 4.3: A jumper has been installed to short the CT at the alternator JB – Jumper to be removed once CTs will be connected and shorted at the CRO GCP via permanent cable. | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  | Jumper to be removed once permanent cable is connected. | 2024-09-04T05:12:29.257 | Thao-my, Alexandre | PS5 - Milestone E
PL-000362 | PS5-60-UR-8100G |  | A | E | 4.4: During preservation, VTs are disconnected in the cable terminal box to perform Insulation Resistance test. | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  | Any cable disconnected to be insulated and to be reconnected prior commissioning activities. | 2024-09-04T05:14:25.560 | Thao-my, Alexandre | PS5 - Milestone E
PL-000363 | PS5-25-VP-1100 |  | B | P | 2: Check for any damage during transportation. | EPS VENDOR | PS5-25-01 - Export Pipeline Pig Receiver | 2025-05-27T07:37:23.000 | Closed |  |  | 2024-09-04T07:51:58.000 | Zhang, Hui | PS5 - Milestone H
PL-000364 | PS5-25-VP-1100 |  | C | M | Some areas inside the pig receiver are rust | EPS VENDOR | PS5-25-01 - Export Pipeline Pig Receiver |  | Originated |  |  | 2024-09-04T07:51:58.000 | Zhang, Hui | PS5 - Milestone H
PL-000365 | PS5-25-VP-1200 |  | C | M | Some place in the pig lancher is rust | EPS VENDOR | PS5-25-07 - Export Pipeline Pig Launcher |  | Originated |  |  | 2024-09-04T07:51:59.000 | Zhang, Hui | PS5 - Milestone H
PL-000423 | PS5-60-UR-8100E |  | B | M | 4:EXHAUST FLANGE IS NOT PAINTED. | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | PAINT THE EXHAUST FLANGE | 2024-10-07T12:09:13.110 | khan, mojammil | PS5 - Milestone D
PL-000424 | PS5-60-UR-8100E |  | A | M | 4.1:AIR INLET FILTER IS DAMAGED | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2024-10-07T12:17:21.077 | khan, mojammil | PS5 - Milestone D
PL-000425 | PS5-60-UR-8100E |  | A | M | 4.2:THERE IS NO LUBE OIL INSIDE THE ALTERNATOR NON DRIVE END BEARING HOUSING. | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | FILL THE LUBE OIL. | 2024-10-07T12:23:06.547 | khan, mojammil | PS5 - Milestone D
PL-000426 | PS5-60-UR-8100E |  | B | M | 4.3:THE FILTER HAS NO OIL INSIDE IT. | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | FILL THE OIL INSIDE THE FILTER | 2024-10-07T12:27:25.597 | khan, mojammil | PS5 - Milestone D
PL-000427 | PS5-60-UR-8100E |  | C | M | 4.4:THERE IS RUST INSIDE THE DAMPER AND SEVERAL PARTS OF THE GENERATOR . | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | CLEAN IT WITH SAND PAPER AND APPLY GREASE | 2024-10-07T12:30:27.423 | khan, mojammil | PS5 - Milestone D
PL-000428 | PS5-60-UR-8100E |  | A | M | 4.5:OIL LEAKAGE FROM MULTIPLE LOCATIONS | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | TORQUE PROPERLY THEN CHECK AGAIN. | 2024-10-07T12:34:48.767 | khan, mojammil | PS5 - Milestone D
PL-000429 | PS5-60-UR-8100E |  | C | M | 4.6:PAINT DAMAGED FROM BODY OF THE GENERATOR | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | TOUCH UP PAINTING REQUIRED | 2024-10-07T12:39:01.547 | khan, mojammil | PS5 - Milestone D
PL-000430 | PS5-60-UR-8100E |  | C | M | 4.7:LIFTING POINT PAINT DAMAGED | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | TOUCH UP PAINTING REQUIRED | 2024-10-07T12:44:33.227 | khan, mojammil | PS5 - Milestone D
PL-000431 | PS5-60-UR-8100F |  | B | E | 4:Jacket water heater control box button is damaged | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  | REPLACE THE BUTTON | 2024-10-07T13:00:37.617 | khan, mojammil | PS5 - Milestone D
PL-000432 | PS5-60-UR-8100F |  | B | M | 4.1:unavailability of oil in the filter | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  | fill the oil. | 2024-10-07T13:03:08.310 | khan, mojammil | PS5 - Milestone D
PL-000433 | PS5-60-UR-8100F |  | A | M | 4.2:low oil level in the NDE end of alternator side glass. | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  | fill the lube oil. | 2024-10-07T13:10:53.597 | khan, mojammil | PS5 - Milestone D
PL-000434 | PS5-60-UR-8100F |  | C | M | 4.3:The head of the cam shaft cover plug bolt is damaged | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2024-10-07T13:15:45.470 | khan, mojammil | PS5 - Milestone D
PL-000435 | PS5-60-UR-8100F |  | C | M | 4.4:The generator has multiple rusts,Including damper | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  | CLEAN IT WITH SAND PAPER AND APPLY GREASE | 2024-10-07T13:18:59.607 | khan, mojammil | PS5 - Milestone D
PL-000436 | PS5-60-UR-8100F |  | A | M | 4.5:The generator has multiple leakages | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  | torque properly then check again. | 2024-10-07T13:23:08.790 | khan, mojammil | PS5 - Milestone D
PL-000437 | PS5-60-UR-8100F |  | C | M | 4.6:lifting points paint peeling; a little paint damage on the generator | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2024-10-07T13:26:43.333 | khan, mojammil | PS5 - Milestone D
PL-000467 | PS5-01-UK-6100 |  | C | M | 4:DOOR CANOPY IS DAMAGED | EPS VENDOR | PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100) |  | Originated |  | NEED TO FIX THE DOOR CANOPY | 2024-11-14T05:24:13.863 | khan, mojammil | PS5 - Milestone F
PL-000468 | PS5-01-UK-6100 |  | C | M | 4.1:THE KNOB OF THE EMERGENCY FIRE DOOR IS MISSING | EPS VENDOR | PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100) |  | Originated |  | NEED TO PROVIDE THE NEW KNOBS | 2024-11-14T05:28:46.823 | khan, mojammil | PS5 - Milestone F
PL-000469 | PS5-01-UK-6100 |  | C | M | 4.2: 4 DOOR KEYS ARE BEND | EPS VENDOR | PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100) |  | Originated |  | PROVIDE NEW KEYS | 2024-11-14T05:32:26.070 | khan, mojammil | PS5 - Milestone F
PL-000478 | PS5-25-MOV-0026 |  | B | I | Ensure that the mechanical stopper minimum flow through 25-MOV-0026 is higher than the export pump minimum flow. | EACOP | PS5-25-01 - Export Pipeline Pig Receiver |  | Originated |  | All Launcher/Receiver drawings modified accordingly. The minimum opening of the MOV-0026 to be confirmed during commissioning. | 2024-11-18T06:12:27.000 | Riima, Peter | PS5 - Milestone H
PL-000479 | PS5-25-MOV-0027 |  | B | I | Ensure that the mechanical stopper minimum flow through 25-MOV-0027 is higher than the export pump minimum flow. | EACOP | PS5-25-06 - Crude Oil Export Pumps Discharge |  | Originated |  | All Launcher/Receiver drawings modified accordingly. The minimum opening of the MOV-0027 to be confirmed during commissioning. | 2024-11-18T06:14:51.000 | Riima, Peter | PS5 - Milestone H
PL-000497 | PS5-05-UR-8100 |  | A | M | 4:THE TWO VIBRATION ISOLATORS, MEANT TO BE PLACED UNDER THE RADIATOR, HAVE BEEN MISTAKENLY INSTALLED BENEATH THE ENGINE. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T10:41:26.000 | Closed |  | NEED TO EXCHANGE THE VIBRATION ISOLATOR WITH THE RADIATOR ISOLATORS . | 2024-12-03T04:58:29.820 | khan, mojammil | PS5 - Milestone C
PL-000498 | PS5-05-UR-8100 |  | A | M | 4.1:LEVEL TRANSMITTER ON DIESEL TANK NOT INSTALLED. AND NOT FOUND ON LOCATION. REFERENCE PID TZ-MID-60-UTR2-130001_05. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T10:46:11.000 | Closed |  | INSTALL ONE TRANSMITTER | 2024-12-03T05:03:45.093 | khan, mojammil | PS5 - Milestone C
PL-000499 | PS5-05-UR-8100 |  | C | M | 4.2:CORROSION OBSERVED ON CASING OF THE TURBO CHARGER | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T10:47:47.000 | Closed |  |  | 2024-12-03T05:14:53.583 | khan, mojammil | PS5 - Milestone C
PL-000500 | PS5-05-UR-8100 |  | A | E | 4.3:THE EMERGENCY LIGHT IS SEVERELY DAMAGED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T10:48:31.000 | Closed |  |  | 2024-12-03T05:18:34.213 | khan, mojammil | PS5 - Milestone C
PL-000501 | PS5-05-UR-8100 |  | A | I | 4.4:THE FLAME DETECTOR IS NEITHER INSTALLED NOR SECURELY MOUNTED; INSTEAD, IT IS HANGING LOOSELY FROM THE CABLE TRAY IN DIESEL TANK ROOM. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2024-12-03T05:20:15.727 | khan, mojammil | PS5 - Milestone C
PL-000502 | PS5-05-UR-8100 |  | C | M | 4.5:AC FINS ARE PARTIALLY DAMAGED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T10:49:29.000 | Closed |  |  | 2024-12-03T05:22:46.257 | khan, mojammil | PS5 - Milestone C
PL-000503 | PS5-05-UR-8100 |  | C | M | 4.6:EXHAUST PIPE SEALANT IS DAMAGED. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:12:10.000 | Closed |  |  | 2024-12-03T05:24:34.790 | khan, mojammil | PS5 - Milestone C
PL-000504 | PS5-05-UR-8100 |  | C | M | 4.7:THE MONORAIL CRANE IS IMPROPERLY INSTALLED, WITH ITS WHEEL MISALIGNED AND OUT OF POSITION, CREATING A SIGNIFICANT RISK OF MALFUNCTION AND OPERATIONAL FAILURE | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2024-12-03T05:27:51.857 | khan, mojammil | PS5 - Milestone C
PL-000505 | PS5-05-UR-8100 |  | C | M | 4.8:AC UNIT PLASTIC PIPE IS DEFORMED AND DAMAGED DUE TO THE CLAMP BEING OVERLY TIGHTENED. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:14:25.000 | Closed |  |  | 2024-12-03T05:32:44.223 | khan, mojammil | PS5 - Milestone C
PL-000508 | PS5-05-UR-8100 |  | C | M | 4.9:CANOPY RUBBER PROTECTION IS MISSING. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:14:49.000 | Closed |  |  | 2024-12-03T05:35:26.223 | khan, mojammil | PS5 - Milestone C
PL-000512 | PS5-05-UR-8100 |  | A | E | 4.10:2 EXTERNAL LIGHTS FOR MAIN DOORS (BRACKET BEND, LIGHT PROTECTION FALLEN OFF) | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:15:17.000 | Closed |  |  | 2024-12-03T05:43:08.980 | khan, mojammil | PS5 - Milestone C
PL-000513 | PS5-05-UR-8100 |  | C | M | 4.11:ENGINE RADIATOR TO VENTILATION OUTLET CHAMBER NOT SEALED PROPERLY. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:15:42.000 | Closed |  |  | 2024-12-03T05:45:24.420 | khan, mojammil | PS5 - Milestone C
PL-000514 | PS5-05-UR-8100 |  | C | M | 4.12:VENT OUTLET CHAMBER TO DAY TANK PARTITION WALL IS NOT PROPERLY SEALED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:16:08.000 | Closed |  |  | 2024-12-03T05:49:01.763 | khan, mojammil | PS5 - Milestone C
PL-000515 | PS5-05-UR-8100 |  | C | M | 4.13:SUPPORT BEAM (FOR MONORAIL BEAM) FLANGE FACE IS HAVING GAPS | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:16:34.000 | Closed |  |  | 2024-12-03T05:51:39.770 | khan, mojammil | PS5 - Milestone C
PL-000516 | PS5-05-UR-8100 |  | B | E | 4.14:EARTHING CABLE JUMPERS BETWEEN ELECTRICAL CABLE TRAYS ARE NOT EXISTING ON MANY LOCATIONS | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2024-12-03T05:54:06.697 | khan, mojammil | PS5 - Milestone C
PL-000517 | PS5-05-UR-8100 |  | C | I | 4.15:INSTRUMENT CABLE RUNNING ON COOLING PIPE WITH TIE RODS | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2024-12-03T05:56:33.330 | khan, mojammil | PS5 - Milestone C
PL-000518 | PS5-05-UR-8100 |  | A | I | 4.16:INSTRUMENT CABLE TERMINATION TO RADIATOR IS NOT PROPERLY FIXED. (NO CABLE INSULATION ) | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2024-12-03T06:00:28.753 | khan, mojammil | PS5 - Milestone C
PL-000519 | PS5-05-UR-8100 |  | C | M | 4.17:THERE IS NO TAG NUMBER ON TROLLEY BEAM ,MANUAL TROLLEY & CHAIN BLOCKS | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2024-12-03T06:03:17.083 | khan, mojammil | PS5 - Milestone C
PL-000520 | PS5-05-UR-8100 |  | A | M | 4.18:SPARE NOZZLE N3 ON DIESEL TANK HAS NO RATED BLIND, NO GASKET AND BOLT SETS. REFERENCE PID TZ-MID-60-UTR2-130001_05. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2024-12-03T06:05:22.000 | khan, mojammil | PS5 - Milestone C
PL-000521 | PS5-05-UR-8100 |  | C | M | 4.19:NOZZLE 10 (FUEL FILLING WITH OVERFILL PREVENTION VALVE) FITTED WITH PTFE TAPE. REFERENCE PID TZ-MID-60-UTR2-130001_05. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2024-12-03T06:07:41.010 | khan, mojammil | PS5 - Milestone C
PL-000522 | PS5-05-UR-8100 |  | C | E | 4.20:LIGHTING JB DOES NOT HAVE TAG NUMBER JB DOES NOT HAVE MOISTURE ABSORBER (SUCH AS DESSICANT BAG- VPCI) | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2024-12-03T06:09:51.347 | khan, mojammil | PS5 - Milestone C
PL-000523 | PS5-05-UR-8100 |  | A | E | 4.21:THERE IS NO “AIR SHUT OFF BUTTON” THERE IS NO PROTECTION CAP ON CABLE TERMINATION POINT. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2024-12-03T06:10:43.300 | khan, mojammil | PS5 - Milestone C
PL-000524 | PS5-05-UR-8100 |  | A | E | 4.22:KEYS FOR JB IS MISSING | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:20:32.000 | Closed |  |  | 2024-12-03T06:15:11.313 | khan, mojammil | PS5 - Milestone C
PL-000525 | PS5-05-UR-8100 |  | C | M | 4.23:THE DOOR LOCK YIELDS ONLY WHEN TURNS AT AN ABSURD ANGLE. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:20:58.000 | Closed |  |  | 2024-12-03T06:19:33.567 | khan, mojammil | PS5 - Milestone C
PL-000526 | PS5-05-UR-8100 |  | B | M | 4.24:THE AIR INLET HOOD FRAME IS SEVERELY DAMAGED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:21:22.000 | Closed |  |  | 2024-12-03T06:27:31.287 | khan, mojammil | PS5 - Milestone C
PL-000527 | PS5-05-UR-8100 |  | C | M | 4.25:THE GASKET FOR THE INLET HOOD IS COMPLETELY TORN AND COMPROMISED. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:21:49.000 | Closed |  |  | 2024-12-03T06:29:34.140 | khan, mojammil | PS5 - Milestone C
PL-000528 | PS5-05-UR-8100 |  | C | M | 4.26:AIR OUTLET HOOD FRAME IS SLIGHTLY BEND. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:22:09.000 | Closed |  |  | 2024-12-03T06:31:13.550 | khan, mojammil | PS5 - Milestone C
PL-000529 | PS5-05-UR-8100 |  | A | M | 4.27:GLYCERINE LEAKAGE FROM THE HYDRAULIC CABIN PRESSURE GAUGE. THE GLYCERINE LEVEL INSIDE THE PG IS LOW. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:24:00.000 | Closed |  |  | 2024-12-03T06:35:41.520 | khan, mojammil | PS5 - Milestone C
PL-000530 | PS5-05-UR-8100 |  | C | M | 4.28:OIL IS FOUND SPILLED ON THE BASE PLATE OF THE HYDRAULIC CABIN | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:24:51.000 | Closed |  |  | 2024-12-03T06:37:14.433 | khan, mojammil | PS5 - Milestone C
PL-000531 | PS5-05-UR-8100 |  | C | M | 4.29:THE DAMPER COVER IN THE HYDRAULIC CABIN IS BEND. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:25:25.000 | Closed |  |  | 2024-12-03T06:39:52.053 | khan, mojammil | PS5 - Milestone C
PL-000532 | PS5-05-UR-8100 |  | C | M | 4.30:HANDRAIL PAINT DAMAGED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:26:11.000 | Closed |  |  | 2024-12-03T06:43:33.890 | khan, mojammil | PS5 - Milestone C
PL-000533 | PS5-05-UR-8100 |  | B | M | 4.3INSULATION ON MUFFLER FLANGE AREA ARE DAMAGED, NOT PROPERLY SEALED. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:26:33.000 | Closed |  |  | 2024-12-03T06:45:51.887 | khan, mojammil | PS5 - Milestone C
PL-000534 | PS5-05-UR-8100 |  | B | M | 4.32:INSULATION DONE ON MUFFLER HAS MANY OPENING TO EXPOSED AIR. (SUCH AS LIFTING LUG, SUPPORT, CLADDING TO CLADDING AREAS) | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:27:10.000 | Closed |  |  | 2024-12-03T06:56:45.877 | khan, mojammil | PS5 - Milestone C
PL-000535 | PS5-05-UR-8100 |  | C | M | 4.33:MUFFLER BOLTS AND NUTS ARE FULLY RUSTED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:27:37.000 | Closed |  |  | 2024-12-03T06:58:05.293 | khan, mojammil | PS5 - Milestone C
PL-000536 | PS5-05-UR-8100 |  | C | M | 4.34:MUFFLER INSULATED SURFACES & FLANGES FOUND NOT PAINTED.IT SHOULD BE BLACK AS PER TZ-MID-60-UTR2-180023_02_AFC SECTION 4.6. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:28:01.000 | Closed |  |  | 2024-12-03T07:00:35.500 | khan, mojammil | PS5 - Milestone C
PL-000537 | PS5-05-UR-8100 |  | C | M | 4.35:THE WELDING AND GRINDING ON THE MUFFLER EXHAUST PIPE ARE OF POOR QUALITY. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:28:48.000 | Closed |  |  | 2024-12-03T07:03:05.657 | khan, mojammil | PS5 - Milestone C
PL-000540 | PS5-05-UR-8100 |  | C | M | 4.36:THE PIPE IN THE MUFFLER BOX , IS SHOWING SIGNS OF RUST AND IS UNPAINTED. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:29:16.000 | Closed |  |  | 2024-12-03T07:05:27.667 | khan, mojammil | PS5 - Milestone C
PL-000541 | PS5-05-UR-8100 |  | A | M | 4.37:WATER MIST CABINET N2 CYLINDERS DELIVERED WITH PRESSURE. (WE DONT KNOW WHAT TYPE OF GAS INSIDE) | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:30:23.000 | Closed |  |  | 2024-12-03T07:08:29.220 | khan, mojammil | PS5 - Milestone C
PL-000542 | PS5-05-UR-8100 |  | A | M | 4.38:WATER MIST CABINET PTFE TAPE USED FOR THREADED JOINTS. (CYLINDER – VALVE CONNECTIONS) | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:32:21.000 | Closed |  |  | 2024-12-03T07:10:35.490 | khan, mojammil | PS5 - Milestone C
PL-000546 | PS5-05-UR-8100 |  | A | M | 4.39:THE KEY SEEMS TO BE MALFUNCTIONING AND ISN'T OPENING THE DOOR | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:33:04.000 | Closed |  |  | 2024-12-03T07:13:35.710 | khan, mojammil | PS5 - Milestone C
PL-000547 | PS5-05-UR-8100 |  | C | M | 4.40:WATER MIST CABINET PAINTED IN WHITE. IT SHOULD BE RED AS PER TZ-MID-60-WPR2-120001 (SECTION 6.2, PAGE 11/39) | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:34:31.000 | Closed |  | No action required since as per latest project documendation | 2024-12-03T07:15:46.240 | khan, mojammil | PS5 - Milestone C
PL-000548 | PS5-05-UR-8100 |  | C | M | 4.41:THERE IS A CRACK IN THE WELD OF THE MIST CABIN | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:35:19.000 | Closed |  |  | 2024-12-03T07:21:55.260 | khan, mojammil | PS5 - Milestone C
PL-000549 | PS5-05-UR-8100 |  | C | M | 4.42:MIST CABIN AND MUFFLER PAINT DAMAGED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:35:51.000 | Closed |  |  | 2024-12-03T07:23:55.040 | khan, mojammil | PS5 - Milestone C
PL-000550 | PS5-05-UR-8100 |  | C | M | 4.43:SPARE INSULATION , CLADDING (TO INSULATE AND CLAD MUFFLER RELATED JOINTS), ATTACHMENT BOLT SET, NOT RECEIVED, AND DETAILED PACKING LIST IS NOT AVAILABLE. | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2024-12-03T07:31:34.630 | khan, mojammil | PS5 - Milestone C
PL-000564 | PS5-61-IDH-3100A |  | A | E | Revision to Sulzer/NIDEC wiring for VSD for the General Alarm and General Trips. | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A | 2025-06-24T01:31:43.000 | Closed |  |  | 2024-12-16T06:05:26.997 | Thao-my, Alexandre | PS5 - Milestone H
PL-000565 | PS5-61-IDH-3100B |  | A | E | Revision to Sulzer/NIDEC wiring for VSD for the General Alarm and General Trips. | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B | 2025-06-24T01:32:58.000 | Closed |  |  | 2024-12-16T06:05:26.997 | Thao-my, Alexandre | PS5 - Milestone H
PL-000566 | PS5-61-IDH-3100C |  | A | E | Revision to Sulzer/NIDEC wiring for VSD for the General Alarm and General Trips. | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C | 2025-06-24T01:33:40.000 | Closed |  |  | 2024-12-16T06:05:26.997 | Thao-my, Alexandre | PS5 - Milestone H
PL-000612 | PS5-05-UR-8100 |  | A | M | Swapping of Radiator isolator/Engine isolator | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:42:31.000 | Closed |  | Unatrac shall do the reparation before commissioning | 2025-01-07T07:07:49.000 | Benyahia, Zied | PS5 - Milestone C
PL-000621 | PS5-60-UR-8100E |  | A | E | Potential transformer connection inside the alternator box | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | the cables shll be connected before commissioning | 2025-01-08T07:17:02.000 | Benyahia, Zied | PS5 - Milestone D
PL-000622 | PS5-60-UR-8100E |  | A | E | CTs at the alternator Juncon Box Jumpered (2CT1/2CT2) | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | Jumper will be removed during the installation of the respective interconnecting cables. | 2025-01-08T07:21:03.000 | Benyahia, Zied | PS5 - Milestone D
PL-000623 | PS5-60-UR-8100F |  | A | E | Potential transformer connections inside the | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  | the cables shall be connected before commissioning | 2025-01-08T07:28:51.000 | Benyahia, Zied | PS5 - Milestone D
PL-000624 | PS5-60-UR-8100F |  | A | E | CTs at the alternator Juncon Box are Jumpered (2CT1/2CT2) | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  | Jumper will be removed during the installation of the respective interconnecting cables | 2025-01-08T10:23:35.000 | Benyahia, Zied | PS5 - Milestone D
PL-000702 | PS5-61-IU-3100A |  | C | M | 4:Found radiator bottom and top angle bar support bolt & nuts need to be tighted properly. | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | need to tight properly | 2025-02-14T06:37:09.690 | khan, mojammil | PS5 - Milestone H
PL-000703 | PS5-61-IU-3100A |  | C | M | 4.1:Found all transformer radiator support paint need to be provided | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-02-14T06:42:56.640 | khan, mojammil | PS5 - Milestone H
PL-000704 | PS5-61-IU-3100B |  | C | M | 4:Found radiator bottom area unpainted steel angle bar support need to be painted | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-02-14T06:48:12.390 | khan, mojammil | PS5 - Milestone H
PL-000705 | PS5-61-IU-3100B |  | C | M | 4.1:Found all transformer radiator support paint need to be provided | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-02-14T06:50:24.463 | khan, mojammil | PS5 - Milestone H
PL-000706 | PS5-61-IU-3100C |  | C | M | 4:Found radiator bottom and top angle bar support bolt & nuts need to be tighted properly. | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-02-14T06:53:08.087 | khan, mojammil | PS5 - Milestone H
PL-000707 | PS5-61-IU-3100C |  | C | M | 4.1:Found all transformer radiator support paint need to be provided | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-02-14T06:54:32.710 | khan, mojammil | PS5 - Milestone H
PL-000711 | PS5-71-PA-3100A |  | A | M | 4:CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | CPP AGI | PS5-71-16 - Diesel Fuel Supply Pump A/B |  | Originated |  |  | 2025-02-17T06:20:18.973 | khan, mojammil | PS5 - Milestone F
PL-000712 | PS5-71-PA-3100B |  | A | M | 4:CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | CPP AGI | PS5-71-16 - Diesel Fuel Supply Pump A/B |  | Originated |  |  | 2025-02-17T06:23:09.200 | khan, mojammil | PS5 - Milestone F
PL-000713 | PS5-71-PA-3200 |  | A | M | 4:CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | CPP AGI | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-17T06:28:05.110 | khan, mojammil | PS5 - Milestone F
PL-000720 | PS5-60-UA-5100 |  | C | M | 4:THE WOODEN CRATE IS COMPLETELY SHATTERED. | EPS UNATRAC | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  |  | 2025-02-17T12:20:22.593 | khan, mojammil | PS5 - Milestone B
PL-000721 | PS5-60-UA-5100 |  | B | M | 4.1:THE PRESSURE GAUGE IS SLIGHTLY BENT DUE TO THE IMPACT FROM THE BROKEN WOODEN CRATE. | EPS UNATRAC | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  |  | 2025-02-17T12:32:46.813 | khan, mojammil | PS5 - Milestone B
PL-000722 | PS5-60-UA-5100 |  | C | M | 4.2:SOME OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  |  | 2025-02-17T12:34:41.193 | khan, mojammil | PS5 - Milestone B
PL-000723 | PS5-60-UA-5100 |  | A | M | 4.3:THE HEAT EXCHANGER PIPE IS BROKEN FROM THE COMPRESSOR HEAD. | EPS UNATRAC | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  |  | 2025-02-17T12:36:18.733 | khan, mojammil | PS5 - Milestone B
PL-000724 | PS5-60-UA-5100 |  | B | M | 4.4:NO PROPER PACKING LIST PROVIDED FOR COMMISSIONING SPARES | EPS UNATRAC | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  |  | 2025-02-17T12:37:28.093 | khan, mojammil | PS5 - Milestone B
PL-000725 | PS5-60-UA-5100 |  | C | M | 4.5:TRACES OF COOLANT FOUND ON THE TOP OF THE COOLANT TANK | EPS UNATRAC | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  |  | 2025-02-17T12:38:50.090 | khan, mojammil | PS5 - Milestone B
PL-000726 | PS5-60-UA-5100 |  | C | M | 4.6:SOME PARTS ARE COMPLETELY RUSTED | EPS UNATRAC | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  |  | 2025-02-17T12:40:08.083 | khan, mojammil | PS5 - Milestone B
PL-000727 | PS5-60-UO-81100A |  | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A |  | Originated |  |  | 2025-02-17T13:42:54.767 | khan, mojammil | PS5 - Milestone B
PL-000728 | PS5-60-UO-81100B |  | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B |  | Originated |  |  | 2025-02-17T13:46:54.337 | khan, mojammil | PS5 - Milestone B
PL-000729 | PS5-60-UO-81100C |  | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C |  | Originated |  |  | 2025-02-17T13:50:18.140 | khan, mojammil | PS5 - Milestone D
PL-000730 | PS5-60-UO-81100D |  | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D |  | Originated |  |  | 2025-02-17T13:52:20.320 | khan, mojammil | PS5 - Milestone D
PL-000731 | PS5-60-UO-81100E |  | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-60-53 - Lube Oil Separator Module PS5-60-UO-81100E |  | Originated |  |  | 2025-02-17T13:54:24.543 | khan, mojammil | PS5 - Milestone D
PL-000732 | PS5-60-UO-81100F |  | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-60-54 - Lube Oil Separator Module PS5-60-UO-81100F |  | Originated |  |  | 2025-02-17T13:56:15.013 | khan, mojammil | PS5 - Milestone D
PL-000733 | PS5-60-UO-81100G |  | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-60-55 - Lube Oil Separator Module PS5-60-UO-81100G |  | Originated |  |  | 2025-02-17T13:58:01.927 | khan, mojammil | PS5 - Milestone E
PL-000734 | PS5-60-UZ-8200A |  | C | M | 4:THE PAINT ON THE INJECTOR TIP COOLING MODULE FLANGE IS CRACKED | EPS UNATRAC | PS5-60-35 - Injector Tip Cooling Module A |  | Originated |  |  | 2025-02-18T07:18:51.850 | khan, mojammil | PS5 - Milestone B
PL-000735 | PS5-60-UZ-8200A |  | C | M | 4.1:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | EPS UNATRAC | PS5-60-35 - Injector Tip Cooling Module A |  | Originated |  |  | 2025-02-18T07:21:14.343 | khan, mojammil | PS5 - Milestone B
PL-000736 | PS5-60-UZ-8200B |  | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | EPS UNATRAC | PS5-60-36 - Injector Tip Cooling Module B |  | Originated |  |  | 2025-02-18T07:24:26.520 | khan, mojammil | PS5 - Milestone B
PL-000737 | PS5-60-UZ-8200C |  | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | EPS UNATRAC | PS5-60-37 - Injector Tip Cooling Module C |  | Originated |  |  | 2025-02-18T07:45:32.113 | khan, mojammil | PS5 - Milestone D
PL-000738 | PS5-60-UZ-8200D |  | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | EPS UNATRAC | PS5-60-38 - Injector Tip Cooling Module D |  | Originated |  |  | 2025-02-18T07:47:51.383 | khan, mojammil | PS5 - Milestone D
PL-000739 | PS5-60-UZ-8200E |  | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | EPS UNATRAC | PS5-60-39 - Injector Tip Cooling Module E |  | Originated |  |  | 2025-02-18T07:51:00.700 | khan, mojammil | PS5 - Milestone D
PL-000740 | PS5-60-UZ-8200F |  | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | EPS UNATRAC | PS5-60-40 - Injector Tip Cooling Module F |  | Originated |  |  | 2025-02-18T07:53:08.670 | khan, mojammil | PS5 - Milestone D
PL-000741 | PS5-60-VS-9100A |  | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | EPS UNATRAC | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A |  | Originated |  |  | 2025-02-18T08:06:35.387 | khan, mojammil | PS5 - Milestone B
PL-000742 | PS5-60-VS-9100B |  | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | EPS UNATRAC | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B |  | Originated |  |  | 2025-02-18T08:09:43.510 | khan, mojammil | PS5 - Milestone B
PL-000743 | PS5-60-VS-9100B |  | B | M | 4.1:WATER INGRESS HAS BEEN DETECTED INSIDE THE MIST ELIMINATOR AND THE MOTOR | EPS UNATRAC | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B |  | Originated |  |  | 2025-02-18T08:11:54.570 | khan, mojammil | PS5 - Milestone B
PL-000744 | PS5-60-VS-9100C |  | B | M | 4:WATER INGRESS HAS BEEN DETECTED INSIDE THE MIST ELIMINATOR AND THE MOTORS. | EPS UNATRAC | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C |  | Originated |  |  | 2025-02-18T08:15:07.650 | khan, mojammil | PS5 - Milestone D
PL-000745 | PS5-60-VS-9100C |  | B | M | 4.1:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | EPS UNATRAC | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C |  | Originated |  |  | 2025-02-18T08:18:23.187 | khan, mojammil | PS5 - Milestone D
PL-000746 | PS5-60-VS-9100D |  | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | EPS UNATRAC | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D |  | Originated |  |  | 2025-02-18T08:22:04.193 | khan, mojammil | PS5 - Milestone D
PL-000747 | PS5-60-VS-9100E |  | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | EPS UNATRAC | PS5-60-46 - Oil Mist Separator Skid PS5-60-VS-9100E |  | Originated |  |  | 2025-02-18T08:24:41.093 | khan, mojammil | PS5 - Milestone D
PL-000748 | PS5-60-VS-9100F |  | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | EPS UNATRAC | PS5-60-47 - Oil Mist Separator Skid PS5-60-VS-9100F |  | Originated |  |  | 2025-02-18T08:27:15.503 | khan, mojammil | PS5 - Milestone D
PL-000749 | PS5-60-VS-9100G |  | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | EPS UNATRAC | PS5-60-48 - Oil Mist Separator Skid PS5-60-VS-9100G |  | Originated |  |  | 2025-02-18T08:29:31.590 | khan, mojammil | PS5 - Milestone E
PL-000750 | PS5-71-UZ-6500 |  | A | E | 4:THE JB DOOR OF THE DO SEPARATOR IS NOT FIXED, AND THE BOLTS ARE MISSING. | EPS UNATRAC | PS5-71-18 - Diesel Separator Module |  | Originated |  |  | 2025-02-18T08:38:17.447 | khan, mojammil | PS5 - Milestone F
PL-000751 | PS5-71-UZ-6800A |  | C | M | 4:SOME OPENINGS ARE IMPROPERLY PLUGGED | EPS UNATRAC | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  |  | 2025-02-18T08:49:40.807 | khan, mojammil | PS5 - Milestone H
PL-000752 | PS5-71-UZ-6800A |  | A | M | 4.1:THE PSV AND FIT WERE IMPROPERLY SECURED, AND WE DISCOVERED THE PSV CARELESSLY DISPLACED, LYING UPSIDE DOWN ON THE GROUND.(NEED TO BE INSTALLED) | EPS UNATRAC | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  |  | 2025-02-18T08:51:42.630 | khan, mojammil | PS5 - Milestone H
PL-000753 | PS5-71-UZ-6800A |  | A | M | 4.2:THE FCV IS NOT CONNECTED ON A SINGLE SIDE. | EPS UNATRAC | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  |  | 2025-02-18T08:55:07.910 | khan, mojammil | PS5 - Milestone H
PL-000754 | PS5-71-UZ-6800A |  | A | E | 4.3:Control panel key is missing. | EPS UNATRAC | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  |  | 2025-02-18T08:57:25.680 | khan, mojammil | PS5 - Milestone H
PL-000755 | PS5-71-UZ-6800B |  | A | E | 4:CONTROL PANEL KEY IS MISSING | EPS UNATRAC | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  |  | 2025-02-18T10:48:36.073 | khan, mojammil | PS5 - Milestone H
PL-000756 | PS5-71-UZ-6800B |  | B | M | 4.1:NO LUBE OIL AVAILABLE AT THE VIEWING GLASS. | EPS UNATRAC | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  |  | 2025-02-18T10:53:05.193 | khan, mojammil | PS5 - Milestone H
PL-000757 | PS5-71-UZ-6800B |  | C | M | 4.2:A LOT OF OPENINGS ARE NOT PROPERLY PLUGGED | EPS UNATRAC | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  |  | 2025-02-18T10:54:31.563 | khan, mojammil | PS5 - Milestone H
PL-000758 | PS5-71-UZ-6800B |  | A | M | 4.3:THE PSV, FLOW GAUGE, AND SPOOLS ARE NOT INSTALLED AND LYING ON THE GROUND. (NEED TO BE INSTALLED) | EPS UNATRAC | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  |  | 2025-02-18T10:55:58.000 | khan, mojammil | PS5 - Milestone H
PL-000759 | PS5-60-UZ-8200G |  | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED. | EPS UNATRAC | PS5-60-41 - Injector Tip Cooling Module G |  | Originated |  |  | 2025-02-18T11:09:48.873 | khan, mojammil | PS5 - Milestone E
PL-000760 | PS5-28-VDC-1100 |  | A | M | 4:THE INSULATION RING FOR THE CLOSED DRAIN DRUM IS DAMAGED. | EPS VENDOR | PS5-28-03 - Closed Drain Drum and Pump 01 | 2025-05-27T07:22:04.000 | Closed |  |  | 2025-02-18T11:15:39.000 | khan, mojammil | PS5 - Milestone G
PL-000761 | PS5-28-VDC-1100 |  | C | M | 4.1:THE CLOSED DRAIN DRUM EXHIBITS PAINT DAMAGE. | EPS VENDOR | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  |  | 2025-02-18T11:27:39.877 | khan, mojammil | PS5 - Milestone G
PL-000762 | PS5-28-VDC-1100 |  | B | M | 4.2:NO PACKING NOTE AVAILABLE FOR COMM. & STARTUP SPARES . FOUND- 4INCH 150 ASME GASKET(QUANTITY-1), REGULATOR KNOB, 1 BOLT, 10 STUD BOLT & 20 HEX NUT, 4INCH 150 ASME GASKET(QUANTITY -6) 2 MANUAL. | EPS VENDOR | PS5-28-03 - Closed Drain Drum and Pump 01 |  | Originated |  |  | 2025-02-18T11:30:24.337 | khan, mojammil | PS5 - Milestone G
PL-000763 | PS5-71-UZ-6200 |  | C | M | 4:THE CONTAINER IS DAMAGED | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:27:13.087 | khan, mojammil | PS5 - Milestone F
PL-000764 | PS5-71-UZ-6200 |  | C | M | 4.1:THE CONTAINER HAS SIGNIFICANT PAINT DAMAGE. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:32:07.203 | khan, mojammil | PS5 - Milestone F
PL-000765 | PS5-71-UZ-6200 |  | A | E | 4.2:THE TUBE LIGHT FELL FROM ITS ORIGINAL POSITION AND GOT DAMAGED | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:33:14.560 | khan, mojammil | PS5 - Milestone F
PL-000766 | PS5-71-UZ-6200 |  | C | M | 4.3:THE SPOOL FROM THE DISPENSER HAS PAINT DAMAGE. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:35:41.190 | khan, mojammil | PS5 - Milestone F
PL-000767 | PS5-71-UZ-6200 |  | A | M | 4.4:THE METALLIC FLEXIBLE CONNECTION IS BROKEN AND DAMAGED. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:36:53.570 | khan, mojammil | PS5 - Milestone F
PL-000768 | PS5-71-UZ-6200 |  | C | M | 4.5:THE DISPENSER COVERS ARE NOT PROPERLY MOUNTED AND HAVE FALLEN TO THE GROUND. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:38:22.530 | khan, mojammil | PS5 - Milestone F
PL-000769 | PS5-71-UZ-6200 |  | B | M | 4.6:THE GASKET FOR THE SIDE VIEWING GLASS IS DAMAGED. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:41:07.920 | khan, mojammil | PS5 - Milestone F
PL-000770 | PS5-71-UZ-6200 |  | C | M | 4.7:THE NUT & BOLT FOR THE SIDE VIEWING GLASS IS MISSING. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:43:35.527 | khan, mojammil | PS5 - Milestone F
PL-000771 | PS5-71-UZ-6200 |  | C | M | 4.8:THE ROLLING WIRE IS COMPRESSED BENEATH THE STRUCTURE. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:46:10.960 | khan, mojammil | PS5 - Milestone F
PL-000772 | PS5-71-UZ-6200 |  | C | M | 4.9:THE FLOW INDICATOR TRANSMITTER IS NOT MOUNTED OR BOLTED SECURELY. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:47:26.793 | khan, mojammil | PS5 - Milestone F
PL-000773 | PS5-71-UZ-6200 |  | B | M | 4.10:OPENED THE ROOF HATCH, BUT THE KEY IS STILL NOT WORKING; LOCK & KEY NEEDS TO BE REPLACED | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:48:39.033 | khan, mojammil | PS5 - Milestone F
PL-000774 | PS5-71-UZ-6200 |  | C | M | 4.11:THE INLET SPOOL FOR THE VESSEL IS NOT MOUNTED PROPERLY. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:50:22.877 | khan, mojammil | PS5 - Milestone F
PL-000775 | PS5-71-UZ-6200 |  | B | E | 4.12:THE CABLE LAID IN THE WALKWAY NEEDS TO BE REMOVED AND PROPERLY ORGANIZED IN THE CABLE TRAY/CHANNEL. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:53:29.367 | khan, mojammil | PS5 - Milestone F
PL-000776 | PS5-71-UZ-6200 |  | A | E | 4.13:THE CABLE NEEDS TO BE PROTECTED FROM SHARP EDGES. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:55:25.610 | khan, mojammil | PS5 - Milestone F
PL-000777 | PS5-71-UZ-6200 |  | C | M | 4.14:THE CHANNEL SHOULD BE FIXED SECURELY ON BOTH ENDS WITH SCREWS, AND A WIRE TAG SHOULD BE PROVIDED | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:56:38.763 | khan, mojammil | PS5 - Milestone F
PL-000778 | PS5-71-UZ-6200 |  | C | E | 4.15:ALL THE PAPER TAG SHOULD BE REPLACED WITH A STAINLESS STEEL (SS) TAG | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:58:16.937 | khan, mojammil | PS5 - Milestone F
PL-000779 | PS5-71-UZ-6200 |  | C | E | 4.16:ALL INSTRUMENT HANGING TAG (SS TAG) SHOULD BE PROVIDED. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T10:59:32.210 | khan, mojammil | PS5 - Milestone F
PL-000780 | PS5-71-UZ-6200 |  | C | M | 4.17:THE DISPENSER IS NOT SECURELY FIXED AND IS SHAKING. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T11:01:08.537 | khan, mojammil | PS5 - Milestone F
PL-000781 | PS5-71-UZ-6200 |  | B | M | 4.18:OPENED THE TECHNICAL ROOM DOOR; THE DOOR LOCK WAS JAMMED AND NOW IS WORKING, BUT NOT SMOOTHLY. THE LOCK COVER IS DAMAGED AND NEED TO BE REPLACED, AND THE DOOR FRAME IS NOT FIXED PROPERLY, RESULTING IN HEAVY SHAKING. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T11:02:33.907 | khan, mojammil | PS5 - Milestone F
PL-000782 | PS5-71-UZ-6200 |  | A | E | 4.19:THE TUBE LIGHT HAS FALLEN FROM ITS ORIGINAL POSITION AND IS HANGING IN THE TECHNICAL ROOM. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T11:04:15.070 | khan, mojammil | PS5 - Milestone F
PL-000783 | PS5-71-UZ-6200 |  | C | M | 4.20:TWO NUT BOLTS ARE MISSING FROM THE M LADDER SUPPORT. | EPS VENDOR | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  |  | 2025-02-19T11:05:30.007 | khan, mojammil | PS5 - Milestone F
PL-000812 | PS5-60-UR-8100A |  | C | M | 4:THERE IS A SLIGHT BEND ON THE BODY OF THE ADAPTOR(ADAPTOR Ø650 to Øout 508 L1280 - inlet engine ) | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T05:25:22.300 | khan, mojammil | PS5 - Milestone B
PL-000813 | PS5-60-UR-8100A |  | C | M | 4.1:TWO OF THE STRAIGHT LENGTHS ARE BENT IN THREE PLACES(ADJUSTABLE STRAIGHT LENGTH L2850- 3000mm Ø650) | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T05:29:17.157 | khan, mojammil | PS5 - Milestone B
PL-000814 | PS5-60-UR-8100A |  | C | M | 4.2:FOUND MINOR SCRATCHES, GAPS ON THE OUTER COVER THAT COULD ALLOW WATER ENTRY INTO THE INSULATED AREA ,Gaps not properly filled/sealed, Partially used mastic to seal which have not working(STRAIGHT LENGTH L10000mm DIA 950/1150 EXHAUST LINE) | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T05:47:51.933 | khan, mojammil | PS5 - Milestone B
PL-000815 | PS5-60-UR-8100A |  | B | M | 4.3:A SMALL CUT WAS FOUND ON THE OUTER COVER OF THE STRAIGHT LENGTH L10000mm DIA 950/1150 EXHAUST LINE | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T05:52:30.180 | khan, mojammil | PS5 - Milestone B
PL-000816 | PS5-60-UR-8100A |  | C | M | 4.4:FOUND MINOR SCRATCHES, GAPS ON THE OUTER COVER THAT COULD ALLOW WATER ENTRY INTO THE INSULATED AREA , AND SMALL CUTS .(Gaps not properly filled/sealed, Partially used mastic to seal which have not working)this is general comment for SRN 302 | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T06:07:30.993 | khan, mojammil | PS5 - Milestone B
PL-000817 | PS5-60-UR-8100A |  | C | M | 4.6:FOUND MINOR SCRATCHES, GAPS ON THE OUTER COVER THAT COULD ALLOW WATER ENTRY INTO THE INSULATED AREA , AND SMALL CUTS .(Gaps not properly filled/sealed, Partially used mastic to seal which have not working)-STRAIGHT LENGTH L1250mm DIA 450/650 EXHAUST LINE | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T06:15:35.330 | khan, mojammil | PS5 - Milestone B
PL-000818 | PS5-60-UR-8100A |  | C | M | 4.7:FOUND MINOR SCRATCHES, GAPS ON THE OUTER COVER THAT COULD ALLOW WATER ENTRY INTO THE INSULATED AREA .(Gaps not properly filled/sealed, Partially used mastic to seal which have not working)-ADJUSTABLE LENGTH L6000-6250mm DIA 950/1150 EXHAUST LINE | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T06:21:06.760 | khan, mojammil | PS5 - Milestone B
PL-000819 | PS5-60-UR-8100A |  | B | M | 4.8:NO PROPER PACKING LIST/NOTE AVAILABLE FOR SRN 303 FASTNERS. FOUND BOLT- M12*60=3500, M16*80=450, M30*80=670, M36*80=690, M36*90=60 NUT- M36=750, M12=3500, M16=450 ,, M30=30 WASHER- M36=1500, M13=7000 ,M16=900, M31=700 | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T06:23:27.207 | khan, mojammil | PS5 - Milestone B
PL-000820 | PS5-60-UR-8100A |  | C | M | 4.9:FOUND SOME EXTRA MATERIAL IN SRN 303 (Not mentioned in PL) SILICON NEUTRA- 72 PCS. RIVETS -6 BOX PROETEX PTFE TAPE - 15 PCS ROPE SEAL - 1 PACKET | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T06:26:43.840 | khan, mojammil | PS5 - Milestone B
PL-000821 | PS5-60-UR-8100A |  | B | M | 4.10:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100A | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T06:43:19.377 | khan, mojammil | PS5 - Milestone B
PL-000822 | PS5-60-UR-8100C |  | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100C | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  |  | 2025-02-22T06:46:41.200 | khan, mojammil | PS5 - Milestone D
PL-000823 | PS5-60-UR-8100D |  | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100D | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-02-22T06:49:20.223 | khan, mojammil | PS5 - Milestone D
PL-000824 | PS5-60-UR-8100E |  | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100E | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2025-02-22T06:52:01.410 | khan, mojammil | PS5 - Milestone D
PL-000825 | PS5-60-UR-8100G |  | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100G | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-02-22T06:54:21.090 | khan, mojammil | PS5 - Milestone E
PL-000826 | PS5-60-UR-8100F |  | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100F | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-02-22T06:56:29.570 | khan, mojammil | PS5 - Milestone D
PL-000827 | PS5-60-UR-8100B |  | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100B | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2025-02-22T06:58:22.300 | khan, mojammil | PS5 - Milestone B
PL-000828 | PS5-60-UR-8100G |  | B | E | 4.1: THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41700A/B) | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-02-22T07:08:39.053 | khan, mojammil | PS5 - Milestone E
PL-000829 | PS5-60-UR-8100A |  | B | M | 4.11:THERE IS NO PROPER PACKING LIST, AND ACCORDING TO THE COLLI LIST, 1 REGULATING RING IS MISSING. ONLY 5 RINGS WERE FOUND ACROSS ALL THE BOXES.-SHIPPED LOOSE ITEM SRN 311 | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T07:12:22.210 | khan, mojammil | PS5 - Milestone B
PL-000830 | PS5-60-UR-8100A |  | B | M | 4.12:NO PROPER PACKING LIST AVAILABLE- SRN 311 CAPITAL SPARES | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T07:16:23.553 | khan, mojammil | PS5 - Milestone B
PL-000831 | PS5-60-UR-8100A |  | B | M | 4.13:THE DRYER COVER IS DAMAGED- INSTRUMENTATION AIR STATION PS5-60-UA-5200 | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T07:19:47.480 | khan, mojammil | PS5 - Milestone B
PL-000832 | PS5-60-UR-8100A |  | A | M | 4.14:2 OF THE FLEXIBLE HOSES ARE DAMAGED AND NEEDS REPLACEMENT-INSTRUMENTATION AIR STATION PS5-60-UA-5200 | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T07:26:54.290 | khan, mojammil | PS5 - Milestone B
PL-000833 | PS5-60-UR-8100A |  | A | M | 4.15:THE SPRINGS HAVE BEEN DISPLACED FROM THE BOTTOM OF THE EQUIPMENT.-INSTRUMENTATION AIR STATION PS5-60-UA-5200 | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T07:30:38.563 | khan, mojammil | PS5 - Milestone B
PL-000834 | PS5-60-UR-8100A |  | B | M | 4.16:THE COMPRESSOR COVER GUIDE IS DAMAGED-INSTRUMENTATION AIR STATION PS5-60-UA-5200 | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T07:33:04.730 | khan, mojammil | PS5 - Milestone B
PL-000835 | PS5-60-UR-8100A |  | B | M | 4.17:THE PRV 5206 OUTLET IS NOT PLUGGED.-INSTRUMENTATION AIR STATION PS5-60-UA-5200 | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T07:35:14.213 | khan, mojammil | PS5 - Milestone B
PL-000836 | PS5-60-UR-8100A |  | B | M | 4.18: THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41100A/B) | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T07:49:48.420 | khan, mojammil | PS5 - Milestone B
PL-000837 | PS5-60-UR-8100C |  | B | E | 4.1: THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41300A/B) | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  |  | 2025-02-22T07:52:35.660 | khan, mojammil | PS5 - Milestone D
PL-000838 | PS5-60-UR-8100D |  | B | E | 4.1:THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41400A/B) | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-02-22T07:54:24.980 | khan, mojammil | PS5 - Milestone D
PL-000839 | PS5-60-UR-8100E |  | B | E | 4.1:THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41500A/B) | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2025-02-22T07:56:41.940 | khan, mojammil | PS5 - Milestone D
PL-000840 | PS5-60-UR-8100F |  | B | E | 4.1:THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41600A/B) | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-02-22T07:59:13.960 | khan, mojammil | PS5 - Milestone D
PL-000841 | PS5-60-UR-8100B |  | B | E | 4.1:THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41200A/B) | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2025-02-22T08:01:25.277 | khan, mojammil | PS5 - Milestone B
PL-000842 | PS5-60-UR-8100A |  | C | M | 4.19:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T08:07:59.240 | khan, mojammil | PS5 - Milestone B
PL-000843 | PS5-60-UR-8100C |  | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  |  | 2025-02-22T08:09:48.010 | khan, mojammil | PS5 - Milestone D
PL-000844 | PS5-60-UR-8100D |  | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-02-22T08:13:36.607 | khan, mojammil | PS5 - Milestone D
PL-000845 | PS5-60-UR-8100E |  | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2025-02-22T08:15:48.273 | khan, mojammil | PS5 - Milestone D
PL-000846 | PS5-60-UR-8100G |  | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-02-22T08:19:28.137 | khan, mojammil | PS5 - Milestone E
PL-000847 | PS5-60-UR-8100F |  | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-02-22T08:21:41.097 | khan, mojammil | PS5 - Milestone D
PL-000848 | PS5-60-UR-8100B |  | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2025-02-22T08:23:21.210 | khan, mojammil | PS5 - Milestone B
PL-000849 | PS5-60-UR-8100G |  | C | M | 4.3:THE Y-PIECE IS BENT AT A CERTAIN POINT. | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-02-22T08:26:05.923 | khan, mojammil | PS5 - Milestone E
PL-000850 | PS5-60-UR-8100A |  | C | M | 4.20:Found Electric compressor motor solenoid valve power and earthing cable damaged for Instrumentation air station package (PS5-60-UA-5200). | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T08:28:41.483 | khan, mojammil | PS5 - Milestone B
PL-000851 | PS5-60-UR-8100A |  | C | M | 4.21:All CO Control panel tag no need to be corrected as per building layout drawing- SRN 311 CO CONTROL CABINET | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T08:31:49.980 | khan, mojammil | PS5 - Milestone B
PL-000852 | PS5-60-UR-8100A |  | C | M | 4.22:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T08:36:49.500 | khan, mojammil | PS5 - Milestone B
PL-000853 | PS5-60-UR-8100C |  | C | M | 4.3:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  |  | 2025-02-22T08:39:39.737 | khan, mojammil | PS5 - Milestone D
PL-000854 | PS5-60-UR-8100D |  | C | M | 4.3:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-02-22T08:41:51.480 | khan, mojammil | PS5 - Milestone D
PL-000855 | PS5-60-UR-8100E |  | C | M | 4.3:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2025-02-22T08:44:07.410 | khan, mojammil | PS5 - Milestone D
PL-000856 | PS5-60-UR-8100G |  | C | M | 4.4:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-02-22T08:48:28.860 | khan, mojammil | PS5 - Milestone E
PL-000857 | PS5-60-UR-8100F |  | C | M | 4.3:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-02-22T08:50:47.640 | khan, mojammil | PS5 - Milestone D
PL-000858 | PS5-60-UR-8100B |  | C | M | 4.3:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2025-02-22T08:54:01.853 | khan, mojammil | PS5 - Milestone B
PL-000859 | PS5-60-UR-8100A |  | B | M | 4.23:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100A | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T09:01:14.297 | khan, mojammil | PS5 - Milestone B
PL-000860 | PS5-60-UR-8100C |  | B | M | 4.4:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100C | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  |  | 2025-02-22T09:03:39.000 | khan, mojammil | PS5 - Milestone D
PL-000861 | PS5-60-UR-8100D |  | B | M | 4.4:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100D | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-02-22T09:06:07.050 | khan, mojammil | PS5 - Milestone D
PL-000862 | PS5-60-UR-8100E |  | B | M | 4.4:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100E | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2025-02-22T09:55:57.997 | khan, mojammil | PS5 - Milestone D
PL-000863 | PS5-60-UR-8100G |  | B | M | 4.5:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100G | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-02-22T09:58:29.210 | khan, mojammil | PS5 - Milestone E
PL-000864 | PS5-60-UR-8100F |  | B | M | 4.4:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100F | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-02-22T10:00:45.063 | khan, mojammil | PS5 - Milestone D
PL-000865 | PS5-60-UR-8100B |  | B | M | 4.4:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100B | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2025-02-22T10:03:05.663 | khan, mojammil | PS5 - Milestone B
PL-000866 | PS5-60-UR-8100E |  | A | M | 4.5:THE AIR STARTING RECEIVER PS5-60-VA-5100E SOLENOID VALVE IS DISCONNECTED AND LYING ON THE GROUND. | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2025-02-22T10:06:26.263 | khan, mojammil | PS5 - Milestone D
PL-000867 | PS5-60-UR-8100F |  | C | M | 4.5:THE MATERIAL OF THE VESSEL IS UNEVEN AND IRREGULAR.(AIR STARTING RECEIVER PS5-60-VA-5100F) | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-02-22T10:09:50.293 | khan, mojammil | PS5 - Milestone D
PL-000868 | PS5-60-UR-8100A |  | B | M | 4.24:THE AIR RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED(PS5-60-VA-5200) | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-02-22T10:13:32.147 | khan, mojammil | PS5 - Milestone B
PL-000870 | PS5-28-UZ-8100 |  | B | M | 4:FOUND TYRES WITH BUMPS(H150 PUMP SET +MOTOR+ MOBILE TROLLEY) | EPS VENDOR | PS5-28-10 - Oil Skimmer Package |  | Originated |  |  | 2025-02-24T07:08:52.820 | khan, mojammil | PS5 - Milestone I
PL-000871 | PS5-28-UZ-8100 |  | B | M | 4.1:THE H150 PUMPSET HAS OPENINGS THAT ARE NOT PROPERLY PLUGGED. | EPS VENDOR | PS5-28-10 - Oil Skimmer Package |  | Originated |  |  | 2025-02-24T07:12:47.160 | khan, mojammil | PS5 - Milestone I
PL-000872 | PS5-28-UZ-8100 |  | C | M | 4.2:THE TERMINAL BOX EXHIBITS PAINT DAMAGE.(H150 PUMP SET +MOTOR+ MOBILE TROLLEY) | EPS VENDOR | PS5-28-10 - Oil Skimmer Package |  | Originated |  |  | 2025-02-24T07:14:19.530 | khan, mojammil | PS5 - Milestone I
PL-000873 | PS5-28-UZ-8100 |  | A | M | 4.3:START-UP SPARES ARE NOT AVAILABLE. | EPS VENDOR | PS5-28-10 - Oil Skimmer Package |  | Originated |  |  | 2025-02-24T07:16:39.153 | khan, mojammil | PS5 - Milestone I
PL-000874 | PS5-28-UZ-8100 |  | B | M | 4.4:OVERAGE-FOUND INDUSTRIAL PLUG & SOCKET- OUTLETS DECONTACTOR AND BOXES,CLOSING MECHANISM & SOCKET DXN6. | EPS VENDOR | PS5-28-10 - Oil Skimmer Package |  | Originated |  |  | 2025-02-24T07:18:26.523 | khan, mojammil | PS5 - Milestone I
PL-001011 | PS5-60-IH-0002 |  | C | E | Panel Tag Number need to be provided for PS5-60-IH-0002/1&2 | EPS UNATRAC | PS5-60-22 - Power Gen Master UCP |  | Originated |  |  | 2025-04-01T14:51:16.000 | thurai, Sivakumar | PS5 - Milestone B
PL-001012 | PS5-60-IE-0002A |  | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002A | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-04-02T14:17:32.000 | thurai, Sivakumar | PS5 - Milestone B
PL-001013 | PS5-60-IE-0002B |  | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002B | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2025-04-02T14:22:12.000 | thurai, Sivakumar | PS5 - Milestone B
PL-001014 | PS5-60-IE-0002C |  | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002C | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  |  | 2025-04-02T14:33:50.000 | thurai, Sivakumar | PS5 - Milestone D
PL-001015 | PS5-60-IE-0002D |  | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002D | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-04-02T14:35:35.000 | thurai, Sivakumar | PS5 - Milestone D
PL-001016 | PS5-60-IE-0002E |  | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002E | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2025-04-02T14:37:30.000 | thurai, Sivakumar | PS5 - Milestone D
PL-001017 | PS5-60-IE-0002F |  | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002F | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-04-02T14:40:36.000 | thurai, Sivakumar | PS5 - Milestone D
PL-001018 | PS5-60-IE-0002G |  | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002G | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-04-02T14:42:09.000 | thurai, Sivakumar | PS5 - Milestone E
PL-001019 | PS5-60-IE-0004 |  | B | E | Panel key need to be provided for PS5-60-IE-0004 | EPS UNATRAC | PS5-60-22 - Power Gen Master UCP |  | Originated |  |  | 2025-04-02T14:44:38.000 | thurai, Sivakumar | PS5 - Milestone B
PL-001050 | PS5-60-IH-0001B |  | B | E | Damaged bottom plinth needs to be fixed properly for PS5-60-IH-0001B/3&4 | EPS UNATRAC | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs |  | Originated |  |  | 2025-04-03T08:52:18.000 | thurai, Sivakumar | PS5 - Milestone B
PL-001051 | PS5-60-IH-0001B |  | B | E | Panel C4 compartment door not open need to be rectified for PS5-60-IH-0001B/3&4 | EPS UNATRAC | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs |  | Originated |  |  | 2025-04-03T08:55:08.000 | thurai, Sivakumar | PS5 - Milestone B
PL-001052 | PS5-60-IE-0004 |  | A | E | Workstation desktop package inside mouse missing and need to be provided (4CE251CSBC) | EPS UNATRAC | PS5-60-22 - Power Gen Master UCP |  | Originated |  |  | 2025-04-03T09:04:33.000 | thurai, Sivakumar | PS5 - Milestone B
PL-001228 | PS5-28-VSP-1300A |  | C | M | 4:FOUR JACKING BOLTS ARE FOUND MISSING FROM THE SEAL OIL DRAIN DRUM | EPS VENDOR | PS5-28-13 - Seal Oil Drain Drum & Pump A |  | Originated |  |  | 2025-05-05T13:57:12.470 | khan, mojammil | PS5 - Milestone H
PL-001229 | PS5-28-VSP-1300B |  | C | M | 4:FOUR JACKING BOLTS ARE FOUND MISSING FROM THE SEAL OIL DRAIN DRUM | EPS VENDOR | PS5-28-14 - Seal Oil Drain Drum & Pump B |  | Originated |  |  | 2025-05-05T14:04:56.547 | khan, mojammil | PS5 - Milestone H
PL-001230 | PS5-28-VSP-1300C |  | C | M | 4:FOUR JACKING BOLTS ARE FOUND MISSING FROM THE SEAL OIL DRAIN DRUM | EPS VENDOR | PS5-28-15 - Seal Oil Drain Drum & Pump C |  | Originated |  |  | 2025-05-05T14:06:44.927 | khan, mojammil | PS5 - Milestone H
PL-001231 | PS5-25-PA-3100A |  | B | M | 4:IN THE PACKING LIST, THE M32 CABLE GLAND AND SHROUD SHOULD BE 3, BUT WE RECEIVED ONLY 2 | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:07:41.003 | khan, mojammil | PS5 - Milestone H
PL-001232 | PS5-25-PA-3100A |  | C | M | 4.1:THE PLUGS FOR GATE VALVE 130 AND 134 ARE MISSING | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:14:09.707 | khan, mojammil | PS5 - Milestone H
PL-001233 | PS5-25-PA-3100A |  | B | M | 4.2:PSV 104 CALIBRATION SEAL WIRE IS BROKEN | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:16:34.480 | khan, mojammil | PS5 - Milestone H
PL-001234 | PS5-25-PA-3100A |  | C | M | 4.3:MOTOR TERMINAL BOX SUPPORT IS MISSING | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A | 2025-06-24T01:41:28.000 | Closed |  |  | 2025-05-06T08:22:21.750 | khan, mojammil | PS5 - Milestone H
PL-001235 | PS5-25-PA-3100A |  | A | M | 4.4:FLANGE CONNECTION TO FO 103 – NUT BOLT MISSING | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:23:32.960 | khan, mojammil | PS5 - Milestone H
PL-001236 | PS5-25-PA-3100A |  | C | E | 4.5:PS5-25-TE-8103A TRAFFOLYTE TAG IS DAMAGED | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:27:45.890 | khan, mojammil | PS5 - Milestone H
PL-001237 | PS5-25-PA-3100A |  | C | M | 4.6:SOME OF THE BOLTS IN THE PUMP BEARING HOUSING ARE RUSTED | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:28:53.153 | khan, mojammil | PS5 - Milestone H
PL-001238 | PS5-25-PA-3100A |  | C | E | 4.7:JB KEYS NOT FOUND | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:30:55.900 | khan, mojammil | PS5 - Milestone H
PL-001239 | PS5-25-PA-3100A |  | B | E | 4.8:TIT 3012 SENSOR NOT PROPERLY SECURE, THE SENSOR IS EXPOSED , NEED TO BE INSTALLED | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:32:18.330 | khan, mojammil | PS5 - Milestone H
PL-001240 | PS5-25-PA-3100A |  | A | E | 4.9:EARTHING POINTS MISSING GROUNDING CONNECTIONS | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:34:24.987 | khan, mojammil | PS5 - Milestone H
PL-001241 | PS5-25-PA-3100A |  | C | E | 4.10:CABLE TAG FOR ORANGE CABLE MISSING(PS5-79-IP-0001) | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:36:05.060 | khan, mojammil | PS5 - Milestone H
PL-001242 | PS5-25-PA-3100A |  | B | M | 4.11:CANOPY & CANOPY SUPPORT MISSING(PS5-25-LIT-8102A) | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:39:29.907 | khan, mojammil | PS5 - Milestone H
PL-001243 | PS5-25-PA-3100A |  | B | M | 4.12:CANOPY MISSING(PS5-25-PIT-8102A) | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:40:54.143 | khan, mojammil | PS5 - Milestone H
PL-001244 | PS5-25-PA-3100A |  | C | E | 4.13:CABLE TAG MISSING FOR ALL IP DEVICES (PS5-79-IP-9902/9003/9004/0003 ) | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:43:08.520 | khan, mojammil | PS5 - Milestone H
PL-001245 | PS5-25-PA-3100A |  | C | M | 4.14:CANOPY NOT PROVIDED FOR JB AS ELECTRONIC COMPONENTS ARE PRESENT INSIDE THE JB(PS5-25-BI-1801A) | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-06T08:45:03.450 | khan, mojammil | PS5 - Milestone H
PL-001246 | PS5-25-PA-3100B |  | B | M | 4:IN THE PACKING LIST, THE M32 CABLE GLAND AND SHROUD SHOULD BE 3, BUT WE RECEIVED ONLY 2 | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:18:56.730 | khan, mojammil | PS5 - Milestone H
PL-001247 | PS5-25-PA-3100B |  | A | M | 4.1:THE PIPE FLANGE TO THE LUBE OIL COOLER IS MISSING 4 NUTS, BOLTS, AND A GASKET | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:21:23.837 | khan, mojammil | PS5 - Milestone H
PL-001248 | PS5-25-PA-3100B |  | C | M | 4.2:THE MOTOR DM 102 IS NOT SECURED AND IS SHAKING , 2 SCREWS ARE MISSING | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:27:21.360 | khan, mojammil | PS5 - Milestone H
PL-001249 | PS5-25-PA-3100B |  | C | M | 4.3:SOME OF THE BOLTS IN THE PUMP BEARING HOUSING ARE RUSTED | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:29:02.780 | khan, mojammil | PS5 - Milestone H
PL-001250 | PS5-25-PA-3100B |  | C | M | 4.4:THE PLUGS FOR GATE VALVE 132 AND 133 ARE MISSING | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:32:12.900 | khan, mojammil | PS5 - Milestone H
PL-001251 | PS5-25-PA-3100B |  | C | M | 4.5:PSV STUD BOLT IS MISSING | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:33:37.533 | khan, mojammil | PS5 - Milestone H
PL-001252 | PS5-25-PA-3100B |  | C | M | 4.6:MOTOR TERMINAL BOX SUPPORT IS MISSING | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B | 2025-06-24T01:42:20.000 | Closed |  |  | 2025-05-06T11:34:49.033 | khan, mojammil | PS5 - Milestone H
PL-001253 | PS5-25-PA-3100B |  | B | E | 4.7:TIT 3012 SENSOR NOT PROPERLY SECURE, THE SENSOR IS EXPOSED , NEED TO BE INSTALLED | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:36:04.753 | khan, mojammil | PS5 - Milestone H
PL-001255 | PS5-25-PA-3100B |  | C | E | 4.8:JB KEYS NOT FOUND | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:38:10.860 | khan, mojammil | PS5 - Milestone H
PL-001256 | PS5-25-PA-3100B |  | A | M | 4.9:THE TEMP GAUGE, PROVIDED AS A LOOSE ITEM, HAS NO LOCK NUT | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:39:34.617 | khan, mojammil | PS5 - Milestone H
PL-001257 | PS5-25-PA-3100B |  | A | E | 4.10:EARTHING POINTS MISSING GROUNDING CONNECTIONS | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:40:46.253 | khan, mojammil | PS5 - Milestone H
PL-001258 | PS5-25-PA-3100B |  | C | E | 4.11:CABLE TAG FOR ORANGE CABLE MISSING (PS5-79-IP-0002) | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:42:40.713 | khan, mojammil | PS5 - Milestone H
PL-001259 | PS5-25-PA-3100B |  | B | M | 4.12:CANOPY & CANOPY SUPPORT MISSING (PS5-25-LIT-8102B) | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:43:40.090 | khan, mojammil | PS5 - Milestone H
PL-001260 | PS5-25-PA-3100B |  | B | M | 4.13:CANOPY MISSING (PS5-25-PIT-8102B) | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:44:50.917 | khan, mojammil | PS5 - Milestone H
PL-001261 | PS5-25-PA-3100B |  | C | E | 4.14:CABLE TAG MISSING FOR ALL IP DEVICES (PS5-79-IP-9902/9003/9004/0003) | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:46:02.690 | khan, mojammil | PS5 - Milestone H
PL-001262 | PS5-25-PA-3100B |  | C | M | 4.15:CANOPY NOT PROVIDED FOR JB AS ELECTRONIC COMPONENTS ARE PRESENT INSIDE THE JB .(PS5-25-BI-1801B) | EPS SULZER | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-05-06T11:47:04.653 | khan, mojammil | PS5 - Milestone H
PL-001263 | PS5-25-PA-3100C |  | B | M | 4:IN THE PACKING LIST, THE M32 CABLE GLAND AND SHROUD SHOULD BE 3, BUT WE RECEIVED ONLY 2 | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:03:17.573 | khan, mojammil | PS5 - Milestone H
PL-001264 | PS5-25-PA-3100C |  | C | M | 4.1:PSV STUD BOLT IS MISSING | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:04:47.263 | khan, mojammil | PS5 - Milestone H
PL-001265 | PS5-25-PA-3100C |  | B | E | 4.2:TIT 3012 SENSOR IS SLIGHTLY BEND AND NOT PROPERLY SECURED, THE SENSOR IS EXPOSED . NEED TO BE INSTALLED | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:09:28.130 | khan, mojammil | PS5 - Milestone H
PL-001266 | PS5-25-PA-3100C |  | C | E | 4.3:JB KEYS NOT FOUND | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:11:18.933 | khan, mojammil | PS5 - Milestone H
PL-001267 | PS5-25-PA-3100C |  | A | M | 4.4:THE TEMP GAUGE, PROVIDED AS A LOOSE ITEM, HAS NO LOCK NUT | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:12:26.217 | khan, mojammil | PS5 - Milestone H
PL-001268 | PS5-25-PA-3100C |  | C | M | 4.5:THE PLUGS FOR GATE VALVE 132 IS MISSING | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:13:40.227 | khan, mojammil | PS5 - Milestone H
PL-001269 | PS5-25-PA-3100C |  | A | E | 4.6:EARTHING POINTS MISSING GROUNDING CONNECTIONS | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:15:46.017 | khan, mojammil | PS5 - Milestone H
PL-001270 | PS5-25-PA-3100C |  | C | E | 4.7:CABLE TAG FOR ORANGE CABLE MISSING (PS5-79-IP-0003) | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:17:22.493 | khan, mojammil | PS5 - Milestone H
PL-001271 | PS5-25-PA-3100C |  | B | M | 4.8:CANOPY & CANOPY SUPPORT MISSING (PS5-25-LIT-8102C) | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:18:11.450 | khan, mojammil | PS5 - Milestone H
PL-001272 | PS5-25-PA-3100C |  | B | M | 4.9:CANOPY MISSING (PS5-25-PIT-8102C) | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:20:21.223 | khan, mojammil | PS5 - Milestone H
PL-001273 | PS5-25-PA-3100C |  | C | E | 4.10:CABLE TAG MISSING FOR ALL IP DEVICES (PS5-79-IP-9902/9003/9004/0003 ) | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:23:26.277 | khan, mojammil | PS5 - Milestone H
PL-001274 | PS5-25-PA-3100C |  | C | M | 4.11:JB CANOPY MISSING (PS5-25-BI-1274C) | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:24:24.577 | khan, mojammil | PS5 - Milestone H
PL-001275 | PS5-25-PA-3100C |  | C | M | 4.12:CANOPY NOT PROVIDED FOR JB AS ELECTRONIC COMPONENTS ARE PRESENT INSIDE THE JB. (PS5-25-BI-1801C) | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-05-06T12:25:15.103 | khan, mojammil | PS5 - Milestone H
PL-001276 | PS5-25-PA-3100C |  | C | M | 4.13:MOTOR TERMINAL BOX SUPPORT IS MISSING | EPS SULZER | PS5-25-04 - Crude Oil Export Pump C | 2025-06-24T01:43:13.000 | Closed |  |  | 2025-05-06T13:03:11.203 | khan, mojammil | PS5 - Milestone H
PL-001303 | PS5-25-UJ-6100 |  | A | M | 4:As per the packing list, 3 PGs were listed, but only 2 were received. One PG is missing. | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-08T06:46:41.567 | khan, mojammil | PS5 - Milestone H
PL-001304 | PS5-25-UJ-6100 |  | B | M | 4.1:Received 2 pressure gauges, both of which are leaking from the dial. Replacement or refilling by the vendor is required | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-08T06:48:38.173 | khan, mojammil | PS5 - Milestone H
PL-001305 | PS5-25-UJ-6100 |  | B | M | 4.2: Missing as per packing list ( 60. Rubber metal cushion, 65.Stud, 70.Wear insert, 80. Hexagon nut not found) | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-08T06:54:43.763 | khan, mojammil | PS5 - Milestone H
PL-001306 | PS5-25-UJ-6100 |  | C | M | 4.3:Overage material (control gear unit received which is not showing in PL) | EPS SULZER | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-05-08T07:10:19.573 | khan, mojammil | PS5 - Milestone H
PL-001312 | PS5-71-HE-2400A |  | C | M | 4:FOUND 6 nos CABLE GLANDS 4 nos RTJ GASKETS WHICH ARE NOT SHOWING IN PACKING LIST , 2 nos SLIDING PLATE (OVERAGE) | EPS VENDOR | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-05-08T12:17:13.307 | khan, mojammil | PS5 - Milestone H
PL-001313 | PS5-71-HE-2400A |  | A | M | 4.1:4NOS. GASKETS MISSING (AS PER PL 8NOS.) | EPS VENDOR | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-05-08T12:18:28.107 | khan, mojammil | PS5 - Milestone H
PL-001314 | PS5-71-HE-2400A |  | A | M | 4.2:6NOS. BOLTS MISSING (AS PER PL 12NOS.) | EPS VENDOR | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-05-08T12:19:53.313 | khan, mojammil | PS5 - Milestone H
PL-001315 | PS5-71-HE-2400A |  | A | M | 4.3:12 NOS. NUTS MISSING (AS PER PL 24NOS.) | EPS VENDOR | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-05-08T12:21:21.367 | khan, mojammil | PS5 - Milestone H
PL-001316 | PS5-71-HE-2400A |  | A | M | 4.4:12 NOS. WASHERS MISSING (AS PER PL 24NOS.) | EPS VENDOR | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-05-08T12:24:00.053 | khan, mojammil | PS5 - Milestone H
PL-001317 | PS5-71-HE-2400A |  | C | E | 4.5:ELECTRICAL CABLE ENTRIES WERE NOT PLUGGED | EPS VENDOR | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-05-08T12:24:50.393 | khan, mojammil | PS5 - Milestone H
PL-001318 | PS5-71-HE-2400A |  | B | M | 4.6:4 EACH BOLTS MISSING ON 2 FLANGES | EPS VENDOR | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-05-08T12:26:23.150 | khan, mojammil | PS5 - Milestone H
PL-001319 | PS5-71-HE-2400B |  | B | M | 4:TOTAL 8 BOLTS MISSING ON 2 FLANGES | EPS VENDOR | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-05-08T12:31:46.353 | khan, mojammil | PS5 - Milestone H
PL-001320 | PS5-53-PA-3100A |  | C | M | 4:PAINT DAMAGE IN THE MOTOR TERMINAL BOX | EPS VENDOR | PS5-53-02 - Water Distribution Pump A/B |  | Originated |  |  | 2025-05-08T12:41:56.537 | khan, mojammil | PS5 - Milestone E
PL-001321 | PS5-53-PA-3100B |  | C | M | 4:PAINT DAMAGE IN THE MOTOR TERMINAL BOX | EPS VENDOR | PS5-53-02 - Water Distribution Pump A/B |  | Originated |  |  | 2025-05-08T12:44:29.703 | khan, mojammil | PS5 - Milestone E
PL-001322 | PS5-28-PA-3300 |  | C | M | 4:We received two vertical pumps, but the plugs are not available | EPS VENDOR | PS5-28-06 - Relief Drum and Pump | 2025-07-15T10:31:12.000 | Closed |  |  | 2025-05-08T12:50:38.777 | khan, mojammil | PS5 - Milestone G
PL-001323 | PS5-28-PA-3400 |  | C | M | 4:We received two vertical pumps, but the plugs are not available. | EPS VENDOR | PS5-28-03 - Closed Drain Drum and Pump 01 | 2025-07-15T10:32:56.000 | Closed |  |  | 2025-05-08T12:54:53.423 | khan, mojammil | PS5 - Milestone G
PL-001324 | PS5-25-ZS-1201 |  | B | M | 4:PIG SIGNALLER FLANGE SURFACE IS RUSTED | EPS VENDOR | PS5-25-07 - Export Pipeline Pig Launcher |  | Originated |  |  | 2025-05-08T13:05:11.937 | khan, mojammil | PS5 - Milestone H
PL-001328 | PS5-71-PA-3500A |  | B | M | 4:Oil leakage detected from the pump (PS5-71-PA-3500A) | EPS VENDOR | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  |  | 2025-05-09T11:33:45.840 | khan, mojammil | PS5 - Milestone B
PL-001329 | PS5-71-PA-3500B |  | B | M | 4:Oil leakage detected from the pump (PS5-71-PA-3500B) | EPS VENDOR | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  |  | 2025-05-09T11:41:48.970 | khan, mojammil | PS5 - Milestone B
PL-001330 | PS5-28-PA-3700A |  | B | M | 4:Oil leakage detected from the pump (PS5-28-PA-3700A) | EPS VENDOR | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  |  | 2025-05-09T11:46:39.397 | khan, mojammil | PS5 - Milestone E
PL-001331 | PS5-28-PA-3700A |  | C | M | 4.1:Pump body flanges are rusted (PS5-28-PA-3700A) | EPS VENDOR | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  |  | 2025-05-09T11:49:34.637 | khan, mojammil | PS5 - Milestone E
PL-001332 | PS5-28-PA-3700B |  | B | M | 4:Oil leakage detected from the pump (PS5-28-PA-3700B) | EPS VENDOR | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  |  | 2025-05-09T11:52:20.400 | khan, mojammil | PS5 - Milestone E
PL-001333 | PS5-53-TR-4100 |  | C | M | 4:(PACKAGE NO :6) 10000 X 2000= 2 pcs OVERAGE | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank |  | Originated |  |  | 2025-05-09T12:19:47.953 | khan, mojammil | PS5 - Milestone C
PL-001334 | PS5-53-TR-4100 |  | C | M | 4.1:(PACKAGE NO :10), 120X120X8 = 2000MM LENGTH 1 pcs OVERAGE | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank |  | Originated |  |  | 2025-05-09T12:20:57.993 | khan, mojammil | PS5 - Milestone C
PL-001335 | PS5-53-TR-4100 |  | C | M | 4.2:(PACKAGE: 6 & 7 ) 2 PLATE DAMAGE | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank |  | Originated |  |  | 2025-05-09T12:21:47.843 | khan, mojammil | PS5 - Milestone C
PL-001336 | PS5-53-TR-4100 |  | C | M | 4.3:(PACKAGE:14 ) 2 ROOF PLATE DAMAGE | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank |  | Originated |  |  | 2025-05-09T12:24:41.597 | khan, mojammil | PS5 - Milestone C
PL-001337 | PS5-53-TR-4100 |  | C | M | 4.4:(PACKAGE:15 ) 1 ROOF PLATE DAMAGE | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank |  | Originated |  |  | 2025-05-09T12:26:57.083 | khan, mojammil | PS5 - Milestone C
PL-001338 | PS5-53-TR-4100 |  | B | M | 4.5:(PACKAGE:10) CURB ANGLE FOUND BEND | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank |  | Originated |  |  | 2025-05-09T12:29:57.073 | khan, mojammil | PS5 - Milestone C
PL-001339 | PS5-53-TR-4100 |  | A | M | 4.6:THE MG TANK ANODE SHOULD BE SUPPLIED WITH U BOLT, MOUNTING BRACKET, DOUBLE NUT, FLAT WASHER, AND LOCK WASHER; HOWEVER, WE ONLY RECEIVED THE ANODES.(CP SYSTEM MATERIAL , SRN-517) | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank |  | Originated |  |  | 2025-05-09T12:31:25.117 | khan, mojammil | PS5 - Milestone C
PL-001397 | PS5-78-JC-9100A |  | C | M | 4:ROPE DRUM (GROOVE OF THE STEEL ROPE) OF THE HOIST IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-07T10:56:07.000 | Closed |  |  | 2025-05-10T13:40:29.703 | khan, mojammil | PS5 - Milestone E
PL-001398 | PS5-78-JC-9100A |  | C | M | 4.1:HOOK IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-07T10:56:34.000 | Closed |  |  | 2025-05-10T13:45:40.750 | khan, mojammil | PS5 - Milestone E
PL-001407 | PS5-78-JC-9100A |  | B | E | 4.2:ELECTRICAL PANEL BOARD IS DAMAGED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2025-05-12T05:21:33.850 | khan, mojammil | PS5 - Milestone E
PL-001408 | PS5-78-JC-9100A |  | B | M | 4.3:2 BOLTS MISSING IN PANNEL AT TROLLEY BUMBER | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-07T10:56:58.000 | Closed |  |  | 2025-05-12T05:23:09.017 | khan, mojammil | PS5 - Milestone E
PL-001409 | PS5-78-JC-9100A |  | B | E | 4.4: GROUNTING / EARTHING POINT NOT PROVIDED FOR THE PANNEL BOXES | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-07T10:59:05.000 | Closed |  |  | 2025-05-12T05:25:57.637 | khan, mojammil | PS5 - Milestone E
PL-001410 | PS5-78-JC-9100A |  | B | E | 4.5:CABLE FERRULES NEED TO BE PROVIDED FOR ALL THE PANNEL BOXES | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2025-05-12T05:28:54.887 | khan, mojammil | PS5 - Milestone E
PL-001411 | PS5-78-JC-9100A |  | C | M | 4.6:TAG NUMBERS OF ALL THE PANEL BOX/JBS NEED TO BE FIXED PROPERLY(WITH REVETS OR SCREWS) | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:19:31.000 | Closed |  |  | 2025-05-12T05:30:34.353 | khan, mojammil | PS5 - Milestone E
PL-001412 | PS5-78-JC-9100A |  | A | M | 4.7: PENDANT TRACK IS BEND | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:57:01.000 | Closed |  |  | 2025-05-12T05:39:09.247 | khan, mojammil | PS5 - Milestone E
PL-001413 | PS5-78-JC-9100A |  | B | M | 4.8:PAINT DAMAGE / PARENT METAL DAMAGE FOUND ON GIRDER. | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:19:55.000 | Closed |  |  | 2025-05-12T05:41:30.667 | khan, mojammil | PS5 - Milestone E
PL-001414 | PS5-78-JC-9100A |  | B | M | 4.9:PLATFORM DAMAGED (PAINT AND METAL DAMAGES, SEVERE BENDS ON THE PLATFORM) | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:20:12.000 | Closed |  |  | 2025-05-12T05:43:02.063 | khan, mojammil | PS5 - Milestone E
PL-001415 | PS5-78-JC-9100A |  | B | M | 4.10:THE HANDRAIL HAS PAINT DAMAGE AND IS SEVERELY BENT DUE TO MISHANDLING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:20:26.000 | Closed |  |  | 2025-05-12T05:45:23.443 | khan, mojammil | PS5 - Milestone E
PL-001416 | PS5-78-JC-9100A |  | B | M | 4.11:DOOR LOCK HANDLE IS MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2025-05-12T05:47:40.307 | khan, mojammil | PS5 - Milestone E
PL-001417 | PS5-78-JC-9100A |  | C | M | 4.12:HAND RAIL PAINT DAMAGE | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:20:45.000 | Closed |  |  | 2025-05-12T05:50:16.040 | khan, mojammil | PS5 - Milestone E
PL-001418 | PS5-78-JC-9100A |  | C | M | 4.13:HANDRAIL BOLT NUT MISSING (6 NOS) | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:20:58.000 | Closed |  |  | 2025-05-12T05:51:18.440 | khan, mojammil | PS5 - Milestone E
PL-001419 | PS5-78-JC-9100A |  | C | M | 4.14:CABLE TROLLEYS UNIT IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:21:11.000 | Closed |  |  | 2025-05-12T05:53:34.200 | khan, mojammil | PS5 - Milestone E
PL-001420 | PS5-78-JC-9100A |  | A | M | 4.15:DOOR FIXING SCREWS ARE MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:57:53.000 | Closed |  |  | 2025-05-12T05:55:31.950 | khan, mojammil | PS5 - Milestone E
PL-001421 | PS5-78-JC-9100A |  | A | M | 4.16:C HANGERS NOT RECEIVED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:58:09.000 | Closed |  |  | 2025-05-12T05:56:47.167 | khan, mojammil | PS5 - Milestone E
PL-001422 | PS5-78-JC-9100A |  | C | M | 4.17:THE TRACK ON TOP OF THE OVER HEAD CRANE GIRDER IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:21:39.000 | Closed |  |  | 2025-05-12T05:57:16.187 | khan, mojammil | PS5 - Milestone E
PL-001425 | PS5-78-JC-9100B |  | C | M | 4:ROPE DRUM (GROOVE OF THE STEEL ROPE) OF THE HOIST IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:21:54.000 | Closed |  |  | 2025-05-12T06:28:39.530 | khan, mojammil | PS5 - Milestone E
PL-001426 | PS5-78-JC-9100B |  | C | M | 4.1:PS5-78-DE-352008 HOISTING UNIT PAINT IS DAMAGED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:22:05.000 | Closed |  |  | 2025-05-12T06:29:57.507 | khan, mojammil | PS5 - Milestone E
PL-001427 | PS5-78-JC-9100B |  | B | E | 4.2:GROUNTING / EARTHING PONINT NOT PROVIDED FOR THE PANNEL | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:22:17.000 | Closed |  |  | 2025-05-12T10:44:40.090 | khan, mojammil | PS5 - Milestone E
PL-001428 | PS5-78-JC-9100B |  | B | E | 4.3:CABLE FERRULES NEED TO BE PROVIDED FOR ALL THE PANNEL BOXES | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2025-05-12T10:46:14.990 | khan, mojammil | PS5 - Milestone E
PL-001429 | PS5-78-JC-9100B |  | C | E | 4.4:TAG NUMBERS OF ALL THE PANEL BOX/JBS NEED TO BE FIXED PROPERLY | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:22:36.000 | Closed |  |  | 2025-05-12T12:55:35.047 | khan, mojammil | PS5 - Milestone E
PL-001430 | PS5-78-JC-9100B |  | B | M | 4.5:PAINT DAMAGE / PARENT METAL DAMAGE FOUND ON GIRDER | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:22:50.000 | Closed |  |  | 2025-05-12T12:57:06.240 | khan, mojammil | PS5 - Milestone E
PL-001431 | PS5-78-JC-9100B |  | C | M | 4.6:HAND RAIL AND PLATFORM PAINT IS DAMAGED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:23:08.000 | Closed |  |  | 2025-05-12T13:04:23.200 | khan, mojammil | PS5 - Milestone E
PL-001432 | PS5-78-JC-9100B |  | B | M | 4.7:DOOR LOCK MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2025-05-12T13:05:43.693 | khan, mojammil | PS5 - Milestone E
PL-001433 | PS5-78-JC-9100B |  | B | M | 4.8:HAND RAIL IS SEVERELY BEND | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:23:22.000 | Closed |  |  | 2025-05-12T13:06:50.373 | khan, mojammil | PS5 - Milestone E
PL-001435 | PS5-78-JC-9100B |  | A | M | 4.9:14 C HANGERS NOT RECEIVED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:58:38.000 | Closed |  |  | 2025-05-12T13:08:38.560 | khan, mojammil | PS5 - Milestone E
PL-001436 | PS5-78-JC-9100B |  | C | M | 4.10:CABLE TROLLEY UNIT IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Completed |  |  | 2025-05-12T13:09:19.490 | khan, mojammil | PS5 - Milestone E
PL-001438 | PS5-78-JC-9100B |  | C | M | 4.11:SWITCH STOP UNIT PAINT IS DAMAGED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Completed |  |  | 2025-05-12T13:13:41.997 | khan, mojammil | PS5 - Milestone E
PL-001447 | PS5-78-JC-9100B |  | C | M | 4.12:6 HAND RAIL BOLTS MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Completed |  |  | 2025-05-12T13:50:59.727 | khan, mojammil | PS5 - Milestone E
PL-001448 | PS5-78-JC-9100B |  | A | M | 4.13:DOOR FIXING SCREWS ARE MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:58:50.000 | Closed |  |  | 2025-05-12T13:52:39.087 | khan, mojammil | PS5 - Milestone E
PL-001449 | PS5-78-JC-9100B |  | B | M | 4.14:2 BOLTS MISSING IN PANNEL AT TROLLEY BUMBER | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:23:43.000 | Closed |  |  | 2025-05-12T13:55:08.380 | khan, mojammil | PS5 - Milestone E
PL-001450 | PS5-78-JC-9100B |  | C | M | 4.15:THE TRACK ON TOP OF THE OVER HEAD CRANE GIRDER IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:24:02.000 | Closed |  |  | 2025-05-12T13:56:35.043 | khan, mojammil | PS5 - Milestone E
PL-001451 | PS5-78-JC-9100C |  | C | M | 4:ROPE DRUM (GROOVE OF THE STEEL ROPE) OF THE HOIST IS RUSTED. | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:24:17.000 | Closed |  |  | 2025-05-13T04:16:46.750 | khan, mojammil | PS5 - Milestone E
PL-001452 | PS5-78-JC-9100C |  | C | M | 4.1:HOOK BLOCK AREA IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:24:31.000 | Closed |  |  | 2025-05-13T04:18:36.447 | khan, mojammil | PS5 - Milestone E
PL-001453 | PS5-78-JC-9100C |  | C | M | 4.2:HOISTING UNIT 2 LOCK NUTS ARE RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:24:46.000 | Closed |  |  | 2025-05-13T04:19:57.870 | khan, mojammil | PS5 - Milestone E
PL-001454 | PS5-78-JC-9100C |  | B | E | 4.3: GROUNTING / EARTHING POINT IS NOT PROVIDED FOR THE PANNEL | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:25:10.000 | Closed |  |  | 2025-05-13T04:21:07.777 | khan, mojammil | PS5 - Milestone E
PL-001455 | PS5-78-JC-9100C |  | B | E | 4.4:CABLE FERRULES NEED TO BE PROVIDED FOR ALL PANNEL BOXES | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2025-05-13T04:23:04.563 | khan, mojammil | PS5 - Milestone E
PL-001456 | PS5-78-JC-9100C |  | C | E | 4.5:TAG NUMBERS OF ALL THE PANEL BOX/JB NEED TO BE FIXED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:25:26.000 | Closed |  |  | 2025-05-13T04:24:22.643 | khan, mojammil | PS5 - Milestone E
PL-001457 | PS5-78-JC-9100C |  | C | M | 4.6:WARNING STICKER IS DAMAGE | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:25:41.000 | Closed |  |  | 2025-05-13T04:26:13.623 | khan, mojammil | PS5 - Milestone E
PL-001458 | PS5-78-JC-9100C |  | B | M | 4.7:2 BOLTS MISSING IN THE PANNEL AT TROLLEY BUMBER | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:25:57.000 | Closed |  |  | 2025-05-13T04:28:06.083 | khan, mojammil | PS5 - Milestone E
PL-001459 | PS5-78-JC-9100C |  | A | M | 4.8:TOOL MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:59:01.000 | Closed |  |  | 2025-05-13T04:29:11.630 | khan, mojammil | PS5 - Milestone E
PL-001460 | PS5-78-JC-9100C |  | B | M | 4.9:PAINT DAMAGE / PARENT METAL DAMAGE FOUND ON GIRDER | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:26:10.000 | Closed |  |  | 2025-05-13T04:30:34.343 | khan, mojammil | PS5 - Milestone E
PL-001461 | PS5-78-JC-9100C |  | A | M | 4.10:PENDANT TRACK IS BEND | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:59:15.000 | Closed |  |  | 2025-05-13T04:31:39.623 | khan, mojammil | PS5 - Milestone E
PL-001462 | PS5-78-JC-9100C |  | B | M | 4.11:3 HAND RAIL SEVERELY BEND DUE TO MISHANDLING. | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:26:28.000 | Closed |  |  | 2025-05-13T04:33:14.527 | khan, mojammil | PS5 - Milestone E
PL-001463 | PS5-78-JC-9100C |  | C | M | 4.12:HAND RAIL & PLATFORM PAINT IS DAMAGED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:26:39.000 | Closed |  |  | 2025-05-13T04:34:29.560 | khan, mojammil | PS5 - Milestone E
PL-001464 | PS5-78-JC-9100C |  | C | M | 4.13:6 HANDRAIL NUT BOLT MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:26:56.000 | Closed |  |  | 2025-05-13T04:35:58.760 | khan, mojammil | PS5 - Milestone E
PL-001465 | PS5-78-JC-9100C |  | A | M | 4.14:9 DOOR FIXING SCREWS ARE MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:59:46.000 | Closed |  |  | 2025-05-13T04:37:31.917 | khan, mojammil | PS5 - Milestone E
PL-001466 | PS5-78-JC-9100C |  | A | M | 4.15:14 C- HANGERS NOT RECEIVED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T05:59:58.000 | Closed |  |  | 2025-05-13T04:39:02.837 | khan, mojammil | PS5 - Milestone E
PL-001467 | PS5-78-JC-9100C |  | C | M | 4.16:CABLE TROLLEY UNIT IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:27:12.000 | Closed |  |  | 2025-05-13T04:39:29.410 | khan, mojammil | PS5 - Milestone E
PL-001468 | PS5-78-JC-9100C |  | C | M | 4.17:THE TRACK ON TOP OF THE OVER HEAD CRANE GIRDERE IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:27:26.000 | Closed |  |  | 2025-05-13T04:41:26.090 | khan, mojammil | PS5 - Milestone E
PL-001469 | PS5-78-JC-9100D |  | B | M | The Hoist fan cover/ support found damage and need to be replaced-Damage during transportation | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  | Hoist Fan & Cover need to be changed. During OH crane D testing, Hoist Fan from other unit will be used temporary. | 2025-05-13T04:59:36.240 | khan, mojammil | PS5 - Milestone E
PL-001470 | PS5-78-JC-9100D |  | B | M | The brake resistor found damage and need to be replaced-Damage during transportation | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  | The brake resistor along with VSD unit found damage and need to be replaced. OH crane D will be tested only at Speed 1 and to be re-checked after installation of new resistor. | 2025-05-13T05:00:47.230 | khan, mojammil | PS5 - Milestone E
PL-001471 | PS5-78-JC-9100D |  | C | M | 4.2:HOISTING UNIT IS NOT PROPERLY PACKED. | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:27:55.000 | Closed |  |  | 2025-05-13T05:03:45.267 | khan, mojammil | PS5 - Milestone E
PL-001472 | PS5-78-JC-9100D |  | C | M | 4.3:ROPE DRUM (GROOVE OF THE STEEL ROPE) OF THE HOIST IS RUSTED. | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:28:04.000 | Closed |  |  | 2025-05-13T05:04:35.270 | khan, mojammil | PS5 - Milestone E
PL-001473 | PS5-78-JC-9100D |  | B | M | 4.4:2 BOLTS MISSING IN THE PANNEL OF THE TROLLEY BUMBER | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:28:16.000 | Closed |  |  | 2025-05-13T05:06:44.690 | khan, mojammil | PS5 - Milestone E
PL-001474 | PS5-78-JC-9100D |  | B | E | 4.5:GROUNTING/ EARTHING POINT NOT PROVIDED FOR THE PANEL | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:28:29.000 | Closed |  |  | 2025-05-13T05:08:24.883 | khan, mojammil | PS5 - Milestone E
PL-001475 | PS5-78-JC-9100D |  | B | E | 4.6:CABLE FERRULES NEED TO BE PROVIDED FOR ALL THE PANNEL BOXES | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2025-05-13T05:10:06.553 | khan, mojammil | PS5 - Milestone E
PL-001476 | PS5-78-JC-9100D |  | C | E | 4.7:TAG NUMBERS OF ALL THE PANEL BOX/JBs NEED TO BE FIXED PROPERLY. | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:28:45.000 | Closed |  |  | 2025-05-13T05:14:45.237 | khan, mojammil | PS5 - Milestone E
PL-001477 | PS5-78-JC-9100D |  | B | M | 4.8:PAINT DAMAGE / PARENT METAL DAMAGE FOUND ON THE GIRDER | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:29:00.000 | Closed |  |  | 2025-05-13T05:37:51.150 | khan, mojammil | PS5 - Milestone E
PL-001478 | PS5-78-JC-9100D |  | A | M | 4.9:PENDANT TRACK IS DAMAGED AND BEND. | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T06:00:19.000 | Closed |  |  | 2025-05-13T05:39:04.877 | khan, mojammil | PS5 - Milestone E
PL-001479 | PS5-78-JC-9100D |  | C | M | 4.10:HAND RAIL IS SEVERELY BEND DUE TO MISHANDLING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:29:16.000 | Closed |  |  | 2025-05-13T05:40:23.940 | khan, mojammil | PS5 - Milestone E
PL-001480 | PS5-78-JC-9100D |  | C | M | 4.11:HAND RAIL AND PLATFORM PAINT IS DAMAGED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:29:29.000 | Closed |  |  | 2025-05-13T05:41:18.990 | khan, mojammil | PS5 - Milestone E
PL-001481 | PS5-78-JC-9100D |  | B | M | 4.12:DOOR LOCK HANDLE MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2025-05-13T05:42:23.837 | khan, mojammil | PS5 - Milestone E
PL-001482 | PS5-78-JC-9100D |  | A | M | 4.13:ONE OVERAGE BOX OF CARBOLINE FIREPROOF COATING IS LEAKING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T06:00:52.000 | Closed |  |  | 2025-05-13T05:44:14.810 | khan, mojammil | PS5 - Milestone E
PL-001483 | PS5-78-JC-9100D |  | A | M | 4.14:9 DOOR FIXING SCREWS ARE MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T06:01:07.000 | Closed |  |  | 2025-05-13T05:47:49.437 | khan, mojammil | PS5 - Milestone E
PL-001484 | PS5-78-JC-9100D |  | C | M | 4.15:6 HANDRAIL NUT BOLT MISSING | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:29:45.000 | Closed |  |  | 2025-05-13T05:48:38.817 | khan, mojammil | PS5 - Milestone E
PL-001485 | PS5-78-JC-9100D |  | A | M | 4.16:14 C HANGERS NOT RECEIVED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-03-04T06:01:21.000 | Closed |  |  | 2025-05-13T05:49:41.410 | khan, mojammil | PS5 - Milestone E
PL-001486 | PS5-78-JC-9100D |  | C | M | 4.17:CABLE TROLLEYS UNIT IS RUSTED | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:29:59.000 | Closed |  |  | 2025-05-13T05:50:03.787 | khan, mojammil | PS5 - Milestone E
PL-001487 | PS5-78-JC-9100D |  | C | M | 4.18:THE TRACK ON TOP OF THE OVER HEAD CRANE GIRDER IS RUST | EPS VENDOR | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:30:12.000 | Closed |  |  | 2025-05-13T05:51:13.847 | khan, mojammil | PS5 - Milestone E
PL-001488 | PS5-60-PA-3300 |  | A | M | CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | EPS UNATRAC | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  |  | 2025-05-13T05:58:57.000 | khan, mojammil | PS5 - Milestone E
PL-001490 | PS5-05-UR-8100 |  | A | M | DUE TO THE MISALIGNMENT OF PENETRATIONS BETWEEN EDG & HYDRAULIC CABIN FIRE FIGHTING SYSTEM TUBING CANNOT BE CONNECTED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:42:51.000 | Closed |  |  | 2025-05-14T08:41:21.000 | khan, mojammil | PS5 - Milestone C
PL-001491 | PS5-05-UR-8100 |  | A | M | DUE TO THE MISALIGNMENT OF PENETRATIONS BETWEEN EDG & MIST CABIN FIRE FIGHTING SYSTEM TUBING CANNOT BE CONNECTED | EPS UNATRAC | PS5-05-01 - Emergency Diesel Generator Package | 2026-02-04T11:43:17.000 | Closed |  |  | 2025-05-14T08:42:43.000 | khan, mojammil | PS5 - Milestone C
PL-001547 | PS5-71-PA-3500A |  | A | M | CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | EPS VENDOR | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  |  | 2025-05-20T13:13:15.000 | khan, mojammil | PS5 - Milestone B
PL-001548 | PS5-71-PA-3500B |  | A | M | CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | EPS VENDOR | PS5-71-21 - Diesel Transfer Pump A/B |  | Originated |  |  | 2025-05-20T13:15:11.000 | khan, mojammil | PS5 - Milestone B
PL-001566 | PS5-53-PA-3100A |  | A | M | USE CAT 15W40 LUBE OIL FOR PRESERVATION, FLUSH AND USE THE PROPER LUBE OIL. | EPS VENDOR | PS5-53-02 - Water Distribution Pump A/B |  | Originated |  |  | 2025-05-22T07:14:32.000 | Guan, Gang | PS5 - Milestone E
PL-001610 | PS5-60-EA-2400A |  | A | M | 4:NOZZLE/BRANCH ZAGGED DUE TO IMPROPER FABRICATION REQUIRED TO BE RECTIFIED | EPS UNATRAC | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2025-06-17T07:21:32.003 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001614 | PS5-60-EA-2400B |  | C | M | 4:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2025-06-17T07:47:07.520 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001615 | PS5-60-EA-2400B |  | C | M | 4.1:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2025-06-17T07:51:23.963 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001616 | PS5-60-EA-2400B |  | A | M | 4.2:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2025-06-17T07:53:15.880 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001617 | PS5-60-EA-2200A |  | C | M | 4:END COVER OF THE HEADDER(CLADDING) DAMAGE (MAY BE DURING TRANSPORTATION) | EPS UNATRAC | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2025-06-17T08:00:13.967 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001618 | PS5-60-EA-2200A |  | A | M | 4.1:NOZZLE/BRANCH ZAGGED DUE TO IMPROPER FABRICATION REQUIRED TO BE RECTIFIED | EPS UNATRAC | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2025-06-17T08:03:04.313 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001619 | PS5-60-EA-2200A |  | C | M | 4.2:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2025-06-17T08:05:17.257 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001620 | PS5-60-EA-2200A |  | C | M | 4.3:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2025-06-17T08:10:55.580 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001622 | PS5-60-EA-2200A |  | A | M | 4.5:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2025-06-17T08:14:46.690 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001623 | PS5-60-EA-2200B |  | C | M | 4:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2025-06-17T08:24:37.577 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001624 | PS5-60-EA-2500A |  | A | M | 4:NOZZLE/BRANCH ZAGGED DUE TO IMPROPER FABRICATION REQUIRED TO BE RECTIFIED | EPS UNATRAC | PS5-60-74 - Engine E Cooling system |  | Originated |  |  | 2025-06-17T10:58:35.220 | mwigamba, john | PS5 - Milestone D
PL-001625 | PS5-60-EA-2100A |  | C | M | 4:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2025-06-20T11:52:49.453 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001626 | PS5-60-EA-2100A |  | C | M | 4.1:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2025-06-20T11:56:17.243 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001627 | PS5-60-EA-2100A |  | A | M | 4.2:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2025-06-20T11:58:17.753 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001628 | PS5-60-EA-2100B |  | C | M | 4:VALVE HANDLE COATING/COVER MISSING | EPS UNATRAC | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2025-06-20T12:04:11.657 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001629 | PS5-60-EA-2100B |  | C | M | 4.1:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2025-06-20T12:07:05.717 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001630 | PS5-60-EA-2100B |  | C | M | 4.2:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2025-06-20T12:08:33.383 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001631 | PS5-60-EA-2100B |  | A | M | 4.3:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2025-06-20T12:10:11.860 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001632 | PS5-60-EA-2400A |  | C | M | 4.1:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2025-06-20T12:15:09.803 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001633 | PS5-60-EA-2400A |  | C | M | 4.2:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2025-06-20T12:17:13.537 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001634 | PS5-60-EA-2400A |  | A | M | 4.3:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2025-06-20T12:18:43.510 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001641 | PS5-60-EA-2200B |  | C | M | 4.2:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2025-06-24T07:28:48.907 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001642 | PS5-60-EA-2200B |  | A | M | 4.3:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2025-06-24T07:30:23.780 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001643 | PS5-60-EA-2500A |  | C | M | 4.1:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-74 - Engine E Cooling system |  | Originated |  |  | 2025-06-24T07:39:33.820 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001645 | PS5-60-EA-2500A |  | C | M | 4.3:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-74 - Engine E Cooling system |  | Originated |  |  | 2025-06-24T07:42:10.587 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001646 | PS5-60-EA-2500A |  | A | M | 4.4:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-74 - Engine E Cooling system |  | Originated |  |  | 2025-06-24T07:44:26.423 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001647 | PS5-60-EA-2500B |  | A | M | 4:HEADDER AND BRANCH GOT SEVERE DAMAGE (May be during transportation) AND NEED TO BE RECTIFIED | EPS UNATRAC | PS5-60-74 - Engine E Cooling system |  | Originated |  |  | 2025-06-24T07:50:41.657 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001648 | PS5-60-EA-2500B |  | C | M | 4.1:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-74 - Engine E Cooling system |  | Originated |  |  | 2025-06-24T07:53:06.793 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001650 | PS5-60-EA-2500B |  | C | M | 4.2:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-74 - Engine E Cooling system |  | Originated |  |  | 2025-06-24T10:13:50.907 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001651 | PS5-60-EA-2500B |  | A | M | 4.3:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-74 - Engine E Cooling system |  | Originated |  |  | 2025-06-24T10:17:19.597 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001652 | PS5-60-EA-2600A |  | A | M | 4:NOZZLE/BRANCH ZAGGED DUE TO IMPROPER FABRICATION REQUIRED TO BE RECTIFIED | EPS UNATRAC | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2025-06-24T10:21:12.453 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001653 | PS5-60-EA-2600A |  | C | M | 4.1:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2025-06-24T10:22:53.970 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001655 | PS5-60-EA-2600A |  | C | M | 4.3:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2025-06-24T10:25:07.167 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001656 | PS5-60-EA-2600A |  | A | M | 4.4:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2025-06-24T10:26:45.200 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001657 | PS5-60-EA-2600A |  | A | M | 4.5:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2025-06-24T10:29:08.727 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001658 | PS5-60-EA-2600B |  | C | M | 4:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2025-06-24T10:32:09.147 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001659 | PS5-60-EA-2600B |  | C | M | 4.1:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2025-06-24T10:33:51.483 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001660 | PS5-60-EA-2600B |  | A | M | 4.2:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2025-06-24T10:35:12.043 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001661 | PS5-60-EA-2700A |  | C | M | 4:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2025-06-24T10:39:11.757 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001662 | PS5-60-EA-2700A |  | C | M | 4.1:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2025-06-24T10:40:35.670 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001663 | PS5-60-EA-2700A |  | A | M | 4.2:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2025-06-24T10:42:09.113 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001664 | PS5-60-EA-2700B |  | C | M | 4:SOME FINS FOUND DAMAGE | EPS UNATRAC | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2025-06-24T10:44:53.810 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001665 | PS5-60-EA-2700B |  | C | M | 4.1:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | EPS UNATRAC | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2025-06-24T10:46:27.013 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001666 | PS5-60-EA-2700B |  | A | M | 4.2:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | EPS UNATRAC | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2025-06-24T10:47:46.850 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001668 | PS5-74-UB-5100 |  | B | M | 4.1:All carbon steel (CS) bolts on the skid are rusted | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:28:39.037 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001669 | PS5-74-UB-5100 |  | B | M | 4.2:Equipment PS5-74-VF-1300B one name plate missing | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:30:10.703 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001670 | PS5-74-UB-5100 |  | C | M | 4.3:Color change observed on galvanizing of equipment and tubing supports. | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:31:38.277 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001671 | PS5-74-UB-5100 |  | C | M | 4.4:Skid base frame was found dirty and not properly cleaned prior to tansportation | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:32:57.240 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001672 | PS5-74-UB-5100 |  | A | M | 4.5:The outlet pressure gauge (PS5-74-PG-5103) needle is not functioning properly (Showing positive pressure ) | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:34:08.253 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001673 | PS5-74-UB-5100 |  | A | M | 4.6:Pressure gauge needle pointing below zero, may need to replace | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:35:27.423 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001674 | PS5-74-UB-5100 |  | B | M | 4.7:All stud bolts installed at the flange connections are over length | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:36:36.217 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001675 | PS5-74-UB-5100 |  | C | M | 4.8:Found rust of the SS earthing leg | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:37:48.837 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001676 | PS5-74-UB-5100 |  | C | M | 4.9:Welded area was not properly painted at all earthing boss. | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:39:32.330 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001677 | PS5-74-UB-5100 |  | C | M | 4.10:piping and branch connections were not properly painted | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:40:48.693 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001678 | PS5-74-UB-5100 |  | A | M | 4.11:Pipe to elbow weld joint found ruptured, Need to replace the elbow | EPS VENDOR | PS5-74-01 - N2 Generation Skid |  | Originated |  |  | 2025-06-28T10:41:54.310 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-001690 | PS5-61-IU-3100A |  | A | M | Oil leakage found from the transformer body nozzle weld area prior to installation | EPS VENDOR | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Vender need to be rectified | 2025-07-09T11:26:57.000 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001691 | PS5-28-UO-8200 |  | C | M | 4:Minor damage found during inspection, suspected to be caused during transportation | EPS VENDOR | PS5-28-11 - Open Drain Interceptor |  | Originated |  |  | 2025-07-11T05:46:26.573 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-001692 | PS5-28-UO-8200 |  | C | M | 4.1:Detials are not clear in the PL/SRN | EPS VENDOR | PS5-28-11 - Open Drain Interceptor |  | Originated |  |  | 2025-07-11T05:48:14.967 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-001693 | PS5-28-UO-8200 |  | C | M | 4.2:Detials are not clear in the PL/SRN | EPS VENDOR | PS5-28-11 - Open Drain Interceptor |  | Originated |  |  | 2025-07-11T05:49:48.353 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-001694 | PS5-28-UO-8200 |  | B | M | 4.3:Minor damage observed inside the drainage interceptor. Also not in the correct position | EPS VENDOR | PS5-28-11 - Open Drain Interceptor |  | Originated |  |  | 2025-07-11T05:51:35.723 | THANGARATHINAM, ajikumar | PS5 - Milestone I
PL-001695 | PS5-60-UZ-8900B |  | C | M | 4:It was observed that the insulation is not properly sealed | EPS UNATRAC | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  |  | 2025-07-14T05:30:17.370 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001696 | PS5-60-UZ-8900B |  | B | M | 4.1:Pressure gauge (PS5-60-PG-8905B)needle pointing below zero, may need to replace | EPS UNATRAC | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  |  | 2025-07-14T05:38:53.010 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001697 | PS5-60-UZ-8900B |  | B | M | 4.2:Pressure gauge (PS5-60-PG-8901B)needle pointing below zero, may need to replace | EPS UNATRAC | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  |  | 2025-07-14T05:40:33.580 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001698 | PS5-60-UZ-8900B |  | B | M | 4.3:Pressure gauge (PS5-60-PG-8903B)needle pointing positive, may need to replace | EPS UNATRAC | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  |  | 2025-07-14T05:41:55.303 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001699 | PS5-60-UZ-8900C |  | C | M | 4:It was observed that the insulation is not properly sealed | EPS UNATRAC | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C |  | Originated |  |  | 2025-07-14T05:45:08.430 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001700 | PS5-60-UZ-8900D |  | C | M | 4:It was observed that the insulation is not properly sealed | EPS UNATRAC | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D |  | Originated |  |  | 2025-07-14T05:48:21.383 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001701 | PS5-60-UZ-8900D |  | B | M | 4.1:Pressure gauge (PS5-60-PG-8906D)needle pointing below zero, may need to replace | EPS UNATRAC | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D |  | Originated |  |  | 2025-07-14T05:49:32.193 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001703 | PS5-60-UZ-8900E |  | C | M | 4.1:It was observed that the insulation is not properly sealed | EPS UNATRAC | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E |  | Originated |  |  | 2025-07-14T05:52:49.340 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001704 | PS5-60-UZ-8900F |  | C | M | 4:Diesel leak found, but source not yet identified (May be improper cleanning after FAT | EPS UNATRAC | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Originated |  |  | 2025-07-14T05:58:34.740 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001705 | PS5-60-UZ-8900F |  | C | M | 4.1:It was observed that the insulation is not properly sealed | EPS UNATRAC | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Originated |  |  | 2025-07-14T06:00:31.750 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001706 | PS5-60-UZ-8900F |  | B | M | 4.2:Pressure gauge (PS5-60-PG-8902F)needle pointing below zero, may need to replace | EPS UNATRAC | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Originated |  |  | 2025-07-14T06:01:44.090 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001708 | PS5-60-UZ-8900F |  | B | M | 4.4:Pressure gauge (PS5-60-PG-8905F)needle pointing below zero, may need to replace | EPS UNATRAC | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Originated |  |  | 2025-07-14T06:03:30.233 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001709 | PS5-60-UZ-8900G |  | C | M | 4:It was observed that the insulation is not properly sealed | EPS UNATRAC | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G |  | Originated |  |  | 2025-07-14T06:08:53.757 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001710 | PS5-60-UZ-8900G |  | B | M | 4.1:Pressure gauge (PS5-60-PG-8905G) needle pointing positive, may need to replace | EPS UNATRAC | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G |  | Originated |  |  | 2025-07-14T06:10:15.750 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001711 | PS5-60-UZ-8900G |  | B | M | 4.2:Pressure gauge (PS5-60-PG-8902G) needle pointing below zero, may need to replace | EPS UNATRAC | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G |  | Originated |  |  | 2025-07-14T06:11:35.363 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001712 | PS5-60-UZ-8900G |  | B | M | 4.3:Pressure gauge (PS5-60-PG-8903G)needle pointing below zero, may need to replace | EPS UNATRAC | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G |  | Originated |  |  | 2025-07-14T06:13:52.117 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001713 | PS5-61-IU-0001F |  | C | M | 4:Received Material with tag no. PS5-61-BE-0006A, As per PL PS5-61-IU-0001F. | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-07-14T06:22:27.750 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001714 | PS5-61-IU-0001F |  | C | M | 4.1:Transportation packing (Between radiators) were misplaced/ fallen down resulting damage on the edges of the radiators (May be severe) | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-07-14T06:23:56.433 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001715 | PS5-61-IU-0001G |  | C | M | 4:Received Material with tag no. PS5-61-BE-0007A, As per PL PS5-61-IU-0001G. | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-14T06:28:01.390 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001716 | PS5-61-IU-0001G |  | C | M | 4.1:Transportation packing (Between radiators) were misplaced/ fallen down resulting damage on the edges of the radiators (May be severe) | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-14T06:29:42.953 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001717 | PS5-61-IU-0001G |  | C | M | 4.2:Transportation packing (Between radiators) were misplaced/ fallen down resulting damage on the edges of the radiators (May be severe) | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-14T06:30:43.077 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001722 | PS5-61-IU-0001G |  | C | M | 4.7:Transportation packing (Between radiators) were misplaced/ fallen down resulting damage on the edges of the radiators (May be severe) | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-14T06:35:19.930 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001724 | PS5-71-UZ-6400 |  | C | M | 4.1:Found insulation not properly sealed. | EPS VENDOR | PS5-71-08 - CFO Pre-Pressure Modules |  | Originated |  |  | 2025-07-16T05:38:05.490 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001725 | PS5-71-UZ-6400 |  | B | M | 4.2:Pressure gauge (PS5-71-PG-6401) needle pointing below zero, may need to replace | EPS VENDOR | PS5-71-08 - CFO Pre-Pressure Modules |  | Originated |  |  | 2025-07-16T05:39:45.773 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001726 | PS5-71-UZ-6400 |  | B | M | 4.3:Pressure gauge (PS5-71-PG-6417)needle pointing below zero, may need to replace | EPS VENDOR | PS5-71-08 - CFO Pre-Pressure Modules |  | Originated |  |  | 2025-07-16T05:41:07.977 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001727 | PS5-71-UZ-6400 |  | B | M | 4.4:Pressure gauge (PS5-71-PG-6416)needle pointing below zero, may need to replace | EPS VENDOR | PS5-71-08 - CFO Pre-Pressure Modules |  | Originated |  |  | 2025-07-16T05:43:02.690 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001728 | PS5-71-UZ-6400 |  | B | M | 4.5:Pressure gauge (PS5-71-PG-6414)needle pointing below zero, may need to replace | EPS VENDOR | PS5-71-08 - CFO Pre-Pressure Modules |  | Originated |  |  | 2025-07-16T05:43:59.540 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001729 | PS5-71-UZ-6400 |  | C | M | 4.6:One loose flame arrester delivered (Overage) without bolts, nuts, and gaskets | EPS VENDOR | PS5-71-08 - CFO Pre-Pressure Modules |  | Originated |  |  | 2025-07-16T05:45:14.377 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001730 | PS5-60-UR-8200A |  | B | M | 4:Pressure gauge (PS5-60-PI-8207A, PS5-60-PI-8205A, PS5-60-PI-8206A, PS5-60-PI-8208A)needle pointing positive reading, may need to replace | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-07-16T05:48:43.290 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001731 | PS5-60-UR-8200F |  | B | M | 4:Pressure gauge (PS5-60-TI-8308F, PS5-60-TI-8306F, PS5-60-PI-8208F, PS5-60-PI-8206F)needle pointing positive reading, may need to replace | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  |  | 2025-07-16T05:51:23.540 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001732 | PS5-60-UR-8200E |  | B | M | 4:Pressure gauge (PS5-60-PI-8207E, PS5-60-PI-8208E, PS5-60-PI-8206E, PS5-60-PI-8205E) needle pointing positive reading, may need to replace | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  |  | 2025-07-16T05:53:34.177 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001733 | PS5-60-UR-8200D |  | B | M | 4:Pressure gauge (PS5-60-PI-8207D, PS5-60-PI-8205D, PS5-60-PI-8208D, PS5-60-PI-8206D)needle pointing positive reading, may need to replace | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-07-16T05:56:09.177 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001734 | PS5-60-UR-8200C |  | B | M | 4:Pressure gauge (PS5-60-PI-8207C, PS5-60-TI-8306C, PS5-60-PI-8206C, PS5-60-PI-8208C)needle pointing positive reading, may need to replace | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  |  | 2025-07-16T05:58:18.803 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001735 | PS5-60-UR-8200B |  | B | M | 4:Pressure gauge (PS5-60-PI-8207B,PS5-60-PI-8205B, PS5-60-PI-8206B, PS5-60-PI-8208B) needle pointing positive reading, may need to replace | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2025-07-16T06:02:18.753 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001736 | PS5-60-UR-8300C |  | A | E | 4:"Temperature gauge found broken (PS5-60-TI-8308C)" | EPS UNATRAC | PS5-60-37 - Injector Tip Cooling Module C |  | Originated |  |  | 2025-07-16T06:05:29.730 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001737 | PS5-60-UR-8300C |  | B | E | 4.1:Tube support found missing during inspection | EPS UNATRAC | PS5-60-37 - Injector Tip Cooling Module C |  | Originated |  |  | 2025-07-16T06:06:40.950 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001738 | PS5-60-UR-8300C |  | A | M | 4.2:Found plate removed due to not proper welding. | EPS UNATRAC | PS5-60-37 - Injector Tip Cooling Module C |  | Originated |  |  | 2025-07-16T06:08:09.620 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001739 | PS5-60-UR-8300F |  | B | M | 4:Found top plate is damaged | EPS UNATRAC | PS5-60-40 - Injector Tip Cooling Module F |  | Originated |  |  | 2025-07-16T06:11:19.610 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001740 | PS5-60-UR-8300D |  | A | M | 4:Found plate removed due to not proper welding. | EPS UNATRAC | PS5-60-38 - Injector Tip Cooling Module D |  | Originated |  |  | 2025-07-16T06:13:38.347 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001741 | PS5-60-UR-8300D |  | A | M | 4.1:Cracks found on end plate welding. One of the end plate dittached and fallen down. | EPS UNATRAC | PS5-60-38 - Injector Tip Cooling Module D |  | Originated |  |  | 2025-07-16T06:14:40.080 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001742 | PS5-60-UR-8300D |  | B | M | 4.2:Found damage on top plate damaged | EPS UNATRAC | PS5-60-38 - Injector Tip Cooling Module D |  | Originated |  |  | 2025-07-16T06:15:49.750 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001743 | PS5-60-UR-8300D |  | C | M | 4.3:"Detials not available so not checked " | EPS UNATRAC | PS5-60-38 - Injector Tip Cooling Module D |  | Originated |  |  | 2025-07-16T06:16:43.457 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001744 | PS5-60-LA-0002A |  | B | M | 4:Found panel base damage VMS system cabinet 1 | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  |  | 2025-07-16T06:18:57.170 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001746 | PS5-60-EA-2300A |  | A | M | 4.1:Found rust on fan supports due to improper painting | EPS UNATRAC | PS5-60-72 - Engine C Cooling system |  | Originated |  |  | 2025-07-17T13:31:20.050 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001747 | PS5-60-EA-2300A |  | C | M | 4.2:"Rust found on outside angle of Luve remote radiator PS5-60-EA-2300A" | EPS UNATRAC | PS5-60-72 - Engine C Cooling system |  | Originated |  |  | 2025-07-17T13:32:36.507 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001748 | PS5-60-EA-2300B |  | A | M | 4:Found rust on fan supports due to improper painting | EPS UNATRAC | PS5-60-72 - Engine C Cooling system |  | Originated |  |  | 2025-07-17T13:35:11.533 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001749 | PS5-60-EA-2300B |  | C | M | 4.1:"Rust found on outside angle of Luve remote radiator PS5-60-EA-2300B" | EPS UNATRAC | PS5-60-72 - Engine C Cooling system |  | Originated |  |  | 2025-07-17T13:36:16.247 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001750 | PS5-60-SEA-0001 |  | C | M | 4:Gas Detection Panel PS5-60-SEA-001 arrived as per the packing list, while PS-60-GB-0003 arrived without packing list/SRN and is missing the battery. | EPS VENDOR | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room |  | Originated |  |  | 2025-07-17T13:39:00.383 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001751 | PS5-60-UR-8300G |  | A | M | 4:Tube got severe bend due to the damage of top plate touching (PS5-60-EA-21200G) | EPS UNATRAC | PS5-60-41 - Injector Tip Cooling Module G |  | Originated |  |  | 2025-07-17T13:41:54.393 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001752 | PS5-60-UR-8300G |  | A | M | 4.1:Tube got severe bend due to the damage of top plate touching (PS 5-60-EA-21100G) | EPS UNATRAC | PS5-60-41 - Injector Tip Cooling Module G |  | Originated |  |  | 2025-07-17T13:42:58.570 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001753 | PS5-60-UR-8300G |  | A | M | 4.2:Stitch / tack welding broken and end plate displaced from it's location PS5-60-EA-21200G | EPS UNATRAC | PS5-60-41 - Injector Tip Cooling Module G |  | Originated |  |  | 2025-07-17T13:44:18.687 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001754 | PS5-60-UR-8300G |  | A | M | 4.3:As per packing list, quantity of seal O-rings is 900, but received only 895 | EPS UNATRAC | PS5-60-41 - Injector Tip Cooling Module G |  | Originated |  |  | 2025-07-17T13:45:45.857 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001755 | PS5-60-UR-8200G |  | A | M | 4:As per packing list, 7 Senior Flexonics but received only 5 nos. | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-17T13:51:46.210 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001756 | PS5-60-UR-8200G |  | C | M | 4.1:"No details mentioned in the packing list SO NOT CHECKED (CAT Special tools)""No details mentioned in the packing list SO NOT CHECKED (CAT Special tools)" | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-17T13:54:51.810 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001757 | PS5-60-UR-8200G |  | C | M | 4.2:Paint damage found on oil breather line pipe during inspection | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-17T13:56:39.070 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001758 | PS5-60-UR-8200G |  | C | M | 4.3:Proper details not available for the materials in Colli no:33 | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-17T13:58:13.040 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001759 | PS5-60-UR-8200G |  | A | M | 4.4:During inspection, a leakage of glycerin was found at the pressure gauge. | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  |  | 2025-07-17T13:59:48.240 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-001760 | PS5-61-IU-0001D |  | B | M | 4:Signs of leakage were observed in three different locations | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-07-17T14:24:21.180 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-001877 | PS5-71-IE-0002 |  | A | E | SFU bar neutral to be tighten | EITS | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  |  | 2025-08-25T04:58:01.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-001915 | PS5-61-IU-0001B |  | B | M | 4:Base plate of the transformer found damage on two foots after opening the wooden packing box. This might have happened due to the improper packing of the equipmentfromfactory | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  |  | 2025-09-08T08:04:01.633 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-001919 | PS5-83-EHO-0001A |  | A | M | 4:BOLTS AND NUTS FOR LIGHTING SUPPORT ARE MISING | EPS VENDOR | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-09-09T12:55:40.873 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001920 | PS5-83-EHO-0001A |  | A | M | 4.1:BOLT FOR HAND RAIL BASE PLATE ARE MISSING | EPS VENDOR | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-09-09T12:58:17.260 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001921 | PS5-83-EHO-0001A |  | B | M | 4.2: MINOR DAMAGE OBSERVED ON HVAC COMPRESSOR FINS | EPS VENDOR | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-09-09T13:00:06.060 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001922 | PS5-83-EHO-0001A |  | A | M | 4.3:MAJOR DAMAGE (Might happened during transportation) ON THE MAINTENANCE DOOR AND THE CORNER STRUCTURE OF THE CONTAINER. Door could't open due to this. Need to replace these.Also lot of paint damages on the container. | EPS VENDOR | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-09-09T13:01:20.027 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001923 | PS5-83-EHO-0001A |  | B | M | 4.4: BOLTS DAMAGED IN THE SIDE BOTTOM PORTION OF THE CONTAINER (Transportation damage) | EPS VENDOR | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-09-09T13:02:24.773 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001924 | PS5-83-EHO-0001A |  | B | M | 4.5:E-HOUSE CONTAINER OUT SIDE PAINT DAMAGE | EPS VENDOR | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-09-09T13:04:01.700 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001925 | PS5-83-EHO-0001A |  | A | M | 4.6:LADDER CONNECTING PLATE BOLTS AND NUTS MISING | EPS VENDOR | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-09-09T13:05:33.560 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001926 | PS5-83-EHO-0001A |  | B | M | 4.7:DOOR CAN NOT BE OPEN FROM OUTSIDE DUE TO THE IMPROPER FIXING OF THE HANDLE. NEED TO RECTIFY OR REPLACE BY VENDOR | EPS VENDOR | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  |  | 2025-09-09T13:06:52.537 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001927 | PS5-83-EHO-0001B |  | A | M | 4:L CLAMP BOLT (HAND RAIL CONNECTION) MISSING | EPS VENDOR | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-09-09T13:33:59.223 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001944 | PS5-83-EHO-0001B |  | B | M | 4.1: BOLTS DAMAGED IN THE SIDE BOTTOM PORTION OF THE CONTAINER (Transportation damage) | EPS VENDOR | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-09-12T12:58:46.700 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001945 | PS5-83-EHO-0001B |  | A | M | 4.2:WALLMAX PIPE INLET MISSING | EPS VENDOR | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-09-12T13:02:27.813 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001946 | PS5-83-EHO-0001B |  | A | M | 4.3:WALLMAX PIPE CABLE ENTRY MISSING | EPS VENDOR | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-09-12T13:04:45.137 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001947 | PS5-83-EHO-0001B |  | C | M | 4.4:DOOR CAN NOT BE OPEN FROM OUTSIDE DUE TO THE IMPROPER FIXING OF THE HANDLE. NEED TO RECTIFY OR REPLACE BY VENDOR | EPS VENDOR | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-09-12T13:07:46.543 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001948 | PS5-83-EHO-0001B |  | B | M | 4.5:E-HOUSE CONTAINER OUT SIDE PAINT DAMAGE | EPS VENDOR | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-09-12T13:10:24.867 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001949 | PS5-83-EHO-0001B |  | A | M | 4.6:LADDER CONNECTING PLATE BOLTS NUTS MISING | EPS VENDOR | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-09-12T13:13:37.657 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001950 | PS5-83-EHO-0001C |  | A | M | 4:BOLT FOR HAND RAIL BASE PLATE ARE MISSING | EPS VENDOR | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-09-12T13:17:59.283 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001951 | PS5-83-EHO-0001C |  | A | M | 4.1:TOE GUARD CONNECTING BOLTS ARE MISSING | EPS VENDOR | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-09-12T13:21:29.380 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001952 | PS5-83-EHO-0001C |  | A | M | 4.2:L CLAMP (HAND RAIL CONNECTION) MISSING | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-09-12T13:23:28.763 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001953 | PS5-83-EHO-0001C |  | A | M | 4.3:L CLAMP BOLT (HAND RAIL CONNECTION) MISSING | EPS VENDOR | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-09-12T13:25:18.717 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001954 | PS5-83-EHO-0001C |  | B | M | 4.4: BOLTS DAMAGED IN THE SIDE BOTTOM PORTION OF THE CONTAINER (Transportation damage) | EPS VENDOR | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-09-12T13:27:10.227 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001956 | PS5-83-EHO-0001C |  | B | M | 4.6:E HOUSE CONTAINER DAMAGE AND PAINT DAMAGE | EPS VENDOR | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-09-12T13:28:58.410 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001957 | PS5-83-EHO-0001C |  | A | M | 4.7:LADDER CONNECTING PLATE BOLTS NUTS MISING | EPS VENDOR | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-09-12T13:30:09.447 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001959 | PS5-71-PA-3300B |  | C | M | 4:The accumulator’s support was found on the floor during inspection. | EPS VENDOR | PS5-71-05 - CFO Transfer Pump A/B |  | Originated |  |  | 2025-09-22T10:37:15.367 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001960 | PS5-71-PA-3300B |  | C | M | 4.1:The tube support was found on the floor during inspection. | EPS VENDOR | PS5-71-05 - CFO Transfer Pump A/B |  | Originated |  |  | 2025-09-22T10:43:22.050 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001962 | PS5-71-PA-3400B |  | A | M | 4: Signs of leakage were observed in one location. | EPS VENDOR | PS5-71-13 - CFO Service Pump A/B |  | Originated |  |  | 2025-09-22T11:02:01.957 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-001963 | PS5-61-IU-0001D |  | B | E | Once opened the box, found the plastic cover containing bolts was not sealed. Only 3(out of 62) bolts were there inside the plastic cover-59nos (M10 X 38 stainless steel) bolts/nuts/ washersaremissing | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  |  | 2025-09-23T08:06:40.000 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-002335 | PS5-74-VA-1100 |  | C | M | 4:Found paint damaged at ladder,davit and platform angle | EPS VENDOR | PS5-74-03 - Nitrogen Receiver |  | Originated |  |  | 2025-10-28T12:19:55.440 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002336 | PS5-61-IK-0001 |  | B | E | PS005-E&I-ALL-PL-2439 - ALL CABLE COMPARTMENTS: LABELS FROM OUTGOING FEEDERS SHALL BE BLACK/BROWN/GREY COLOURS | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated | PS005-E&I-ALL-PL-2439 | Refer to Job Card BUILD-COW-0009 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone A
PL-002340 | PS5-61-IJ-0010 |  | B | E | PS005-E&I-ALL-PL-2451 - ALL CUBICLES: FINAL PROTECTION SETTINGS ARE NOT SET. | EITS | PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010) |  | Originated | PS005-E&I-ALL-PL-2451 | Refer to Job Card BUILD-COW-0011 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone G
PL-002341 | PS5-61-IJ-0011 |  | B | E | PS005-E&I-ALL-PL-2452 - ALL CUBICLES: FINAL PROTECTION SETTINGS ARE NOT SET. | EITS | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated | PS005-E&I-ALL-PL-2452 | Refer to Job Card BUILD-COW-0011 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone G
PL-002344 | PS5-61-IK-0001 |  | B | E | PS005-E&I-ALL-PL-2440 - ALL DRAWERS: FINAL PROTECTION SETTINGS NOT SET COMPLETELY IN DRAWERS | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated | PS005-E&I-ALL-PL-2440 | Refer to Job Card BUILD-COW-0017 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone A
PL-002347 | PS5-61-IJ-0001 |  | B | E | PS005-E&I-ALL-PL-2448 - B04 Cell : Missing 1 set of Mechanical Key Lock = 2 CAMLOCK + 1 Key + 2 Spacer with serial number PH3212 (diameter rear side 10mm) was damage | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated | PS005-E&I-ALL-PL-2448 | Refer to Job Card BUILD-COW-0019 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone D
PL-002349 | PS5-08-15CB-1001 |  | A | T | PS005-E&I-M4-PL-2586 - Flood light to be tested in tanzania and to be included in the ISMS SAT. | EITS | PS5-08-15 - Security Data Network (SII SP3 SEC) |  | Originated | PS005-E&I-M4-PL-2586 | Will be part of SAT procedure UT-MID-60-SSF1-178660 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone C
PL-002350 | PS5-08-85DC-1007 |  | A | T | PS005-E&I-ETC-PL-2340 - Battery room door contact TBC if Atex required | EITS | PS5-08-85 - Access Control, POB & e-Mustering |  | Originated | PS005-E&I-ETC-PL-2340 | Refer to Job Card BUILD-COW-0021 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone F
PL-002355 | PS5-08-35CB-1001-CA12 |  | A | T | PS005-E&I-M6-PL-2584 - Cable not terminator due to panel PNC-001 not install yet | EITS | PS5-08-35 - Optical Transport Network |  | Originated | PS005-E&I-M6-PL-2584 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone C
PL-002361 | PS5-09-ACU-0007A-CD01 |  | A | E | PS005-E&I-M4-PL-2366 - Cable One Side Termination (COW) | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated | PS005-E&I-M4-PL-2366 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone A
PL-002362 | PS5-08-11CB-1001-CX21 |  | A | T | PS005-E&I-M4-PL-2260 - Cable one side termination /cow | EITS | PS5-08-11 - Corporate LAN (SIE) |  | Originated | PS005-E&I-M4-PL-2260 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:24:36.233 | Thao-my, Alexandre | PS5 - Milestone C
PL-002363 | PS5-08-11CB-1001-CX22 |  | A | T | PS005-E&I-M4-PL-2261 - Cable one side termination /cow | EITS | PS5-08-11 - Corporate LAN (SIE) |  | Originated | PS005-E&I-M4-PL-2261 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002364 | PS5-08-11CB-1001-CX23 |  | A | T | PS005-E&I-M4-PL-2262 - Cable one side termination /cow | EITS | PS5-08-11 - Corporate LAN (SIE) |  | Originated | PS005-E&I-M4-PL-2262 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002365 | PS5-06-GB-0001A-CS01 |  | A | E | PS005-E&I-ALL-PL-1584 - Cable one side termination due to battery not install here (COW) | EITS | PS5-06-01 - AC UPS - EITS Building |  | Completed | PS005-E&I-ALL-PL-1584 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002366 | PS5-06-GB-0001A-CS03 |  | A | E | PS005-E&I-ALL-PL-1587 - Cable one side termination due to battery not install here (COW) | EITS | PS5-06-01 - AC UPS - EITS Building |  | Completed | PS005-E&I-ALL-PL-1587 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002367 | PS5-06-GB-0001A-CS02 |  | A | E | PS005-E&I-ALL-PL-1590 - Cable one side termination due to battery not install here (COW) | EITS | PS5-06-01 - AC UPS - EITS Building |  | Completed | PS005-E&I-ALL-PL-1590 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002368 | PS5-06-GB-0001A-CS04 |  | A | E | PS005-E&I-ALL-PL-1593 - Cable one side termination due to battery not install here (COW) | EITS | PS5-06-01 - AC UPS - EITS Building |  | Completed | PS005-E&I-ALL-PL-1593 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002369 | PS5-06-GB-0001B-CS01 |  | A | E | PS005-E&I-ALL-PL-1895 - Cable one side termination due to battery not install here (COW) | EITS | PS5-06-01 - AC UPS - EITS Building |  | Completed | PS005-E&I-ALL-PL-1895 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002370 | PS5-06-GB-0001B-CS03 |  | A | E | PS005-E&I-ALL-PL-1898 - Cable one side termination due to battery not install here (COW) | EITS | PS5-06-01 - AC UPS - EITS Building |  | Completed | PS005-E&I-ALL-PL-1898 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002371 | PS5-06-GB-0001B-CS02 |  | A | E | PS005-E&I-ALL-PL-1901 - Cable one side termination due to battery not install here (COW) | EITS | PS5-06-01 - AC UPS - EITS Building |  | Completed | PS005-E&I-ALL-PL-1901 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002372 | PS5-06-GB-0001B-CS04 |  | A | E | PS005-E&I-ALL-PL-1904 - Cable one side termination due to battery not install here (COW) | EITS | PS5-06-01 - AC UPS - EITS Building |  | Completed | PS005-E&I-ALL-PL-1904 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002373 | PS5-61-IE-0101-CA01 |  | A | T | PS005-E&I-M3-PL-2353 - Cable one side termination due to ECS Work station n/a (cow) | EITS | PS5-61-08 - Electrical Control System |  | Originated | PS005-E&I-M3-PL-2353 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002374 | PS5-61-IE-0101-CA02 |  | A | T | PS005-E&I-M3-PL-2354 - Cable one side termination due to ECS Work station n/a (cow) | EITS | PS5-61-08 - Electrical Control System |  | Originated | PS005-E&I-M3-PL-2354 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002375 | PS5-61-IE-0101-CA03 |  | A | T | PS005-E&I-M3-PL-2355 - Cable one side termination due to ECS Work station n/a (cow) | EITS | PS5-61-08 - Electrical Control System |  | Originated | PS005-E&I-M3-PL-2355 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002376 | PS5-04-PNC-0001-CS02 |  | A | E | PS005-E&I-M4-PL-1743 - Cable one side termination due to other side panel not available (COW) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated | PS005-E&I-M4-PL-1743 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002378 | PS5-83-OB-0001 |  | A | B | PS005-E&I-M3-PL-2494 - Cable Still Coiled o top ECS Panel and 15CB Panel | EITS | PS5-83-01 - EITS Building |  | Originated | PS005-E&I-M3-PL-2494 | Refer to Job Card BUILD-COW-0308 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002388 | PS5-08-23LA-1001-CV01 |  | A | T | PS005-E&I-ALL-PL-2558 - Coaxial cable to be tested | EITS | PS5-08-23 - VHF Trunk Radio System |  | Originated | PS005-E&I-ALL-PL-2558 | Refer to Job Card BUILD-COW-0105 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone F
PL-002389 | PS5-61-IJ-0001 |  | A | E | PS005-E&I-ALL-PL-2449 - CT Box Not installed and not inspected. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Completed | PS005-E&I-ALL-PL-2449 | Follow Building Installation Procedures at SITE TZ-MID-63-SSF1-230003 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone D
PL-002408 | PS5-06-IER-0001A |  | A | E | PS005-E&I-ALL-PL-2587 - Ex stoper plug to be installed for spare hole MCCB Box A | EITS | PS5-06-01 - AC UPS - EITS Building |  | Originated | PS005-E&I-ALL-PL-2587 | Refer to Job Card BUILD-COW-0134 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002410 | PS5-06-IER-0001B |  | A | E | PS005-E&I-ALL-PL-2588 - Ex stoper plug to be installed for spare hole MCCB Box B | EITS | PS5-06-01 - AC UPS - EITS Building |  | Originated | PS005-E&I-ALL-PL-2588 | Refer to Job Card BUILD-COW-0134 | 2025-11-07T06:30:22.000 | Thao-my, Alexandre | PS5 - Milestone A
PL-002413 | PS5-61-IK-0001 |  | B | E | PS005-E&I-ALL-PL-2441 - INCOMERS: INCOMER A, B AND C MCT CONFIGURATION DOES NOT FIT THE FIELD CABLE SCHEDULE PROVIDED BY EPS IN DESIGN DOSSIER | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated | PS005-E&I-ALL-PL-2441 | Refer to Job Card BUILD-COW-0148 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002414 | PS5-61-JY-0001 |  | C | E | PS005-E&I-ALL-PL-2454 - Maintenance trolley for BlokSet Air Circuit Breakers is missing | EITS | PS5-78-01 - Lifting and handling equipment | 2026-01-19T16:23:38.000 | Closed | PS005-E&I-ALL-PL-2454 | Delivery of the trolley | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone E
PL-002422 | PS5-04-PSC-0001 |  | A | I | PS005-E&I-M4-PL-0357 - Missing component BP3-68FD-03, BP468FD-04 | EITS | PS5-04-04 - 33kV PCS System |  | Originated | PS005-E&I-M4-PL-0357 | Refer to Job Card BUILD-COW-0026 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002423 | PS5-09-IES-0001 |  | C | E | PS005-HVA-ETC-PL-2254 - No access to operate Emergency stop | EITS | PS5-09-05 - HVAC for EITS Building | 2026-04-23T13:39:23.000 | Closed | PS005-HVA-ETC-PL-2254 | Punch to be closed as per TQR - SSF1-TQR-000136 which is accepted by CPY, so punch no more applicable | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002430 | PS5-09-ACU-0007A |  | A | H | PS005-E&I-M6-PL-2308 - One side cable coil /cow | EITS | PS5-09-05 - HVAC for EITS Building | 2026-03-25T16:03:27.000 | Closed | PS005-E&I-M6-PL-2308 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002431 | PS5-09-ACU-0007B |  | A | H | PS005-E&I-M6-PL-2309 - One side cable coil /cow | EITS | PS5-09-05 - HVAC for EITS Building | 2026-03-25T16:03:45.000 | Closed | PS005-E&I-M6-PL-2309 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002432 | PS5-04-PNC-0001-CA40 |  | A | T | PS005-E&I-M4-PL-2039 - One side termination | EITS | PS5-04-03 - 33kV ICSS System |  | Originated | PS005-E&I-M4-PL-2039 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002433 | PS5-04-PNC-0001-CA55 |  | A | T | PS005-E&I-M4-PL-2041 - One side termination | EITS | PS5-04-03 - 33kV ICSS System |  | Originated | PS005-E&I-M4-PL-2041 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002434 | PS5-04-PNC-0001-CA56 |  | A | T | PS005-E&I-M4-PL-2043 - One side termination | EITS | PS5-04-03 - 33kV ICSS System |  | Originated | PS005-E&I-M4-PL-2043 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002435 | PS5-04-PNC-0001-CA58 |  | A | T | PS005-E&I-M4-PL-2045 - One side termination | EITS | PS5-04-03 - 33kV ICSS System |  | Originated | PS005-E&I-M4-PL-2045 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002436 | PS5-04-PNC-0001-CA59 |  | A | T | PS005-E&I-M4-PL-2047 - One side termination | EITS | PS5-04-03 - 33kV ICSS System |  | Originated | PS005-E&I-M4-PL-2047 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002437 | PS5-04-PNC-0001-CA61 |  | A | T | PS005-E&I-M4-PL-2049 - One side termination | EITS | PS5-04-03 - 33kV ICSS System |  | Originated | PS005-E&I-M4-PL-2049 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002438 | PS5-04-PNC-0001-CA62 |  | A | T | PS005-E&I-M4-PL-2051 - One side termination | EITS | PS5-04-03 - 33kV ICSS System |  | Originated | PS005-E&I-M4-PL-2051 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002439 | PS5-04-PNC-0001-CA63 |  | A | T | PS005-E&I-M4-PL-2053 - One side termination | EITS | PS5-04-03 - 33kV ICSS System |  | Originated | PS005-E&I-M4-PL-2053 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002440 | PS5-04-PNC-0001-CA64 |  | A | T | PS005-E&I-M4-PL-2055 - One side termination | EITS | PS5-04-03 - 33kV ICSS System |  | Originated | PS005-E&I-M4-PL-2055 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002441 | PS5-04-PNC-0001-CA69 |  | A | T | PS005-E&I-M4-PL-2057 - One side termination | EITS | PS5-04-03 - 33kV ICSS System |  | Originated | PS005-E&I-M4-PL-2057 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002442 | PS5-04-PNC-0001-CA70 |  | A | T | PS005-E&I-M4-PL-2059 - One side termination | EITS | PS5-04-03 - 33kV ICSS System |  | Originated | PS005-E&I-M4-PL-2059 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002443 | PS5-04-PNC-0001-CA71 |  | A | T | PS005-E&I-M4-PL-2061 - One side termination | EITS | PS5-04-03 - 33kV ICSS System |  | Originated | PS005-E&I-M4-PL-2061 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002444 | PS5-04-PNC-0001-CA72 |  | A | T | PS005-E&I-M4-PL-2063 - One side termination | EITS | PS5-04-03 - 33kV ICSS System |  | Originated | PS005-E&I-M4-PL-2063 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002445 | PS5-04-PNC-0001-CA73 |  | A | T | PS005-E&I-M4-PL-2065 - One side termination | EITS | PS5-04-03 - 33kV ICSS System |  | Originated | PS005-E&I-M4-PL-2065 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002446 | PS5-04-PNC-0001-CS03 |  | A | E | PS005-E&I-M4-PL-2382 - One side termination due to panel PNC COW | EITS | PS5-04-03 - 33kV ICSS System |  | Originated | PS005-E&I-M4-PL-2382 | Refer to Job Card BUILD-COW-0102 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002448 | PS5-01-LA-0001-CL01 |  | A | E | PS005-E&I-ALL-PL-2589 - Power cable HIPPS Cabinet in General Batch 2 Should be replaced by Fire resistance (Orange cable) | EITS | PS5-0H-01 - HIPPS |  | Originated | PS005-E&I-ALL-PL-2589 | Refer to Job Card BUILD-COW-0083 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone H
PL-002449 | PS5-01-LA-0001-CL02 |  | A | E | PS005-E&I-ALL-PL-2589 - Power cable HIPPS Cabinet in General Batch 2 Should be replaced by Fire resistance (Orange cable) | EITS | PS5-0H-01 - HIPPS |  | Originated | PS005-E&I-ALL-PL-2589 | Refer to Job Card BUILD-COW-0083 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone H
PL-002476 | PS5-61-IK-0001 |  | A | E | PS005-E&I-ALL-PL-2442 - Ring Ethernet cat6 Cables that are extended with coupler to be replaced by longer ones, and should pass through suitable cable opening. | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated | PS005-E&I-ALL-PL-2442 | Refer to Job Card BUILD-COW-0200 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone A
PL-002477 | PS5-02-SGF-0010 |  | C | S | PS005-E&I-ALL-PL-2453 - Safety Kit that are supplied and installed in the substaion have some missing contents, to be check to match Doc. No. UT-MID-60-SSF1-120001 | EITS | PS5-02-01 - Miscellaneous Safety equipment | 2025-12-05T10:21:02.000 | Closed | PS005-E&I-ALL-PL-2453 | Refer to Job Card BUILD-COW-0143 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone H
PL-002484 | PS5-01-LA-0001-CC04 |  | A | I | PS005-E&I-M6-PL-1501 - Termination need to completed in drawing not mention for terminal block AN terminal number in panel ( PS5-01-LA-0001) | EITS | PS5-0H-01 - HIPPS |  | Originated | PS005-E&I-M6-PL-1501 | Refer to Job Card BUILD-COW-0082 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone H
PL-002490 | PS5-61-IE-0002-CA07 |  | A | T | PS005-E&I-M2-PL-1347 - Update cable schedule and termination drawing to be confirm by enginnering | EITS | PS5-61-08 - Electrical Control System | 2026-05-19T15:39:49.000 | Closed | PS005-E&I-M2-PL-1347 | Document update | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002491 | PS5-61-IE-0002-CA08 |  | A | T | PS005-E&I-M2-PL-1349 - Update cable schedule and termination drawing to be confirm by enginnering | EITS | PS5-61-08 - Electrical Control System | 2026-05-19T15:40:09.000 | Closed | PS005-E&I-M2-PL-1349 | Document update | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002492 | PS5-61-IE-0002-CA09 |  | A | T | PS005-E&I-M2-PL-1351 - Update cable schedule and termination drawing to be confirm by enginnering | EITS | PS5-61-08 - Electrical Control System | 2026-05-19T15:40:29.000 | Closed | PS005-E&I-M2-PL-1351 | Document update | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002493 | PS5-61-IE-0002-CA10 |  | A | T | PS005-E&I-M2-PL-1353 - Update cable schedule and termination drawing to be confirm by enginnering | EITS | PS5-61-08 - Electrical Control System | 2026-05-19T15:40:48.000 | Closed | PS005-E&I-M2-PL-1353 | Document update | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002494 | PS5-61-IE-0002-CA11 |  | A | T | PS005-E&I-M2-PL-1355 - Update cable schedule and termination drawing to be confirm by enginnering | EITS | PS5-61-08 - Electrical Control System | 2026-05-19T15:41:05.000 | Closed | PS005-E&I-M2-PL-1355 | Document update | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002495 | PS5-61-IE-0002-CA12 |  | A | T | PS005-E&I-M2-PL-1357 - Update cable schedule and termination drawing to be confirm by enginnering | EITS | PS5-61-08 - Electrical Control System | 2026-05-19T15:41:25.000 | Closed | PS005-E&I-M2-PL-1357 | Document update | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002496 | PS5-08-13CB-1001 |  | A | T | PS005-E&I-M1-PL-2325 - Utilities power not tested, to be tested in tanzania | EITS | PS5-08-13 - Safety Data Network (SII SP3 SAF) |  | Originated | PS005-E&I-M1-PL-2325 | Refer to Job Card BUILD-COW-0242 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002497 | PS5-08-11CB-1001 |  | A | T | PS005-E&I-M1-PL-2326 - Utilities power not tested, to be tested in tanzania | EITS | PS5-08-11 - Corporate LAN (SIE) |  | Originated | PS005-E&I-M1-PL-2326 | Refer to Job Card BUILD-COW-0242 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002498 | PS5-08-35CB-1001 |  | A | T | PS005-E&I-M1-PL-2327 - Utilities power not tested, to be tested in tanzania | EITS | PS5-08-35 - Optical Transport Network |  | Originated | PS005-E&I-M1-PL-2327 | Refer to Job Card BUILD-COW-0242 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002499 | PS5-08-15CB-1001 |  | A | T | PS005-E&I-M1-PL-2328 - Utilities power not tested, to be tested in tanzania | EITS | PS5-08-15 - Security Data Network (SII SP3 SEC) |  | Originated | PS005-E&I-M1-PL-2328 | Refer to Job Card BUILD-COW-0242 | 2025-11-07T06:30:22.023 | Thao-my, Alexandre | PS5 - Milestone C
PL-002505 | PS5-25-MOV-0012 |  | A | P | Valve damaged by the CPP contractor, It shall be repaired or replaced. | CPP AGI | PS5-25-07 - Export Pipeline Pig Launcher |  | Originated |  | CPP contractor shall repair or Replace the MOV. | 2025-11-07T11:56:36.000 | peela, raja | PS5 - Milestone H
PL-002580 | PS5-74-VA-1100 |  | C | M | 4.1:Handrail bend due to mishandling | EPS VENDOR | PS5-74-03 - Nitrogen Receiver |  | Originated |  |  | 2025-11-21T13:49:52.377 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002581 | PS5-74-VA-1100 |  | B | M | 4.2:As per packing list materials are ok. As per drawing we need more bolts. Which is not appearing in the packing list and didn't receive. (Bolt M16x45 w/nut & washer =20 nos and Bolt M12x45 w/nut & washer = 20 nos) | EPS VENDOR | PS5-74-03 - Nitrogen Receiver |  | Originated |  |  | 2025-11-21T13:54:03.290 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002589 | PS5-60-TR-4400 |  | B | M | 4.1:The vertical ladder top cage hoop farication is not correct. Required mirror emage of the present fabricated cage hoop | EPS UNATRAC | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump |  | Originated |  |  | 2025-11-25T05:15:54.090 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-002590 | PS5-01-TR-4300 |  | A | M | 4:During inspection, we found the 2" pipe weld at the bottom of the tank (Branch weld joint) is totally broken | EPS VENDOR | PS5-01-05 - Foam Skid |  | Originated |  |  | 2025-11-25T05:27:35.930 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002591 | PS5-01-TR-4300 |  | A | M | 4.1:The PS4-01-UV-8700 skid was received here instead of the PS5 skid to be replaced with correct one | EPS VENDOR | PS5-01-05 - Foam Skid | 2025-11-27T10:54:13.000 | Closed |  |  | 2025-11-25T05:28:35.337 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002592 | PS5-01-TR-4300 |  | A | M | 4.2:Four flange connections with tag number PS4 have been identified and verified during inspection | EPS VENDOR | PS5-01-05 - Foam Skid | 2025-11-27T11:13:46.000 | Closed |  |  | 2025-11-25T05:30:57.257 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002593 | PS5-28-PR-3900A |  | C | M | 4:During the inspection, it was found that the flange face area had been painted | EPS VENDOR | PS5-28-17 - Reinjection Pump |  | Originated |  |  | 2025-11-25T05:54:41.977 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-002594 | PS5-28-PR-3900A |  | A | M | 4.1:During the inspection, a significant oil leakage was detected on the pump body(Joint) | EPS VENDOR | PS5-28-17 - Reinjection Pump |  | Originated |  |  | 2025-11-25T05:56:03.593 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-002595 | PS5-28-PR-3900A |  | B | M | 4.2:It was observed that the stud installed was shorter than the required length. | EPS VENDOR | PS5-28-17 - Reinjection Pump |  | Originated |  |  | 2025-11-25T06:00:31.907 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-002596 | PS5-28-PR-3900A |  | A | M | 4.3:During the inspection, a significant oil leakage was detected on the boll vave(Joint) | EPS VENDOR | PS5-28-17 - Reinjection Pump |  | Originated |  |  | 2025-11-25T06:02:11.630 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-002597 | PS5-28-PR-3900A |  | C | M | 4.4:Found paint damage at pump area | EPS VENDOR | PS5-28-17 - Reinjection Pump |  | Originated |  |  | 2025-11-25T06:03:17.877 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-002598 | PS5-28-PR-3900B |  | A | M | 4:During inspection, a noticeable oil leakage was detected at the discharge valve area of PS5-28-APO-3901B | EPS VENDOR | PS5-28-17 - Reinjection Pump |  | Originated |  |  | 2025-11-25T06:07:44.413 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-002599 | PS5-28-PR-3900B |  | B | M | 4.1It was observed that the stud installed was shorter than the required length. | EPS VENDOR | PS5-28-17 - Reinjection Pump |  | Originated |  |  | 2025-11-25T06:09:34.090 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-002600 | PS5-01-UV-8700 |  | B | M | 4:Paint damage and U clamp support missing | EPS VENDOR | PS5-01-05 - Foam Skid |  | Originated |  |  | 2025-11-25T06:57:35.910 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002601 | PS5-01-UV-8700 |  | C | M | 4.1:Found paint damage | EPS VENDOR | PS5-01-05 - Foam Skid |  | Originated |  |  | 2025-11-25T06:58:56.350 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002602 | PS5-01-UV-8700 |  | A | M | 4.2:Hilti hit-HY-200-A was expired | EPS VENDOR | PS5-01-05 - Foam Skid |  | Originated |  |  | 2025-11-25T06:59:52.303 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002603 | PS5-01-UV-8700 |  | A | M | 4.3:PS5-01-IE-0001A support clamp bolt missing and support clamp was broken-01-IE-0001A support clamp bolt missing and support clamp was broken | EPS VENDOR | PS5-01-05 - Foam Skid |  | Originated |  |  | 2025-11-25T07:01:21.670 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002604 | PS5-01-UV-8700 |  | A | M | 4.4:Junction box stand 2 bolts are missing | EPS VENDOR | PS5-01-05 - Foam Skid |  | Originated |  |  | 2025-11-25T07:02:39.960 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002605 | PS5-01-UV-8700 |  | A | M | 4.5:1" recirculating line piping flange connection bolts 8 nos and spool 2" flange connection bolts 8 nos are not available with spool or skid | EPS VENDOR | PS5-01-05 - Foam Skid |  | Originated |  |  | 2025-11-25T07:04:45.720 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-002607 | PS5-71-VSV-1200 |  | B | M | 4.1:During the inspection, it was found that the flange face area had Found bend on the nozzle(N5) - Might have happened due to external impact. Also observed paint damage in the location.(No paint damage on the flange or damageonthebolts)been painted | EPS VENDOR | PS5-71-20 - Diesel Fuel Day Tank |  | Completed |  |  | 2025-11-25T10:55:55.027 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-002608 | PS5-01-PA-3200A |  | B | M | 4:During the inspection, it was found that the gasket (331ID × 348OD × 1.5T) was damaged | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:26:42.997 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002609 | PS5-01-PA-3200A |  | B | M | 4.1:As per the packing list (Equipment No. 12286.347), 12 pieces of 1/2" BSP female elbows were listed; they were not received. | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:28:02.823 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002610 | PS5-01-PA-3200A |  | B | M | 4.2:As per the packing list, 4 units of Stud Coupling A-Lok 8MSC8N-316 were scheduled for delivery; only 2 units were received.. | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:29:13.433 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002611 | PS5-01-PA-3200A |  | A | M | 4.3:Hole diameter for the anchor bolts are is lesser than anchor bolt diameter. Need to enlarge the hole diameter to fit withanchorbolt | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Completed |  |  | 2025-11-25T11:30:22.280 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002612 | PS5-01-PA-3200A |  | C | M | 4.4:Oil observed at the pump base frame floor area (Oil indicator glass not fixed properly). | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:31:22.463 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002613 | PS5-01-PA-3200A |  | B | M | 4.5:As per the packing list (Equipment No. 13472-711-076-7), 1/2" OD × 16SWG W/T Tubes (4000 mm ) but not received. | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:33:23.817 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002614 | PS5-01-PA-3200B |  | B | M | 4:During the inspection, it was found that the gasket (331ID × 348OD × 1.5T) was damaged | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:37:49.560 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002615 | PS5-01-PA-3200B |  | B | M | 4.1:As per the packing list (Equipment No. 12286.347), 12 pieces of 1/2" BSP female elbows were listed; they were not received. | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:39:01.310 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002616 | PS5-01-PA-3200B |  | B | M | 4.2:As per the packing list, 4 units of Stud Coupling A-Lok 8MSC8N-316 were scheduled for delivery; only 2 units were received.. | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:40:36.643 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002617 | PS5-01-PA-3200B |  | A | M | 4.3:Hole diameter for the anchor bolts are is lesser than anchor bolt diameter. Need to enlarge the hole diameter to fit withanchorbolt | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Completed |  |  | 2025-11-25T11:41:54.210 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002618 | PS5-01-PA-3200B |  | C | M | 4.4:Oil observed at the pump base frame floor area (Oil indicator glass not fixed properly). | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:42:53.467 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002619 | PS5-01-PA-3200B |  | B | M | 4.5:As per the packing list (Equipment No. 13472-711-076-7), 1/2" OD × 16SWG W/T Tubes (4000 mm ) but not received. | EPS VENDOR | PS5-01-01 - Fire Water Jockey Pump A/B |  | Originated |  |  | 2025-11-25T11:44:27.457 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002621 | PS5-01-PA-3100B |  | B | M | 4.1:Plug missing on the 2 nos valves (with pressure gauge) firewaterpumpB | EPS VENDOR | PS5-01-03 - Fire Water Pump B |  | Originated |  |  | 2025-11-25T11:48:23.293 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002622 | PS5-01-PA-3100B |  | B | M | 4.2:Oil was found in this area (may be oil leakage) | EPS VENDOR | PS5-01-03 - Fire Water Pump B |  | Originated |  |  | 2025-11-25T11:49:56.610 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002623 | PS5-01-PA-3100B |  | B | M | 4.3:The cover plate and nuts and bolts are missing. | EPS VENDOR | PS5-01-03 - Fire Water Pump B |  | Originated |  |  | 2025-11-25T11:50:52.343 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002624 | PS5-01-PA-3100B |  | C | M | 4.4:Observed paint damage on the hose | EPS VENDOR | PS5-01-03 - Fire Water Pump B |  | Originated |  |  | 2025-11-25T11:51:58.940 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002625 | PS5-01-PA-3100B |  | A | M | 4.5:Damage observed on pressure gauge | EPS VENDOR | PS5-01-03 - Fire Water Pump B |  | Originated |  |  | 2025-11-25T11:52:52.937 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002626 | PS5-01-PA-3100B |  | B | M | 4.6:Rubber bush / shock absorber found damage. | EPS VENDOR | PS5-01-03 - Fire Water Pump B |  | Originated |  |  | 2025-11-25T11:53:53.100 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-002627 | PS5-01-UZ-6900 |  | B | M | 4:During the inspection, some nuts of the overhead pipe supports were found on the floor to be reinstated | EPS VENDOR | PS5-01-10 - Water Mist Package |  | Originated |  |  | 2025-11-25T11:58:55.437 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-002634 | PS5-83-OB-0001 |  | A | M | 4.1:As per the packing list 2 units of EDS-C1-106-002 were scheduled for delivery; only 1 unit was received. | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:17:52.980 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002635 | PS5-83-OB-0001 |  | B | M | 4.2:"As per the packing list PS5-3BC-FP-01 Coverplate on deckplate 1Qty listed; that was not received" | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:21:59.973 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002636 | PS5-83-OB-0001 |  | B | M | 4.3:As per the packing list -PS5-A34-03 Dripping Nose 1Qty listed;that was not received | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:22:59.257 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002637 | PS5-83-OB-0001 |  | B | M | 4.4:As per the packing list 6 units of EDS-C1-106-002 were scheduled for delivery; only 2 unit were received. | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:24:12.710 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002638 | PS5-83-OB-0001 |  | A | M | 4.5:As per the packing list -BOLT M10*40HDG 40Qty listed;they were not received | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:25:27.557 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002639 | PS5-83-OB-0001 |  | A | M | 4.6:As per the packing list -CLAMP LADDER 40 Qty listed;they were not received | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:27:19.100 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002640 | PS5-83-OB-0001 |  | B | M | 4.7:As per the packing list 57 units of shroud were scheduled for delivery; only 50 unit were received. | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:28:21.293 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002641 | PS5-83-OB-0001 |  | B | M | 4.8:As per the packing list 414 units of shroud were scheduled for delivery; only 337 unit were received. | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:29:43.673 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002642 | PS5-83-OB-0001 |  | B | M | 4.9:Flashing column (inside the module )PS5-FLS-RF10 is shorter in lenghth and it can not be fix | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:30:54.133 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002643 | PS5-83-OB-0001 |  | B | M | 4.10: item cut on one side due to deep scratch | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:32:05.380 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002644 | PS5-83-OB-0001 |  | A | M | 4.11:NOT COMPLETE ONE PART IS MISSING | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:33:12.800 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002645 | PS5-83-OB-0001 |  | B | M | 4.12:External holes (for the alignment of bolt ) are missalinged /need to modify the hole, Rust found near the joint between module 2&3 | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:34:35.710 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002646 | PS5-83-OB-0001 |  | B | M | 4.13:Holes not provided/drilled/tap for installing deck cover plate Between Module 5/6, 6/3, 5/2, 3/2 | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:36:08.033 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002647 | PS5-83-OB-0001 |  | B | M | 4.14:Duct support ,light support,cable tray misplaced/ collapsed from the location | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:37:44.010 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002648 | PS5-83-OB-0001 |  | B | M | 4.15:Flashing column (inside the module 5/6) PS5-FLS-RF10 is shorter in lenghth and it can not be fix. | EPS VENDOR | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:38:48.593 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002649 | PS5-83-OB-0001 |  | B | M | 4.16:EITS - IT room door not fixed properly and water coming inside during the rain (manufacturing issue) | EITS | PS5-83-01 - EITS Building |  | Originated |  |  | 2025-11-27T07:39:41.313 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-002650 | PS5-08-35CB-1001-CA03 |  | A | T | PS005-E&I-M6-PL-2582 - Cable not terminator due to panel PNC-001 not install yet | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2025-11-27T11:03:05.000 | Thao-my, Alexandre | PS5 - Milestone C
PL-002651 | PS5-08-35CB-1001-CA04 |  | A | T | PS005-E&I-M6-PL-2583 - Cable not terminator due to panel PNC-001 not install yet | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2025-11-27T11:05:47.000 | Thao-my, Alexandre | PS5 - Milestone C
PL-002652 | PS5-08-35CB-1001-CA15 |  | A | T | PS005-E&I-M6-PL-2585 - Cable not terminator due to panel PNC-001 not install yet | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2025-11-27T11:06:53.000 | Thao-my, Alexandre | PS5 - Milestone C
PL-002653 | PS5-61-ISO-9005-05-CS01 |  | A | E | PS005-E&I-ALL-PL-1625 - Cable one side termination due to panel not install yet COW - TAG change to be done | EITS | PS5-61-08 - Electrical Control System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2025-11-27T11:07:46.000 | Thao-my, Alexandre | PS5 - Milestone C
PL-002655 | PS5-09-IES-0002 |  | C | E | PS005-HVA-ETC-PL-2254 - No access to operate Emergency stop | EITS | PS5-09-05 - HVAC for EITS Building | 2025-11-27T15:25:23.000 | Closed |  | Punch to be closed as per TQR - SSF1-TQR-000136 which is accepted by CPY, so punch no more applicable | 2025-11-27T11:10:14.000 | Thao-my, Alexandre | PS5 - Milestone A
PL-002656 | PS5-01-LA-0001-CL03 |  | A | I | PS005-E&I-ALL-PL-2589 - Power cable HIPPS Cabinet in General Batch 2 Should be replaced by Fire resistance (Orange cable) | EITS | PS5-0H-01 - HIPPS |  | Originated |  | Refer to Job Card BUILD-COW-0083 | 2025-11-27T11:11:04.000 | Thao-my, Alexandre | PS5 - Milestone H
PL-002662 | PS5-01-UB-6100 |  | C | I | PS005-E&I-ALL-PL-2426 - Special tool to reset Fire suppression solenoid valve to be provided. One by substation | EITS | PS5-01-09 - Inergen for EITS Building | 2025-12-22T09:44:12.000 | Closed |  | Delivery of the tool | 2025-11-27T11:19:00.000 | Thao-my, Alexandre | PS5 - Milestone A
PL-002663 | PS5-61-ISR-0101 |  | B | E | 4:IP washers are damaged | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2025-11-27T12:55:36.213 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-002664 | PS5-61-ISR-0101 |  | B | E | 4.1:Some cable entries are installed without IPwashers | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2025-11-27T12:57:45.720 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-002665 | PS5-61-ISR-0102 |  | A | M | 4:Pressure gauge glass was dislodged, and the gauge found in a bent position | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2025-11-27T13:00:55.240 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-002666 | PS5-61-ISR-0102 |  | C | M | 4.1:Oil barrel leakage (Since bottom side of the barrel was leaking turnedupsidedown) | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2025-11-27T13:02:05.123 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-002667 | PS5-09-PA-84500A |  | C | M | 4:There is no mention of the tag number on the name plate. | EPS VENDOR | PS5-09-03 - HVAC for Generator Building |  | Originated |  |  | 2025-11-27T13:45:07.387 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-002668 | PS5-09-PA-84500B |  | C | M | 4:There is no mention of the tag number on the name plate. | EPS VENDOR | PS5-09-03 - HVAC for Generator Building |  | Originated |  |  | 2025-11-27T13:48:22.603 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-002669 | PS5-09-PA-84500B |  | A | M | 4.1:Rust was found on the coupling / coupling hub during the inspection. | EPS VENDOR | PS5-09-03 - HVAC for Generator Building |  | Originated |  |  | 2025-11-27T13:49:31.867 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-002670 | PS5-60-TR-4300 |  | C | M | 4:As per the packing list, 2 numbers of compressed non-asbestos fibre gaskets; Received 4 numbers were received, resulting in an overage of 2 numbers. | EPS UNATRAC | PS5-60-24 - Cooling Water Tank & Pump |  | Originated |  |  | 2025-11-28T10:52:20.203 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-002672 | PS5-01-PA-3100B |  | A | M | Pressure gauges removed from the equipment by CPP preservation/ material team to be reistated after piping installation | CPP AGI | PS5-01-03 - Fire Water Pump B |  | Originated |  | CPP to reistate the pressure gauges | 2025-12-01T06:25:53.000 | kuttan, kuttan | PS5 - Milestone C
PL-002868 | PS5-61-IE-0002 |  | B | E | ECS-iVT - 2024-05-29-007 SFP (100Mb or 1Gb) to provide for Ethernet switches, SW02A/SW02B | EITS | PS5-61-08 - Electrical Control System |  | Originated |  | refer to job card ECS-COW-0001 | 2025-12-12T06:03:42.917 | Thao-my, Alexandre | PS5 - Milestone C
PL-002874 | PS5-25-SDV-0054B |  | B | I | 4:The panel board was found to have fallen from its bolt support during transportation. The bolt locations were cracked and torn due to excessive load. | EPS VENDOR | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  |  | 2025-12-12T11:18:11.210 | arun, jabesteen | PS5 - Milestone H
PL-002875 | PS5-25-SDV-0054C |  | B | I | 4:The panel board was found to have fallen from its bolt support during transportation. The bolt locations were cracked and torn due to excessive load. | EPS VENDOR | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  |  | 2025-12-12T11:30:41.543 | arun, jabesteen | PS5 - Milestone H
PL-003051 | PS5-61-JY-0001 |  | C | M | PS005-E&I-COW-1004 - Maintenance trolley for BlokSet : oil filling required | EITS | PS5-78-01 - Lifting and handling equipment |  | Originated |  | Refer to Job Card BUILD-COW-0006 | 2026-01-06T05:42:47.707 | Thao-my, Alexandre | PS5 - Milestone E
PL-003059 | PS5-61-IK-0001 |  | B | E | PS005-E&I-COW-1014 - ATS PLC SOFTWARE (I/O MAPPING) TO BE UPDATED AND TESTED | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0018 | 2026-01-06T05:42:47.707 | Thao-my, Alexandre | PS5 - Milestone A
PL-003063 | PS5-06-IG-0002 |  | C | E | PS005-E&I-COW-1018 - Missing Terminal ID X05 and Terminal numbers 1 to 8 | EITS | PS5-06-01 - AC UPS - EITS Building |  | Completed |  | Refer to Job Card BUILD-COW-0176 | 2026-01-06T05:42:47.707 | Thao-my, Alexandre | PS5 - Milestone A
PL-003068 | PS5-06-IG-0002 |  | B | E | PS005-E&I-COW-1023 - STS SETTINGS TO BE SET | EITS | PS5-06-01 - AC UPS - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0210 | 2026-01-06T05:42:47.707 | Thao-my, Alexandre | PS5 - Milestone A
PL-003077 | PS5-61-IG-0015 |  | A | E | Vendor TB minimum termination capacity is 25 sqmm. Vendor to provide terminals suitable 16 sqmm and to be installed by Construction CTR. | CPP AGI | PS5-62-10 - CRO Generator Building Normal L&SP DB - PS5-61-IG-0015 |  | Originated |  |  | 2026-01-08T06:52:44.320 | Thao-my, Alexandre | PS5 - Milestone B
PL-003078 | PS5-05-IG-0026 |  | A | E | Vendor TB minimum termination capacity is 25 sqmm. Vendor to provide terminals suitable 6 sqmm and to be installed by Construction CTR. | CPP AGI | PS5-62-07 - CRO Generator Electrical Building Emergency Lighting DB - PS5-05-IG-0026 |  | Originated |  |  | 2026-01-08T06:52:44.320 | Thao-my, Alexandre | PS5 - Milestone B
PL-003254 | PS5-25-PIT-0001 |  | A | I | Range calibration to be done | EACOP | PS5-25-01 - Export Pipeline Pig Receiver |  | Originated |  |  | 2026-01-14T12:40:17.767 | Thao-my, Alexandre | PS5 - Milestone H
PL-003259 | PS5-28-PIT-0041 |  | A | I | Range calibration to be done | EACOP | PS5-28-17 - Reinjection Pump |  | Originated |  |  | 2026-01-14T12:40:17.767 | Thao-my, Alexandre | PS5 - Milestone H
PL-003294 | PS5-03-SFSC-0001 |  | A | I | Cyber-FAT-120 Moxa switch for SIS PS2-03-SW-0001 was tested in Vitrolles, the remaining moxa sw are in Batam or they have been already sent to site. | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to INS-COW-0002 | 2026-01-21T05:09:52.963 | Thao-my, Alexandre | PS5 - Milestone A
PL-003415 | PS5-01-PAL-6101 |  | A | I | PS005-E&I-ALL-PL-2608 - PAL Cable that currently installed Flame Retardant (E253359) shall be replace with Fire Resistan cable IEC60331 (Orange). | EITS | PS5-01-09 - Inergen for EITS Building |  | Completed |  | Refer to Job Card BUILD-COW-0405 | 2026-02-10T05:18:20.410 | Thao-my, Alexandre | PS5 - Milestone A
PL-003416 | PS5-01-PAL-6102 |  | A | I | PS005-E&I-ALL-PL-2608 - PAL Cable that currently installed Flame Retardant (E253359) shall be replace with Fire Resistan cable IEC60331 (Orange). | EITS | PS5-01-09 - Inergen for EITS Building |  | Completed |  | Refer to Job Card BUILD-COW-0405 | 2026-02-10T05:18:20.410 | Thao-my, Alexandre | PS5 - Milestone A
PL-003417 | PS5-01-PAL-6103 |  | A | I | PS005-E&I-ALL-PL-2608 - PAL Cable that currently installed Flame Retardant (E253359) shall be replace with Fire Resistan cable IEC60331 (Orange). | EITS | PS5-01-09 - Inergen for EITS Building |  | Completed |  | Refer to Job Card BUILD-COW-0405 | 2026-02-10T05:18:20.410 | Thao-my, Alexandre | PS5 - Milestone A
PL-003473 | PS5-61-IV-0001A-CH01 |  | A | E | 7: | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Repulling of cable, mantain good bending radius. | 2026-02-12T12:15:25.157 | peela, raja | PS5 - Milestone A
PL-003579 | PS5-60-UR-8100A |  | A | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHALL BE COMPLETED (DISCIPILINE - PIPING) | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT SHALL BE COMPLETED AFTER HT | 2026-02-13T13:21:05.920 | arun, jabesteen | PS5 - Milestone B
PL-003580 | PS5-60-UR-8100A |  | A | M | 10.1:FINAL ALIGNMENT SHULD BE DONE | EPS UNATRAC | PS5-60-01 - Power Generation Package A |  | Originated |  | FINAL ALIGNMENT SHULD BE DONE | 2026-02-13T13:31:26.833 | arun, jabesteen | PS5 - Milestone B
PL-003581 | PS5-60-UR-8100B |  | A | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED AFTER HT | 2026-02-13T13:46:21.160 | arun, jabesteen | PS5 - Milestone B
PL-003582 | PS5-60-UR-8100B |  | A | M | 10.1:FINAL ALIGNMENT SHOULD BE DONE | EPS UNATRAC | PS5-60-04 - Power Generation Package B |  | Originated |  | FINAL ALIGNMENT SHOULD BE DONE | 2026-02-13T13:52:08.660 | arun, jabesteen | PS5 - Milestone B
PL-003583 | PS5-60-UR-8100C |  | A | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED AFTER HT | 2026-02-13T13:55:54.823 | arun, jabesteen | PS5 - Milestone D
PL-003584 | PS5-60-UR-8100C |  | A | M | 10.1:FINAL ALIGNMENT SHULD BE DONE | EPS UNATRAC | PS5-60-07 - Power Generation Package C |  | Originated |  | FINAL ALIGNMENT SHULD BE DONE | 2026-02-13T13:58:06.040 | arun, jabesteen | PS5 - Milestone D
PL-003585 | PS5-60-UR-8100D |  | A | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED AFTER HT | 2026-02-13T14:05:42.683 | arun, jabesteen | PS5 - Milestone D
PL-003586 | PS5-60-UR-8100D |  | A | M | 10.1:FINAL ALIGNMENT SHULD BE DONE | EPS UNATRAC | PS5-60-10 - Power Generation Package D |  | Originated |  | FINAL ALIGNMENT SHULD BE DONE | 2026-02-13T14:08:00.040 | arun, jabesteen | PS5 - Milestone D
PL-003587 | PS5-60-UR-8100E |  | A | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | CPP AGI | PS5-60-13 - Power Generation Package E |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED AFTER HT | 2026-02-13T14:13:02.357 | arun, jabesteen | PS5 - Milestone D
PL-003588 | PS5-60-UR-8100E |  | A | M | 10.1:FINAL ALIGNMENT SHULD BE DONE | EPS UNATRAC | PS5-60-13 - Power Generation Package E |  | Originated |  | FINAL ALIGNMENT SHULD BE DONE | 2026-02-13T14:15:01.700 | arun, jabesteen | PS5 - Milestone D
PL-003589 | PS5-60-UR-8100F |  | A | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | CPP AGI | PS5-60-16 - Power Generation Package F |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED AFTER HT | 2026-02-13T14:19:06.617 | arun, jabesteen | PS5 - Milestone D
PL-003590 | PS5-60-UR-8100F |  | A | M | 10.1:FINAL ALIGNMENT SHOULD BE DONE | EPS UNATRAC | PS5-60-16 - Power Generation Package F |  | Originated |  | FINAL ALIGNMENT SHOULD BE DONE | 2026-02-13T14:20:49.163 | arun, jabesteen | PS5 - Milestone D
PL-003591 | PS5-60-UR-8100G |  | A | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED AFTER HT | 2026-02-13T14:23:25.577 | arun, jabesteen | PS5 - Milestone E
PL-003592 | PS5-60-UR-8100G |  | A | M | 10.1:FINAL ALIGNMENT SHOULD BE DONE | EPS UNATRAC | PS5-60-19 - Power Generation Package G |  | Originated |  | FINAL ALIGNMENT SHOULD BE DONE | 2026-02-13T14:24:31.330 | arun, jabesteen | PS5 - Milestone E
PL-003593 | PS5-83-OB-0001_Installation |  | A | M | Structural bolts shall be properly secured & tightened all over the EITS Building area | CPP AGI | PS5-83-01 - EITS Building | 2026-02-24T14:00:42.000 | Closed |  | Structural bolts shall be properly secured & tightened all over the EITS Building area | 2026-02-14T06:59:23.000 | arun, jabesteen | PS5 - Milestone A
PL-003594 | PS5-83-OB-0001_Installation |  | B | B | Proper Leveling, compaction, gravel fill required for the whole EITS building area. | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | Proper Leveling, compaction, gravel fill required for the whole EITS building area. | 2026-02-14T07:10:07.000 | arun, jabesteen | PS5 - Milestone A
PL-003595 | PS5-83-OB-0001_Installation |  | A | M | Grating Clips shall be properly fastened and tightened | CPP AGI | PS5-83-01 - EITS Building | 2026-02-24T14:01:03.000 | Closed |  | Grating Clips shall be properly fastened and tightened | 2026-02-14T07:15:33.000 | arun, jabesteen | PS5 - Milestone A
PL-003596 | PS5-83-OB-0001_Installation |  | B | M | External covers outside the EITS building found gaps, screw damages & holes mismatch. | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | External covers outside the EITS building found gaps, screw damages & holes mismatch should be rectified | 2026-02-14T07:19:22.000 | arun, jabesteen | PS5 - Milestone A
PL-003597 | PS5-83-OB-0001_Installation |  | B | B | Proper finishing required for the EITS building foundations. | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | Proper finishing required for the EITS building foundations. | 2026-02-14T07:23:29.000 | arun, jabesteen | PS5 - Milestone A
PL-003600 | PS5-83-OB-0001_Installation |  | B | E | Sprinkler to be installed after GALT. | EITS | PS5-83-01 - EITS Building |  | Originated |  | Sprinkler to be installed after GALT. | 2026-02-14T07:34:31.000 | arun, jabesteen | PS5 - Milestone A
PL-003601 | PS5-83-OB-0001_Installation |  | A | M | Anchor bolts need to be tightened for HVAC ACU units. | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | Anchor bolts need to be tightened for HVAC ACU units. | 2026-02-14T07:38:50.000 | arun, jabesteen | PS5 - Milestone A
PL-003602 | PS5-83-OB-0001_Installation |  | B | M | Handrail Splice needs to be Welded and Painted at East side area | CPP AGI | PS5-83-01 - EITS Building | 2026-02-24T14:01:21.000 | Closed |  | Handrail Splice needs to be Welded and Painted at East side area | 2026-02-14T07:42:24.000 | arun, jabesteen | PS5 - Milestone A
PL-003605 | PS5-83-OB-0001_Installation |  | A | H | All HVAC ducts were misaligned with the ACU units. | EITS | PS5-83-01 - EITS Building |  | Originated |  | All HVAC ducts were misaligned with the ACU units. | 2026-02-14T07:46:41.000 | arun, jabesteen | PS5 - Milestone A
PL-003606 | PS5-83-OB-0001_Installation |  | A | E | Earthing bonders need to be installed all over structural connection. | EITS | PS5-83-01 - EITS Building |  | Originated |  | Earthing bonders need to be installed all over structural connection | 2026-02-14T07:52:09.000 | arun, jabesteen | PS5 - Milestone A
PL-003608 | PS5-83-OB-0001_Installation |  | A | E | For all Inergen lines U-bolts tightening & Torquing shall be done before GALT | EITS | PS5-83-01 - EITS Building |  | Originated |  | For all Inergen lines U-bolts tightening & Torquing shall be done before GALT | 2026-02-14T07:57:00.000 | arun, jabesteen | PS5 - Milestone A
PL-003609 | PS5-83-OB-0001_Installation |  | A | M | Shutoff Dampers were not installed above the HVAC ACU units (4 Dampers) | CPP AGI | PS5-83-01 - EITS Building | 2026-02-24T14:01:39.000 | Closed |  | Shutoff Dampers were above the HVAC ACU units (4 Dampers)-should be installed | 2026-02-14T08:02:05.000 | arun, jabesteen | PS5 - Milestone A
PL-003610 | PS5-83-OB-0001_Installation |  | A | H | HVAC Ducts leak test shall be performed after finishing the whole installations | EITS | PS5-83-01 - EITS Building |  | Originated |  | HVAC Ducts leak test shall be performed after finishing the whole installations | 2026-02-14T08:05:57.000 | arun, jabesteen | PS5 - Milestone A
PL-003611 | PS5-83-OB-0001_Installation |  | A | B | Missing two elbows (3019F and 3019G) | EITS | PS5-83-01 - EITS Building |  | Originated |  | Missing two elbows (3019F and 3019G) should be installed | 2026-02-14T08:09:26.000 | arun, jabesteen | PS5 - Milestone A
PL-003612 | PS5-83-OB-0001_Installation |  | A | P | MCT not provided for the Inergen pipes which are entering into the Inergen Package | EITS | PS5-83-01 - EITS Building | 2026-05-12T11:53:39.000 | Closed |  | MCT not provided for the Inergen pipes which are entering into the Inergen Package | 2026-02-14T08:15:00.000 | arun, jabesteen | PS5 - Milestone A
PL-003615 | PS5-83-OB-0001_Installation |  | B | E | All EIT cable tray, Ladder, tray supports shall be installed | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | All EIT cable tray, Ladder, tray supports shall be installed. | 2026-02-14T08:18:38.000 | arun, jabesteen | PS5 - Milestone A
PL-003616 | PS5-83-OB-0001_Installation |  | A | E | Electrical earthing around the building shall be completed. | CPP AGI | PS5-83-01 - EITS Building | 2026-02-24T14:03:19.000 | Closed |  | Electrical earthing around the building shall be completed. | 2026-02-14T08:21:38.000 | arun, jabesteen | PS5 - Milestone A
PL-003617 | PS5-61-IU-0011 |  | A | E | 4:During inspection, the junction box fell down due to improper fixing. The item was dispatched without being securely installed. | EPS VENDOR | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  |  | 2026-02-14T11:31:27.620 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-003618 | PS5-61-IU-0011 |  | B | E | 4.1:No cable glands are installed in the DECT MDU PANEL | EPS VENDOR | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  |  | 2026-02-14T11:33:24.200 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-003619 | PS5-61-IU-0011 |  | B | E | 4.2:All installed cables are directly fixed to the transformer without cable trays and/or rigid conduit pipes. | EPS VENDOR | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  |  | 2026-02-14T11:34:50.800 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-003620 | PS5-61-IU-0011 |  | B | E | 4.3:"At the commissioning stage, it is necessary to verify the functionality of the equipment and confirm the absence of any hidden defects. Because panel was unfixed." | EPS VENDOR | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  |  | 2026-02-14T11:36:23.003 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-003621 | BF_PS5-61-IU-0010 |  | B | E | 4:No cable glands are installed in the DECT MDU PANEL | EPS VENDOR | PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010) |  | Originated |  |  | 2026-02-14T11:41:59.533 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-003622 | PS5-61-IU-0010 |  | B | E | 4.1:All installed cables are directly fixed to the transformer without cable trays and/or rigid conduit pipes. | EPS VENDOR | PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010) |  | Originated |  |  | 2026-02-14T11:43:37.660 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-003623 | PS5-01-PA-3100A |  | B | M | 4:All the jack bolts are missing on the base frame of the pump | EPS VENDOR | PS5-01-02 - Fire Water Pump A |  | Originated |  |  | 2026-02-14T11:49:01.793 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-003624 | PS5-01-PA-3100A |  | A | M | 4.1:22 batteries had a voltage below 1V, 6 batteries had a voltage below 1.2V | EPS VENDOR | PS5-01-02 - Fire Water Pump A |  | Originated |  |  | 2026-02-14T11:51:08.820 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-003625 | PS5-01-PA-3100A |  | A | M | 4.2:Silencer not received along with the pump | EPS VENDOR | PS5-01-02 - Fire Water Pump A |  | Completed |  |  | 2026-02-14T11:52:42.530 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-003648 | PS5-01-UZ-610 |  | A | M | 4:As per the packing list, a 0.18-liter Nitrogen (N₂) cylinder is specified with a filling pressure of 200 bar. However, upon receipt at PS5-01-UZ-610, two cylinders were found with pressures of 1300 psi (89.6 Bar), which are below the specified 200 bar requirement. | EPS VENDOR | PS5-01-11 - Inergen for Power Gen Building |  | Originated |  |  | 2026-02-19T11:49:56.420 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-003649 | PS5-71-UN-7200 |  | B | M | 4:"Spare parts have arrived; but no details are mentioned in the packing list. ( gaskets-2 pcs 3/4"" 150# 4 pcs 1"" 150# 4 pcs 1 1/2"" 150# 5 pcs 2"" 150"" 3 pcs 4"" 150# 2 set lamps fuses and connectors (SIBA FUSE 5X20 T 125MA DS10) 1 PCS DIGITAL BARRIER dek-oe-24dc/100k. 1 pcs repeater power supply (Analog barrier) MACX MCR-SL-RPSSI-2I. )" | EPS VENDOR | PS5-71-02 - CFO Allocation Metering Package |  | Originated |  |  | 2026-02-19T13:30:18.920 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003654 | PS5-28-PA-3700A |  | B | M | Coupling hub inside dia is not matching with the shaft dia of pump and motor | EPS VENDOR | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  | vendor to rectify | 2026-02-20T07:17:37.000 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-003655 | PS5-28-PA-3700B |  | A | M | Coupling hub inside dia is not matching with the shaft dia of pump and motor | EPS VENDOR | PS5-28-04 - Closed Drain Drum and Pump 02 |  | Originated |  | vendor to rectify | 2026-02-20T07:21:04.000 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-003692 | PS5-75-UI-6100 |  | B | I | Level Gauge FAT not conducted as the Specific gravity of the water does not allow the instrument float to float. | EACOP | PS5-75-02 - Biocide Injection Package |  | Originated |  | To be verified along with commissioning test | 2026-02-23T12:49:22.000 | Thao-my, Alexandre | PS5 - Milestone G
PL-003701 | PS5-61-IE-0001 |  | B | E | ECS-iFAT-2024-07-02-011 Keyboard and mouse lose connection after power recycle from MCB on ECS Server A & B | EITS | PS5-61-08 - Electrical Control System |  | Originated |  | refer to job card ECS-COW-007 | 2026-02-24T05:20:03.557 | Thao-my, Alexandre | PS5 - Milestone C
PL-003706 | PS5-61-IE-0001 |  | B | E | ECS-ECS - 20255-08-12-003 Configure the static route for ALL ECS/PCS connection | EITS | PS5-61-08 - Electrical Control System |  | Originated |  | refer to job card ECS-COW-0006 | 2026-02-24T05:20:03.557 | Thao-my, Alexandre | PS5 - Milestone C
PL-003714 | PS5-71-TR-4100 |  | A | M | 4:As per the drawing, the deluge piping should be galvanized Carbon steel, but it was received without a galvanized coating. | EPS VENDOR | PS5-71-04 - CFO Storage Tank |  | Originated |  |  | 2026-02-24T13:10:06.950 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003715 | PS5-71-TR-4100 |  | A | M | 4.1:SL NO-11, M10 'U' BOLT - 2" PIPE + 4NUTS (STD) NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:26:42.000 | Closed |  | SL NO-11, M10 'U' BOLT - 2" PIPE + 4NUTS (STD) RECEIVED IN THE NEXT PACKAGE | 2026-02-24T13:12:04.870 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003716 | PS5-71-TR-4100 |  | A | M | 4.2:SL NO - 14 , GASKET 3MM NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:26:08.000 | Closed |  | SL NO - 14 , GASKET 3MM NOT RECEIVED | 2026-02-24T13:13:05.400 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003717 | PS5-71-TR-4100 |  | A | M | 4.3: SL NO - 17, WASHER NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:27:02.000 | Closed |  | SL NO - 17, WASHER NOT RECEIVED | 2026-02-24T13:14:15.343 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003718 | PS5-71-TR-4100 |  | A | M | 4.4:SL NO - 20 , GASKET 762O.D.x600I.D.x1.5THK NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:28:18.000 | Closed |  | SL NO - 20 , GASKET 762O.D.x600I.D.x1.5THK NOT RECEIVED | 2026-02-24T13:15:26.817 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003719 | PS5-71-TR-4100 |  | A | M | 4.5:SL NO - 24 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:28:34.000 | Closed |  | SL NO - 24 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | 2026-02-24T13:16:38.200 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003720 | PS5-71-TR-4100 |  | A | M | 4.6:SL NO - 26 , GASKET 1.5 THK., 6"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:28:53.000 | Closed |  | SL NO - 26 , GASKET 1.5 THK., 6"-150# RF NOT RECEIVED | 2026-02-24T13:18:02.313 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003721 | PS5-71-TR-4100 |  | A | M | 4.7:SL NO - 29 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:29:09.000 | Closed |  | 4.7:SL NO - 29 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | 2026-02-24T13:18:57.017 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003722 | PS5-71-TR-4100 |  | A | M | 4.8:SL NO - 32 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:29:28.000 | Closed |  | SL NO - 32 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | 2026-02-24T13:20:06.950 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003723 | PS5-71-TR-4100 |  | A | M | 4.9:SL NO - 37 , GASKET 4.5 THK., 3"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:29:46.000 | Closed |  | SL NO - 37 , GASKET 4.5 THK., 3"-150# RF NOT RECEIVED | 2026-02-24T13:21:08.703 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003724 | PS5-71-TR-4100 |  | A | M | 4.10:SL NO - 38 , STUD+2NUTS-5/8" UNC NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:30:03.000 | Closed |  | SL NO - 38 , STUD+2NUTS-5/8" UNC NOT RECEIVED | 2026-02-24T13:22:18.360 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003725 | PS5-71-TR-4100 |  | A | M | 4.11:SL NO - 54 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:30:21.000 | Closed |  | SL NO - 54 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | 2026-02-24T13:23:25.320 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003726 | PS5-71-TR-4100 |  | A | M | 4.12:SL NO - 58 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | EPS VENDOR | PS5-71-04 - CFO Storage Tank | 2026-05-14T13:30:44.000 | Closed |  | L NO - 58 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | 2026-02-24T13:24:34.683 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003727 | PS5-71-TR-4200 |  | A | M | 4:As per the drawing, the deluge piping should be galvanized carbon steel, but it was received without a galvanized coating. | EPS VENDOR | PS5-71-12 - CFO Service Tank |  | Originated |  |  | 2026-02-24T13:29:28.133 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003728 | PS5-71-TR-4200 |  | A | M | 4.1:SL NO - 61 , GASKET 762 ,O.D.x600,I.D.x1.5THK NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:32:11.000 | Closed |  | SL NO - 61 , GASKET 762 ,O.D.x600,I.D.x1.5THK NOT RECEIVED | 2026-02-24T13:31:02.293 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003729 | PS5-71-TR-4200 |  | A | M | 4.2:SL NO - 67 , GASKET 3MM NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:33:01.000 | Closed |  | SL NO - 67 , GASKET 3MM NOT RECEIVED | 2026-02-24T13:32:15.527 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003731 | PS5-71-TR-4200 |  | A | M | 4.4:SL NO - 70 , WASHER NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:33:15.000 | Closed |  | SL NO - 70 , WASHER NOT RECEIVED | 2026-02-24T13:33:24.057 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003732 | PS5-71-TR-4200 |  | A | M | 4.5:SL SL NO - 71 , HEX. NUTS M20 NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:33:33.000 | Closed |  | SL NO - 71 , HEX. NUTS M20 NOT RECEIVED | 2026-02-24T13:34:18.187 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003733 | PS5-71-TR-4200 |  | A | M | 4.6:SL NO - 75 , WASHER O.D. 40 x I.D. 18 NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:34:54.000 | Closed |  | SL NO - 75 , WASHER O.D. 40 x I.D. 18 NOT RECEIVED | 2026-02-24T13:36:16.690 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003734 | PS5-71-TR-4200 |  | A | M | 4.7:SL NO - 76 , SPLIT PIN-5Ø NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:35:15.000 | Closed |  | SL NO - 76 , SPLIT PIN-5Ø NOT RECEIVED | 2026-02-24T13:37:18.260 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003735 | PS5-71-TR-4200 |  | A | M | 4.8:SL NO -77 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:35:41.000 | Closed |  | SL NO -77 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | 2026-02-24T13:39:10.940 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003736 | PS5-71-TR-4200 |  | A | M | 4.9:SL NO - 79 , GASKET 1.5 THK., 3"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:36:16.000 | Closed |  | SL NO - 79 , GASKET 1.5 THK., 3"-150# RF NOT RECEIVED | 2026-02-24T13:40:12.990 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003737 | PS5-71-TR-4200 |  | A | M | 4.10:SL NO - 82 , GASKET 4.5 THK., 10"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:36:33.000 | Closed |  | SL NO - 82 , GASKET 4.5 THK., 10"-150# RF NOT RECEIVED | 2026-02-24T13:41:16.850 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003738 | PS5-71-TR-4200 |  | A | M | 4.11:SL NO - 85 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:36:47.000 | Closed |  | SL NO - 85 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | 2026-02-24T13:42:52.970 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003739 | PS5-71-TR-4200 |  | A | M | 4.12:SL NO - 90 , GASKET 4.5 THK., 3"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:37:03.000 | Closed |  | SL NO - 90 , GASKET 4.5 THK., 3"-150# RF NOT RECEIVED | 2026-02-24T13:44:19.240 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003740 | PS5-71-TR-4200 |  | A | M | 4.13:SL NO - 90 , GASKET 4.5 THK., 3"-150# RF NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:37:16.000 | Closed |  | SL NO - 90 , GASKET 4.5 THK., 3"-150# RF NOT RECEIVED | 2026-02-24T13:45:09.410 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003741 | PS5-71-TR-4200 |  | A | M | 4.14:SL NO - 106 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:37:29.000 | Closed |  | SL NO - 106 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | 2026-02-24T13:46:46.080 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003742 | PS5-71-TR-4200 |  | A | M | 4.15:SL NO - 111 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | EPS VENDOR | PS5-71-12 - CFO Service Tank | 2026-05-14T13:37:47.000 | Closed |  | SL NO - 111 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | 2026-02-24T13:48:00.817 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-003743 | PS5-71-TR-4400 |  | A | M | As per the packing list, 3 Nos. of 1/4" nipple are mentioned, but they have not been received. | EPS VENDOR | PS5-71-15 - Diesel Fuel Storage Tank |  | Originated |  | Vendor to rectify | 2026-02-24T14:06:04.000 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-003744 | PS5-53-TR-4100 |  | A | M | As per the packing list, 3 Nos. of vortex breakers are mentioned, but they have not been received. | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank |  | Originated |  | Vendor to rectify | 2026-02-24T14:09:14.000 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-004311 | PS5-60-VS-9100A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-02T10:42:45.157 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004312 | PS5-60-VS-9100B |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-02T10:54:14.483 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004313 | PS5-60-VS-9100C |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-02T11:00:09.387 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004314 | PS5-60-VS-9100D |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-02T11:04:21.727 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004315 | PS5-60-VS-9100F |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping | CPP AGI | PS5-60-47 - Oil Mist Separator Skid PS5-60-VS-9100F |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping | 2026-03-02T11:09:05.243 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004316 | PS5-60-VA-5100C |  | A | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-30 - Air Receiver C & Air Regulator C |  | Originated |  |  | 2026-03-02T12:45:37.510 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004333 | PS5-60-YF-1700A |  | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-03T06:31:39.983 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004334 | PS5-60-YF-1700A |  | C | E | 16.1:EARTHING TO BE DONE | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  | ARTHING TO BE DONE | 2026-03-03T06:32:22.740 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004335 | PS5-60-YF-1700B |  | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-03T06:38:00.760 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004336 | PS5-60-YF-1700B |  | C | E | 16.1:EARTHING TO BE DONE | CPP AGI | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B |  | Originated |  | EARTHING TO BE DONE | 2026-03-03T06:38:35.387 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004340 | PS5-78-JC-9100A |  | C | M | 25:ouch up paint will be carried out | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2026-03-04T04:38:53.837 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004341 | PS5-78-JC-9100B |  | C | M | 25:Touch-up painting will be carried out | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2026-03-04T04:43:17.320 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004342 | PS5-78-JC-9100C |  | C | M | 25:Touch-up painting will be carried out | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2026-03-04T04:44:53.743 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004343 | PS5-78-JC-9100D |  | C | M | 25:Touch-up painting will be carried out | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  |  | 2026-03-04T04:46:36.597 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004344 | PS5-05-UR-8100 |  | A | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2026-03-04T10:06:16.263 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-004345 | PS5-05-UR-8100 |  | A | M | 10.1: Flame arrester to be installed | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2026-03-04T10:35:48.293 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-004346 | PS5-05-UR-8100 |  | A | M | 10.2:Final alignment to be verified | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  |  | 2026-03-04T10:36:23.793 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-004347 | PS5-60-VA-5100A |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-28 - Air Receiver A & Air Regulator A |  | Originated |  |  | 2026-03-04T12:33:23.000 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004348 | PS5-60-VA-5100A |  | B | P | 23.1:EARTHING TO BE DONE | CPP AGI | PS5-60-28 - Air Receiver A & Air Regulator A |  | Originated |  |  | 2026-03-04T12:34:01.427 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004349 | PS5-60-VA-5100B |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-29 - Air Receiver B & Air Regulator B |  | Originated |  |  | 2026-03-04T12:46:11.933 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004350 | PS5-60-VA-5100B |  | B | P | 23.1:EARTHING TO BE DONE | CPP AGI | PS5-60-29 - Air Receiver B & Air Regulator B |  | Originated |  |  | 2026-03-04T12:46:56.717 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004351 | PS5-60-VS-9100E |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-46 - Oil Mist Separator Skid PS5-60-VS-9100E |  | Originated |  |  | 2026-03-04T12:59:34.597 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004352 | PS5-60-VS-9100G |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-48 - Oil Mist Separator Skid PS5-60-VS-9100G |  | Originated |  |  | 2026-03-04T13:09:59.443 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004353 | PS5-60-UZ-8900A |  | A | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A |  | Originated |  |  | 2026-03-04T13:17:49.207 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004354 | PS5-60-VA-5100D |  | A | P | 23:EARTHING TO BE DONE | CPP AGI | PS5-60-31 - Air Receiver D & Air Regulator D |  | Originated |  |  | 2026-03-04T14:05:39.233 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004355 | PS5-60-VA-5100D |  | B | P | 23.1:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-31 - Air Receiver D & Air Regulator D |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-04T14:06:54.250 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004356 | PS5-60-VA-5100E |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-32 - Air Receiver E & Air Regulator E |  | Originated |  |  | 2026-03-04T14:11:23.857 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004357 | PS5-60-VA-5100E |  | B | E | 23.1:EARTHING TO BE DONE | CPP AGI | PS5-60-32 - Air Receiver E & Air Regulator E |  | Originated |  |  | 2026-03-04T14:11:44.880 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004358 | PS5-60-VA-5100F |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-33 - Air Receiver F & Air Regulator F |  | Originated |  |  | 2026-03-04T14:18:39.830 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004359 | PS5-60-VA-5100F |  | B | E | 23.1: EARTHING TO BE DONE | CPP AGI | PS5-60-33 - Air Receiver F & Air Regulator F |  | Originated |  |  | 2026-03-04T14:18:59.577 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004360 | PS5-60-VA-5100G |  | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-34 - Air Receiver G & Air Regulator G |  | Originated |  |  | 2026-03-04T14:25:37.763 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004361 | PS5-60-VA-5100G |  | B | E | 23.1: EARTHING TO BE DONE | CPP AGI | PS5-60-34 - Air Receiver G & Air Regulator G |  | Originated |  |  | 2026-03-04T14:26:00.973 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004362 | PS5-60-YF-1700G |  | B | M | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G |  | Originated |  |  | 2026-03-04T14:39:49.190 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004363 | PS5-60-YF-1700G |  | B | E | 16.1: EARTHING TO BE DONE | CPP AGI | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G |  | Originated |  |  | 2026-03-04T14:40:26.563 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004364 | PS5-60-YF-1700F |  | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Originated |  |  | 2026-03-05T12:51:07.483 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004365 | PS5-60-YF-1700F |  | B | E | 16.1:EARTHING TO BE DONE | CPP AGI | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F |  | Originated |  |  | 2026-03-05T12:51:34.050 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004366 | PS5-60-YF-1700E |  | A | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E |  | Originated |  |  | 2026-03-05T12:55:48.527 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004367 | PS5-60-YF-1700E |  | B | E | 16.1:EARTHING TO BE DONE | CPP AGI | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E |  | Originated |  |  | 2026-03-05T12:56:15.463 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004368 | PS5-60-YF-1700D |  | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D |  | Originated |  |  | 2026-03-05T12:59:29.633 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004369 | PS5-60-YF-1700D |  | B | E | 16.1:EATRHING TO BE DONE | CPP AGI | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D |  | Originated |  |  | 2026-03-05T12:59:50.947 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004370 | PS5-60-YF-1700C |  | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C |  | Originated |  |  | 2026-03-05T13:06:48.617 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004371 | PS5-60-YF-1700C |  | B | E | 16.1:EARTHING TO BE DONE | CPP AGI | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C |  | Originated |  |  | 2026-03-05T13:07:26.887 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004372 | PS5-60-UR-8200A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T13:23:10.510 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004373 | PS5-60-UR-8200B |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T13:26:04.377 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004374 | PS5-60-UR-8200C |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T13:28:26.753 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004375 | PS5-60-UR-8200D |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T13:32:38.910 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004376 | PS5-60-UR-8200E |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-13 - Power Generation Package E |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T13:42:43.950 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004377 | PS5-60-UR-8200F |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-16 - Power Generation Package F |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T13:54:33.130 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-004378 | PS5-60-UR-8200G |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-05T13:58:04.690 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004379 | PS5-78-JC-9100A |  | B | B | ROOF-final installation need to be done In PG area | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | ROOF-final installation need to be done In PG area | 2026-03-06T05:27:24.000 | arun, jabesteen | PS5 - Milestone E
PL-004380 | PS5-78-JC-9100B |  | B | B | ROOF-final installation need to be done In PG area | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | ROOF-final installation need to be done In PG area | 2026-03-06T07:01:12.000 | arun, jabesteen | PS5 - Milestone E
PL-004381 | PS5-78-JC-9100C |  | B | B | ROOF-final installation need to be done In PG area-9100 C | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | ROOF-final installation need to be done In PG area | 2026-03-06T07:05:29.000 | arun, jabesteen | PS5 - Milestone E
PL-004382 | PS5-78-JC-9100D |  | B | B | ROOF-final installation need to be done In PG area | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | ROOF-final installation need to be done In PG area-9100 D | 2026-03-06T07:08:26.000 | arun, jabesteen | PS5 - Milestone E
PL-004384 | PS5-60-IJ-0001A-CH04 |  | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | 2026-03-07T11:12:27.703 | arun, jabesteen | PS5 - Milestone B
PL-004385 | PS5-60-IJ-0001B-CH04 |  | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | 2026-03-07T11:34:01.367 | arun, jabesteen | PS5 - Milestone B
PL-004386 | PS5-60-IJ-0001C-CH04 |  | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | 2026-03-07T11:37:51.250 | arun, jabesteen | PS5 - Milestone D
PL-004387 | PS5-60-IJ-0001D-CH04 |  | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | 2026-03-07T11:40:47.027 | arun, jabesteen | PS5 - Milestone D
PL-004388 | PS5-60-IJ-0001E-CH04 |  | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | CPP AGI | PS5-60-13 - Power Generation Package E |  | Originated |  | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | 2026-03-07T11:44:20.037 | arun, jabesteen | PS5 - Milestone D
PL-004389 | PS5-60-IJ-0001F-CH04 |  | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | CPP AGI | PS5-60-16 - Power Generation Package F |  | Originated |  | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | 2026-03-07T11:47:40.440 | arun, jabesteen | PS5 - Milestone D
PL-004390 | PS5-60-IJ-0001G-CH04 |  | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | 2026-03-07T11:50:00.550 | arun, jabesteen | PS5 - Milestone E
PL-004411 | PS5-78-JC-9100A |  | B | M | Chain to be correctly installed (still hooked on the rail). | CPP AGI | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:45:33.000 | Closed |  | Chain to be correctly installed (still hooked on the rail). | 2026-03-10T07:32:16.000 | arun, jabesteen | PS5 - Milestone E
PL-004412 | PS5-78-JC-9100B |  | B | M | Chain to be installed | CPP AGI | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:46:31.000 | Closed |  | Chain to be installed | 2026-03-10T07:41:42.000 | arun, jabesteen | PS5 - Milestone E
PL-004413 | PS5-78-JC-9100B |  | B | M | Guide rail anti-derailment to be installed | CPP AGI | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:46:51.000 | Closed |  | Guide rail anti-derailment to be installed | 2026-03-10T07:47:12.000 | arun, jabesteen | PS5 - Milestone E
PL-004414 | PS5-78-JC-9100B |  | B | E | 3 pin connectors damaged for motor fan and need to be replaced --> Damage during installation | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | 3 pin connectors damaged for motor fan and need to be replaced --> Damage during installation | 2026-03-10T07:54:11.000 | arun, jabesteen | PS5 - Milestone E
PL-004415 | PS5-78-JC-9100B |  | B | M | Control pendant height to be properly secured within the crane | CPP AGI | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:47:26.000 | Closed |  | Control pendant height to be properly secured within the crane | 2026-03-10T07:56:36.000 | arun, jabesteen | PS5 - Milestone E
PL-004416 | PS5-78-JC-9100B |  | B | E | Rectify the GAP between the C/T power supply and the pendant power supply to avoid any blockage | CPP AGI | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:49:32.000 | Closed |  | Rectify the GAP between the C/T power supply and the pendant power supply to avoid any blockage | 2026-03-10T07:58:23.000 | arun, jabesteen | PS5 - Milestone E
PL-004417 | PS5-78-JC-9100C |  | B | M | Guide rail anti-derailment to be installed | CPP AGI | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:49:50.000 | Closed |  | Guide rail anti-derailment to be installed | 2026-03-10T08:00:43.000 | arun, jabesteen | PS5 - Milestone E
PL-004418 | PS5-78-JC-9100C |  | B | M | Control pendant height to be properly secured within the crane | CPP AGI | PS5-78-01 - Lifting and handling equipment | 2026-05-02T05:50:23.000 | Closed |  | Control pendant height to be properly secured within the crane | 2026-03-10T08:02:37.000 | arun, jabesteen | PS5 - Milestone E
PL-004419 | PS5-78-JC-9100D |  | B | E | VSD failure during testing and need to be changed by vendor (Equipment failure) | EPS VENDOR | PS5-78-01 - Lifting and handling equipment |  | Originated |  | VSD failure during testing and need to be changed by vendor (Equipment failure) | 2026-03-10T08:09:08.000 | arun, jabesteen | PS5 - Milestone E
PL-004420 | PS5-78-JC-9100D |  | B | M | Damaged current collector (swapped to Crane C) to be changed | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | Damaged current collector (swapped to Crane C) to be changed | 2026-03-10T08:12:57.000 | arun, jabesteen | PS5 - Milestone E
PL-004423 | PS5-78-JC-9100A |  | C | E | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | 2026-03-10T08:26:08.000 | arun, jabesteen | PS5 - Milestone E
PL-004424 | PS5-78-JC-9100B |  | C | E | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | 2026-03-10T08:26:51.000 | arun, jabesteen | PS5 - Milestone E
PL-004425 | PS5-78-JC-9100C |  | C | E | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | 2026-03-10T08:27:09.000 | arun, jabesteen | PS5 - Milestone E
PL-004426 | PS5-78-JC-9100D |  | C | E | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | CPP AGI | PS5-78-01 - Lifting and handling equipment |  | Originated |  | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | 2026-03-10T08:27:19.000 | arun, jabesteen | PS5 - Milestone E
PL-004427 | PS5-71-UZ-6500 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-18 - Diesel Separator Module |  | Originated |  |  | 2026-03-10T12:36:04.680 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-004429 | PS5-71-UZ-6700 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-22 - Diesel Fuel Pre Pressure Module |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-10T12:44:16.187 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004433 | PS5-71-UZ-6400 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-08 - CFO Pre-Pressure Modules |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-10T12:52:50.320 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-004436 | PS5-71-UZ-6800A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-10T12:55:36.283 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-004439 | PS5-71-UZ-6800B |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-06 - Crude Fuel Separation Module |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-10T12:58:41.397 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-004454 | PS5-09-ACU-0007B-CG01 |  | A | E | PS005-E&I-M6-PL-2234 - Cable 1 side termination | EITS | PS5-63-04 - Electrical Earthing - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A
PL-004455 | PS5-09-ACU-0007A-CG01 |  | A | E | PS005-E&I-M6-PL-2236 - Cable 1 side termination | EITS | PS5-63-04 - Electrical Earthing - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A
PL-004456 | PS5-04-PNC-0002-CG02 |  | A | E | PS005-E&I-M4-PL-2238 - Cable 1 side termination | EITS | PS5-63-04 - Electrical Earthing - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0308 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A
PL-004457 | PS5-04-PNC-0001-CA64 |  | A | T | PS005-E&I-M4-PL-2350 - Port number (Terminal no.) N/A at interconnection drawing | EITS | PS5-04-03 - 33kV ICSS System | 2026-03-26T09:26:38.000 | Closed |  | Refer to Job Card BUILD-COW-0194 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A
PL-004458 | PS5-08-23AN-0004-CV01 |  | A | T | PS005-E&I-ALL-PL-2559 - Coaxial cable to be tested | EITS | PS5-08-23 - VHF Trunk Radio System |  | Originated |  | Refer to Job Card BUILD-COW-0105 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone F
PL-004459 | PS5-08-23AN-1001-CV01 |  | A | T | PS005-E&I-ALL-PL-2560 - Coaxial cable to be tested | EITS | PS5-08-23 - VHF Trunk Radio System |  | Originated |  | Refer to Job Card BUILD-COW-0105 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone F
PL-004460 | PS5-08-23AN-1002-CV01 |  | A | T | PS005-E&I-ALL-PL-2561 - Coaxial cable to be tested | EITS | PS5-08-23 - VHF Trunk Radio System |  | Originated |  | Refer to Job Card BUILD-COW-0105 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone F
PL-004546 | PS5-06-GB-0001A-CU01 |  | A | I | PS005-E&I-M1-PL-2592 - Cable gland for temperature cable sensor in battery room oversize ( General punch for all the buildings) | EITS | PS5-06-01 - AC UPS - EITS Building |  | Completed |  | Refer to Job Card BUILD-COW-0403 | 2026-03-12T10:52:23.000 | Thao-my, Alexandre | PS5 - Milestone A
PL-004547 | PS5-06-GB-0001B-CU01 |  | A | I | PS005-E&I-M1-PL-2592 - Cable gland for temperature cable sensor in battery room oversize ( General punch for all the buildings) | EITS | PS5-06-01 - AC UPS - EITS Building |  | Completed |  | Refer to Job Card BUILD-COW-0403 | 2026-03-12T10:52:23.000 | Thao-my, Alexandre | PS5 - Milestone A
PL-004548 | PS5-83-OB-0001 |  | A | B | PS005-E&I-M1-PL-2605 - The MCT installed in the battery room must be replaced with an Ex-rated MCT. | EITS | PS5-83-01 - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0404 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A
PL-004549 | PS5-83-OB-0001 |  | A | B | PS005-E&I-M1-PL-2605 - The MCT installed in the battery room must be replaced with an Ex-rated MCT. | EITS | PS5-83-01 - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0404 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A
PL-004550 | PS5-83-OB-0001 |  | A | B | PS005-E&I-M1-PL-2605 - The MCT installed in the battery room must be replaced with an Ex-rated MCT. | EITS | PS5-83-01 - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0404 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A
PL-004551 | PS5-83-OB-0001 |  | A | B | PS005-E&I-M1-PL-2605 - The MCT installed in the battery room must be replaced with an Ex-rated MCT. | EITS | PS5-83-01 - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0404 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A
PL-004552 | PS5-01-UB-6100 |  | C | M | PS005-MEC-ALL-PL-2606 - The name tag is messy, the letters are not straight line | EITS | PS5-01-09 - Inergen for EITS Building |  | Completed |  | Refer to Job Card BUILD-COW-0401 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A
PL-004596 | PS5-83-OB-0001 |  | C | B | PS005-ARC-ALL-PL-2612 - Poor quality of rubber gasket installed on the doors (easy to detaches and some contamined by water) to be replaced with the proper rubber gasket for industrial grade. | EITS | PS5-83-01 - EITS Building |  | Originated |  | Refer to BUILD-COW-0409 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A
PL-004605 | PS5-83-OB-0001 |  | B | B | PS005-E&I-ALL-PL-2609 - Earthing bonding jumpers drawing mark up to be provided. The shorted material to be provided such as earthing boss, bonding jumper 1core 70 mm2, bonding plate inclued holes and Bolt. | EITS | PS5-83-01 - EITS Building | 2026-05-06T07:01:47.000 | Closed |  | Refer to BUILD-COW-0402 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A
PL-004654 | PS5-09-PDT-0004 |  | B | I | PS005-E&I-COW-1827 - Pressure Differential Transmitters (PDTs) installed for the battery exhaust fans to be replaced with fit to purpose PDTs ( new complete product code 3051CD1A22A1KKSY2L4M5Q4Q8T1D0 / 7th digit = "1" for Differential Pressure Range type = –25 to +25 in H2O / (–62.16 to +62.16 mbar) | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0430 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A
PL-004655 | PS5-09-PDT-0005 |  | B | I | PS005-E&I-COW-1828 - Pressure Differential Transmitters (PDTs) installed for the battery exhaust fans to be replaced with fit to purpose PDTs ( new complete product code 3051CD1A22A1KKSY2L4M5Q4Q8T1D0 / 7th digit = "1" for Differential Pressure Range type = –25 to +25 in H2O / (–62.16 to +62.16 mbar) | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0430 | 2026-03-12T10:52:23.767 | Thao-my, Alexandre | PS5 - Milestone A
PL-004837 | PS5-60-UA-5100 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-27 - Compressed Air Starting Skid |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-28T08:02:01.077 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004838 | PS5-60-UA-5200 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-26 - Instrument Air Compressor Skid |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-28T08:05:51.737 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-004839 | PS5-71-UN-7200 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-71-02 - CFO Allocation Metering Package |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-28T08:30:49.017 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-004840 | PS5-01-UV-8700 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-01-05 - Foam Skid |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-28T08:37:30.830 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-004841 | PS5-71-UZ-6200 |  | A | M | 10:OSD PUNCH POINTS TO BE CLOSED | CPP AGI | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station |  | Originated |  | OSD PUNCH POINTS TO BE CLOSED | 2026-03-28T08:40:06.517 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-004842 | PS5-01-UZ-6900 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-01-10 - Water Mist Package |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-28T08:43:14.887 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-004843 | PS5-01-UK-6100 |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100) |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-03-28T14:03:11.827 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-004844 | PS5-71-TR-4200 |  | A | M | During verification of loose materials received from Velath, I have found some issues which is related to materials. Some spools received from the vendor for the Deluge system are not fabricated as per drawing. N9 The spool received is not as per the drawing(3x2 reducer and 3” flange was not welded with the spool and 2” flange welded.). | EPS VENDOR | PS5-71-12 - CFO Service Tank |  | Originated |  | Vendor to rectify | 2026-03-30T10:34:23.000 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-004865 | PS5-04-PNC-0001-CA05 |  | A | T | PS005-E&I-COW-1935 - Cable terminations to be done (Network Cabinet) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004866 | PS5-04-PNC-0001-CA06 |  | A | T | PS005-E&I-COW-1936 - Cable terminations to be done (Network Cabinet) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004867 | PS5-04-PNC-0001-CA07 |  | A | T | PS005-E&I-COW-1937 - Cable terminations to be done (Network Cabinet) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004868 | PS5-04-PNC-0001-CA08 |  | A | T | PS005-E&I-COW-1938 - Cable terminations to be done (Network Cabinet) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004869 | PS5-04-PNC-0001-CA09 |  | A | T | PS005-E&I-COW-1939 - Cable terminations to be done (Network Cabinet) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004870 | PS5-04-PNC-0001-CA10 |  | A | T | PS005-E&I-COW-1940 - Cable terminations to be done (Network Cabinet) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004871 | PS5-04-PNC-0001-CA11 |  | A | T | PS005-E&I-COW-1941 - Cable terminations to be done (Network Cabinet) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004872 | PS5-04-PNC-0001-CA13 |  | A | T | PS005-E&I-COW-1942 - Cable terminations to be done (Network Cabinet) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004873 | PS5-04-PNC-0001-CA14 |  | A | T | PS005-E&I-COW-1943 - Cable terminations to be done (Network Cabinet) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004874 | PS5-04-PNC-0001-CA30 |  | A | T | PS005-E&I-COW-1944 - Cable terminations to be done (Network Cabinet) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004875 | PS5-04-PNC-0001-CA31 |  | A | T | PS005-E&I-COW-1945 - Cable terminations to be done (Network Cabinet) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004876 | PS5-04-PNC-0001-CA74 |  | A | T | PS005-E&I-COW-1946 - Cable terminations to be done (Network Cabinet) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004877 | PS5-04-PNC-0001-CA90 |  | A | T | PS005-E&I-COW-1947 - Cable terminations to be done (Network Cabinet) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004878 | PS5-04-PNC-0001-CA91 |  | A | T | PS005-E&I-COW-1948 - Cable terminations to be done (Network Cabinet) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004879 | PS5-04-PNC-0001-CJ01 |  | A | I | PS005-E&I-COW-1934 - Cable terminations to be done (Network Cabinet) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004880 | PS5-04-PNC-0001-CS01 |  | A | E | PS005-E&I-COW-1949 - Cable terminations to be done (Network Cabinet) | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004881 | PS5-08-11CB-1001-CA20 |  | A | T | PS005-E&I-COW-1950 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-11 - Corporate LAN (SIE) |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004882 | PS5-08-11CB-1001-CA21 |  | A | T | PS005-E&I-COW-1951 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-11 - Corporate LAN (SIE) |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004883 | PS5-08-11CB-1001-CA22 |  | A | T | PS005-E&I-COW-1952 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-11 - Corporate LAN (SIE) |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004884 | PS5-08-11CB-1001-CA23 |  | A | T | PS005-E&I-COW-1953 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-11 - Corporate LAN (SIE) |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004885 | PS5-08-11CB-1001-CA24 |  | A | T | PS005-E&I-COW-1954 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-11 - Corporate LAN (SIE) |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004886 | PS5-08-35CB-1001-CA01 |  | A | T | PS005-E&I-COW-1955 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004887 | PS5-08-35CB-1001-CA02 |  | A | T | PS005-E&I-COW-1956 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004888 | PS5-08-35CB-1001-CA03 |  | A | T | PS005-E&I-COW-1957 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004889 | PS5-08-35CB-1001-CA04 |  | A | T | PS005-E&I-COW-1958 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004890 | PS5-08-35CB-1001-CA05 |  | A | T | PS005-E&I-COW-1959 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004891 | PS5-08-35CB-1001-CA06 |  | A | T | PS005-E&I-COW-1960 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004892 | PS5-08-35CB-1001-CA07 |  | A | T | PS005-E&I-COW-1961 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004893 | PS5-08-35CB-1001-CA08 |  | A | T | PS005-E&I-COW-1962 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004894 | PS5-08-35CB-1001-CA09 |  | A | T | PS005-E&I-COW-1963 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004895 | PS5-08-35CB-1001-CA10 |  | A | T | PS005-E&I-COW-1964 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004896 | PS5-08-35CB-1001-CA11 |  | A | T | PS005-E&I-COW-1965 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004897 | PS5-08-35CB-1001-CA12 |  | A | T | PS005-E&I-COW-1966 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004898 | PS5-08-35CB-1001-CA13 |  | A | T | PS005-E&I-COW-1967 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004899 | PS5-08-35CB-1001-CA14 |  | A | T | PS005-E&I-COW-1968 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004900 | PS5-08-35CB-1001-CA15 |  | A | T | PS005-E&I-COW-1969 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004901 | PS5-08-35CB-1001-CA16 |  | A | T | PS005-E&I-COW-1970 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004902 | PS5-08-35CB-1001-CA17 |  | A | T | PS005-E&I-COW-1971 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004903 | PS5-08-35CB-1001-CA18 |  | A | T | PS005-E&I-COW-1972 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004904 | PS5-08-35CB-1001-CA19 |  | A | T | PS005-E&I-COW-1973 - Cable terminations to be done (Network Cabinet) | EITS | PS5-08-35 - Optical Transport Network |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004905 | PS5-04-PMC-0005-CJ01 |  | A | I | PS005-E&I-COW-1974 - New cable to be added | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0304 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004906 | PS5-04-PMC-0008-CC59 |  | A | I | PS005-E&I-COW-1975 - New cable to be added | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0304 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004907 | PS5-04-PNC-0001-CA94 |  | A | T | PS005-E&I-COW-1976 - New cable to be added | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0304 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004908 | PS5-04-PNC-0001-CA95 |  | A | T | PS005-E&I-COW-1977 - New cable to be added | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0304 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004909 | PS5-08-13CB-1001-CA24 |  | A | T | PS005-E&I-COW-1978 - New cable to be added | EITS | PS5-08-13 - Safety Data Network (SII SP3 SAF) |  | Originated |  | Refer to Job Card BUILD-COW-0304 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004910 | PS5-09-AS-0001A-CD01 |  | A | E | PS005-E&I-COW-1979 - Cable to be removed | EITS | PS5-09-05 - HVAC for EITS Building |  | Completed |  | Refer to Job Card BUILD-COW-0308 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004911 | PS5-09-AS-0001B-CD01 |  | A | E | PS005-E&I-COW-1980 - Cable to be removed | EITS | PS5-09-05 - HVAC for EITS Building |  | Completed |  | Refer to Job Card BUILD-COW-0308 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004912 | PS5-09-AS-0002A-CD01 |  | A | E | PS005-E&I-COW-1981 - Cable to be removed | EITS | PS5-09-05 - HVAC for EITS Building |  | Completed |  | Refer to Job Card BUILD-COW-0308 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004913 | PS5-09-AS-0002B-CD01 |  | A | E | PS005-E&I-COW-1982 - Cable to be removed | EITS | PS5-09-05 - HVAC for EITS Building |  | Completed |  | Refer to Job Card BUILD-COW-0308 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004914 | PS5-61-IJ-0011-CA03 |  | A | T | PS005-E&I-COW-1983 - New cable to be added | EITS | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  | Refer to Job Card BUILD-COW-0304 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone G
PL-004915 | PS5-61-IE-0003-CS03 |  | A | E | PS005-E&I-COW-1984 - Cable to be removed | EITS | PS5-61-08 - Electrical Control System |  | Originated |  | Refer to Job Card BUILD-COW-0308 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-004916 | PS5-04-PNC-0001-CA81 |  | A | T | PS005-E&I-COW-1985 - Cable to be removed | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0308 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004917 | PS5-01-LA-0001-CL03 |  | B | E | PS005-E&I-COW-1986 - Cable TAG labels to be changed | EITS | PS5-0H-01 - HIPPS |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone H
PL-004918 | PS5-03-SFSC-0001-CZ01 |  | B | I | PS005-E&I-COW-1987 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004919 | PS5-03-SFSC-0001-CZ02 |  | B | I | PS005-E&I-COW-1988 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004920 | PS5-03-SFSC-0001-CZ03 |  | B | I | PS005-E&I-COW-1989 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004921 | PS5-03-SFSC-0001-CZ04 |  | B | I | PS005-E&I-COW-1990 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004922 | PS5-03-SFSC-0001-CZ05 |  | B | I | PS005-E&I-COW-1991 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004923 | PS5-03-SFSC-0001-CZ06 |  | B | I | PS005-E&I-COW-1992 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004924 | PS5-03-SFSC-0001-CZ07 |  | B | I | PS005-E&I-COW-1993 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004925 | PS5-03-SFSC-0001-CZ08 |  | B | I | PS005-E&I-COW-1994 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004926 | PS5-03-SFSC-0001-CZ09 |  | B | I | PS005-E&I-COW-1995 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004927 | PS5-03-SFSC-0001-CZ10 |  | B | I | PS005-E&I-COW-1996 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004928 | PS5-03-SFSC-0002-CZ01 |  | B | I | PS005-E&I-COW-1997 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004929 | PS5-03-SFSC-0002-CZ02 |  | B | I | PS005-E&I-COW-1998 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004930 | PS5-03-SFSC-0002-CZ03 |  | B | I | PS005-E&I-COW-1999 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004931 | PS5-03-SFSC-0002-CZ04 |  | B | I | PS005-E&I-COW-2000 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004932 | PS5-03-SFSC-0002-CZ05 |  | B | I | PS005-E&I-COW-2001 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004933 | PS5-03-SFSC-0002-CZ06 |  | B | I | PS005-E&I-COW-2002 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004934 | PS5-03-SFSC-0002-CZ07 |  | B | I | PS005-E&I-COW-2003 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004935 | PS5-03-SFSC-0002-CZ08 |  | B | I | PS005-E&I-COW-2004 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004936 | PS5-03-SFSC-0002-CZ09 |  | B | I | PS005-E&I-COW-2005 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004937 | PS5-03-SFSC-0002-CZ10 |  | B | I | PS005-E&I-COW-2006 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004938 | PS5-03-SFSC-0002-CZ11 |  | B | I | PS005-E&I-COW-2007 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004939 | PS5-03-SFSC-0002-CZ12 |  | B | I | PS005-E&I-COW-2008 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004940 | PS5-03-SFSC-0002-CZ13 |  | B | I | PS005-E&I-COW-2009 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004941 | PS5-03-SFSC-0002-CZ14 |  | B | I | PS005-E&I-COW-2010 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004942 | PS5-03-SFSC-0002-CZ15 |  | B | I | PS005-E&I-COW-2011 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004943 | PS5-03-SFSC-0003-CZ01 |  | B | I | PS005-E&I-COW-2012 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004944 | PS5-03-SFSC-0003-CZ02 |  | B | I | PS005-E&I-COW-2013 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004945 | PS5-03-SFSC-0003-CZ03 |  | B | I | PS005-E&I-COW-2014 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004946 | PS5-03-SFSC-0003-CZ04 |  | B | I | PS005-E&I-COW-2015 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004947 | PS5-03-SFSC-0003-CZ05 |  | B | I | PS005-E&I-COW-2016 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004948 | PS5-03-SFSC-0003-CZ06 |  | B | I | PS005-E&I-COW-2017 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004949 | PS5-03-SFSC-0003-CZ07 |  | B | I | PS005-E&I-COW-2018 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004950 | PS5-03-SFSC-0003-CZ08 |  | B | I | PS005-E&I-COW-2019 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004951 | PS5-03-SFSC-0003-CZ09 |  | B | I | PS005-E&I-COW-2020 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004952 | PS5-03-SFSC-0003-CZ10 |  | B | I | PS005-E&I-COW-2021 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004953 | PS5-03-SFSC-0003-CZ11 |  | B | I | PS005-E&I-COW-2022 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004954 | PS5-03-SFSC-0003-CZ12 |  | B | I | PS005-E&I-COW-2023 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004955 | PS5-03-SFSC-0003-CZ13 |  | B | I | PS005-E&I-COW-2024 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004956 | PS5-03-SFSC-0003-CZ14 |  | B | I | PS005-E&I-COW-2025 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004957 | PS5-03-SFSC-0003-CZ15 |  | B | I | PS005-E&I-COW-2026 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004958 | PS5-03-SFSC-0003-CZ16 |  | B | I | PS005-E&I-COW-2027 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004959 | PS5-03-SFSC-0004-CZ01 |  | B | I | PS005-E&I-COW-2028 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004960 | PS5-03-SFSC-0004-CZ02 |  | B | I | PS005-E&I-COW-2029 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004961 | PS5-03-SFSC-0004-CZ03 |  | B | I | PS005-E&I-COW-2030 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004962 | PS5-03-SFSC-0004-CZ04 |  | B | I | PS005-E&I-COW-2031 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004963 | PS5-03-SFSC-0004-CZ05 |  | B | I | PS005-E&I-COW-2032 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004964 | PS5-03-SFSC-0004-CZ06 |  | B | I | PS005-E&I-COW-2033 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004965 | PS5-03-SFSC-0004-CZ07 |  | B | I | PS005-E&I-COW-2034 - Cable TAG labels to be changed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004966 | PS5-04-PMC-0005-CJ02 |  | B | I | PS005-E&I-COW-2035 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004967 | PS5-04-PNC-0001-CA75 |  | B | T | PS005-E&I-COW-2036 - Cable TAG labels to be changed | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004968 | PS5-04-PSC-0001-CZ01 |  | B | I | PS005-E&I-COW-2037 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004969 | PS5-04-PSC-0001-CZ02 |  | B | I | PS005-E&I-COW-2038 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004970 | PS5-04-PSC-0001-CZ03 |  | B | I | PS005-E&I-COW-2039 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004971 | PS5-04-PSC-0001-CZ04 |  | B | I | PS005-E&I-COW-2040 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004972 | PS5-04-PSC-0001-CZ05 |  | B | I | PS005-E&I-COW-2041 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004973 | PS5-04-PSC-0001-CZ06 |  | B | I | PS005-E&I-COW-2042 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004974 | PS5-04-PSC-0001-CZ07 |  | B | I | PS005-E&I-COW-2043 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004975 | PS5-04-PSC-0001-CZ08 |  | B | I | PS005-E&I-COW-2044 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004976 | PS5-04-PSC-0001-CZ09 |  | B | I | PS005-E&I-COW-2045 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004977 | PS5-04-PSC-0001-CZ10 |  | B | I | PS005-E&I-COW-2046 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004978 | PS5-04-PSC-0001-CZ11 |  | B | I | PS005-E&I-COW-2047 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004979 | PS5-04-PSC-0001-CZ12 |  | B | I | PS005-E&I-COW-2048 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004980 | PS5-04-PSC-0001-CZ13 |  | B | I | PS005-E&I-COW-2049 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004981 | PS5-04-PSC-0001-CZ14 |  | B | I | PS005-E&I-COW-2050 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004982 | PS5-04-PSC-0001-CZ15 |  | B | I | PS005-E&I-COW-2051 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004983 | PS5-04-PSC-0001-CZ16 |  | B | I | PS005-E&I-COW-2052 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004984 | PS5-04-PSC-0001-CZ17 |  | B | I | PS005-E&I-COW-2053 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004985 | PS5-04-PSC-0001-CZ18 |  | B | I | PS005-E&I-COW-2054 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004986 | PS5-04-PSC-0001-CZ19 |  | B | I | PS005-E&I-COW-2055 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004987 | PS5-04-PSC-0001-CZ20 |  | B | I | PS005-E&I-COW-2056 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004988 | PS5-04-PSC-0001-CZ21 |  | B | I | PS005-E&I-COW-2057 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004989 | PS5-04-PSC-0001-CZ22 |  | B | I | PS005-E&I-COW-2058 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004990 | PS5-04-PSC-0001-CZ23 |  | B | I | PS005-E&I-COW-2059 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004991 | PS5-04-PSC-0001-CZ24 |  | B | I | PS005-E&I-COW-2060 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004992 | PS5-04-PSC-0001-CZ25 |  | B | I | PS005-E&I-COW-2061 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004993 | PS5-04-PSC-0001-CZ26 |  | B | I | PS005-E&I-COW-2062 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004994 | PS5-04-PSC-0001-CZ27 |  | B | I | PS005-E&I-COW-2063 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004995 | PS5-04-PSC-0001-CZ28 |  | B | I | PS005-E&I-COW-2064 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004996 | PS5-04-PSC-0002-CZ01 |  | B | I | PS005-E&I-COW-2065 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004997 | PS5-04-PSC-0002-CZ02 |  | B | I | PS005-E&I-COW-2066 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004998 | PS5-04-PSC-0002-CZ03 |  | B | I | PS005-E&I-COW-2067 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-004999 | PS5-04-PSC-0002-CZ04 |  | B | I | PS005-E&I-COW-2068 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005000 | PS5-04-PSC-0002-CZ05 |  | B | I | PS005-E&I-COW-2069 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005001 | PS5-04-PSC-0002-CZ06 |  | B | I | PS005-E&I-COW-2070 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005002 | PS5-04-PSC-0002-CZ07 |  | B | I | PS005-E&I-COW-2071 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005003 | PS5-04-PSC-0002-CZ08 |  | B | I | PS005-E&I-COW-2072 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005004 | PS5-04-PSC-0002-CZ09 |  | B | I | PS005-E&I-COW-2073 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005005 | PS5-04-PSC-0002-CZ10 |  | B | I | PS005-E&I-COW-2074 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005006 | PS5-04-PSC-0002-CZ11 |  | B | I | PS005-E&I-COW-2075 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005007 | PS5-04-PSC-0002-CZ12 |  | B | I | PS005-E&I-COW-2076 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005008 | PS5-04-PSC-0002-CZ13 |  | B | I | PS005-E&I-COW-2077 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005009 | PS5-04-PSC-0002-CZ14 |  | B | I | PS005-E&I-COW-2078 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005010 | PS5-04-PSC-0002-CZ15 |  | B | I | PS005-E&I-COW-2079 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005011 | PS5-04-PSC-0002-CZ16 |  | B | I | PS005-E&I-COW-2080 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005012 | PS5-04-PSC-0002-CZ17 |  | B | I | PS005-E&I-COW-2081 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005013 | PS5-04-PSC-0002-CZ18 |  | B | I | PS005-E&I-COW-2082 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005014 | PS5-04-PSC-0002-CZ19 |  | B | I | PS005-E&I-COW-2083 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005015 | PS5-04-PSC-0002-CZ20 |  | B | I | PS005-E&I-COW-2084 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005016 | PS5-04-PSC-0002-CZ21 |  | B | I | PS005-E&I-COW-2085 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005017 | PS5-04-PSC-0002-CZ22 |  | B | I | PS005-E&I-COW-2086 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005018 | PS5-04-PSC-0002-CZ23 |  | B | I | PS005-E&I-COW-2087 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005019 | PS5-04-PSC-0002-CZ24 |  | B | I | PS005-E&I-COW-2088 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005020 | PS5-04-PSC-0002-CZ25 |  | B | I | PS005-E&I-COW-2089 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005021 | PS5-04-PSC-0002-CZ26 |  | B | I | PS005-E&I-COW-2090 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005022 | PS5-04-PSC-0002-CZ27 |  | B | I | PS005-E&I-COW-2091 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005023 | PS5-04-PSC-0002-CZ28 |  | B | I | PS005-E&I-COW-2092 - Cable TAG labels to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005024 | PS5-05-IG-0003-CD51 |  | B | E | PS005-E&I-COW-2093 - Cable TAG labels to be changed | EITS | PS5-62-12 - EITS 33kV Bld. Emergency L&SP DP - PS5-05-IG-0003 |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005025 | PS5-05-IG-0003-CS51 |  | B | E | PS005-E&I-COW-2094 - Cable TAG labels to be changed | EITS | PS5-62-12 - EITS 33kV Bld. Emergency L&SP DP - PS5-05-IG-0003 |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005026 | PS5-06-GU-0001A-CA01 |  | B | T | PS005-E&I-COW-2095 - Cable TAG labels to be changed | EITS | PS5-06-01 - AC UPS - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005027 | PS5-06-GU-0001A-CA02 |  | B | T | PS005-E&I-COW-2096 - Cable TAG labels to be changed | EITS | PS5-06-01 - AC UPS - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005028 | PS5-06-GU-0001B-CA03 |  | B | T | PS005-E&I-COW-2097 - Cable TAG labels to be changed | EITS | PS5-06-01 - AC UPS - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005029 | PS5-06-GU-0001B-CA04 |  | B | T | PS005-E&I-COW-2098 - Cable TAG labels to be changed | EITS | PS5-06-01 - AC UPS - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005030 | PS5-08-23AN-0004-CV01 |  | B | T | PS005-E&I-COW-2099 - Cable TAG labels to be changed | EITS | PS5-08-23 - VHF Trunk Radio System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone F
PL-005031 | PS5-08-23AN-1001-CV01 |  | B | T | PS005-E&I-COW-2100 - Cable TAG labels to be changed | EITS | PS5-08-23 - VHF Trunk Radio System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone F
PL-005032 | PS5-08-23AN-1002-CV01 |  | B | T | PS005-E&I-COW-2101 - Cable TAG labels to be changed | EITS | PS5-08-23 - VHF Trunk Radio System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone F
PL-005033 | PS5-09-IES-0002-CD02 |  | B | E | PS005-E&I-COW-2102 - Cable TAG labels to be changed | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005034 | PS5-09-PDT-0001-CJ01 |  | B | I | PS005-E&I-COW-2103 - Cable TAG labels to be changed | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005035 | PS5-09-PDT-0002-CJ01 |  | B | I | PS005-E&I-COW-2104 - Cable TAG labels to be changed | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005036 | PS5-09-PDT-0003-CJ01 |  | B | I | PS005-E&I-COW-2105 - Cable TAG labels to be changed | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005037 | PS5-25-IE-0001-CA01 |  | B | T | PS005-E&I-COW-2106 - Cable TAG labels to be changed | EITS | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone H
PL-005038 | PS5-61-IE-0002-CD37 |  | B | E | PS005-E&I-COW-2107 - Cable TAG labels to be changed | EITS | PS5-61-08 - Electrical Control System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-005039 | PS5-61-IE-0002-CD38 |  | B | E | PS005-E&I-COW-2108 - Cable TAG labels to be changed | EITS | PS5-61-08 - Electrical Control System |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone C
PL-005040 | PS5-61-IG-0003-CD51 |  | B | E | PS005-E&I-COW-2109 - Cable TAG labels to be changed | EITS | PS5-62-13 - EITS 33kV Bld. Normal L&SP DP - PS5-61-IG-0003 |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005041 | PS5-61-IG-0003-CS51 |  | B | E | PS005-E&I-COW-2110 - Cable TAG labels to be changed | EITS | PS5-62-13 - EITS 33kV Bld. Normal L&SP DP - PS5-61-IG-0003 |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005042 | PS5-61-IJ-0001-CA01 |  | B | T | PS005-E&I-COW-2111 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005043 | PS5-61-IJ-0001-CA02 |  | B | T | PS005-E&I-COW-2112 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005044 | PS5-61-IJ-0001-CA03 |  | B | T | PS005-E&I-COW-2113 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005045 | PS5-61-IJ-0001-CA04 |  | B | T | PS005-E&I-COW-2114 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005046 | PS5-61-IJ-0001-CA05 |  | B | T | PS005-E&I-COW-2115 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005047 | PS5-61-IJ-0001-CA06 |  | B | T | PS005-E&I-COW-2116 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005048 | PS5-61-IJ-0001-CA07 |  | B | T | PS005-E&I-COW-2117 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005049 | PS5-61-IJ-0001-CD70 |  | B | E | PS005-E&I-COW-2118 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005050 | PS5-61-IJ-0001-CD74 |  | B | E | PS005-E&I-COW-2119 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005051 | PS5-61-IJ-0001-CD75 |  | B | E | PS005-E&I-COW-2120 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005052 | PS5-61-IJ-0001-CD76 |  | B | E | PS005-E&I-COW-2121 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005053 | PS5-61-IJ-0001-CD77 |  | B | E | PS005-E&I-COW-2122 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005054 | PS5-61-IJ-0001-CD78 |  | B | E | PS005-E&I-COW-2123 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005055 | PS5-61-IJ-0001-CD79 |  | B | E | PS005-E&I-COW-2124 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005056 | PS5-61-IJ-0001-CD80 |  | B | E | PS005-E&I-COW-2125 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005057 | PS5-61-IJ-0001-CD81 |  | B | E | PS005-E&I-COW-2126 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005058 | PS5-61-IJ-0001-CD82 |  | B | E | PS005-E&I-COW-2127 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005059 | PS5-61-IJ-0001-CD83 |  | B | E | PS005-E&I-COW-2128 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005060 | PS5-61-IJ-0001-CD84 |  | B | E | PS005-E&I-COW-2129 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005061 | PS5-61-IJ-0001-CD85 |  | B | E | PS005-E&I-COW-2130 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005062 | PS5-61-IJ-0001-CD86 |  | B | E | PS005-E&I-COW-2131 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005063 | PS5-61-IJ-0001-CD87 |  | B | E | PS005-E&I-COW-2132 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005064 | PS5-61-IJ-0001-CD88 |  | B | E | PS005-E&I-COW-2133 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005065 | PS5-61-IJ-0001-CD89 |  | B | E | PS005-E&I-COW-2134 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005066 | PS5-61-IJ-0001-CD90 |  | B | E | PS005-E&I-COW-2135 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005067 | PS5-61-IJ-0001-CD91 |  | B | E | PS005-E&I-COW-2136 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005068 | PS5-61-IJ-0001-CD92 |  | B | E | PS005-E&I-COW-2137 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005069 | PS5-61-IJ-0001-CD93 |  | B | E | PS005-E&I-COW-2138 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005070 | PS5-61-IJ-0001-CD94 |  | B | E | PS005-E&I-COW-2139 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005071 | PS5-61-IJ-0001-CD95 |  | B | E | PS005-E&I-COW-2140 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005072 | PS5-61-IJ-0001-CD96 |  | B | E | PS005-E&I-COW-2141 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005073 | PS5-61-IJ-0001-CD97 |  | B | E | PS005-E&I-COW-2142 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005074 | PS5-61-IJ-0001-CD98 |  | B | E | PS005-E&I-COW-2143 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005075 | PS5-61-IJ-0001-CD99 |  | B | E | PS005-E&I-COW-2144 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005076 | PS5-61-IJ-0001-CS01 |  | B | E | PS005-E&I-COW-2145 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005077 | PS5-61-IJ-0001-CS02 |  | B | E | PS005-E&I-COW-2146 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005078 | PS5-61-IJ-0001-CS03 |  | B | E | PS005-E&I-COW-2147 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005079 | PS5-61-IJ-0001-CS04 |  | B | E | PS005-E&I-COW-2148 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005080 | PS5-61-IJ-0001-CS05 |  | B | E | PS005-E&I-COW-2149 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005081 | PS5-61-IJ-0001-CS06 |  | B | E | PS005-E&I-COW-2150 - Cable TAG labels to be changed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone D
PL-005082 | PS5-61-IJ-0010-CA01 |  | B | T | PS005-E&I-COW-2151 - Cable TAG labels to be changed | EITS | PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone G
PL-005083 | PS5-61-IJ-0010-CA02 |  | B | T | PS005-E&I-COW-2152 - Cable TAG labels to be changed | EITS | PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone G
PL-005084 | PS5-61-IJ-0011-CA01 |  | B | T | PS005-E&I-COW-2153 - Cable TAG labels to be changed | EITS | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone G
PL-005085 | PS5-61-IJ-0011-CA02 |  | B | T | PS005-E&I-COW-2154 - Cable TAG labels to be changed | EITS | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone G
PL-005086 | PS5-61-IJ-0011-CD03 |  | B | E | PS005-E&I-COW-2155 - Cable TAG labels to be changed | EITS | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone G
PL-005087 | PS5-61-IK-0001-CA01 |  | B | T | PS005-E&I-COW-2156 - Cable TAG labels to be changed | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005088 | PS5-61-IK-0001-CA02 |  | B | T | PS005-E&I-COW-2157 - Cable TAG labels to be changed | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005089 | PS5-61-IK-0001-CA03 |  | B | T | PS005-E&I-COW-2158 - Cable TAG labels to be changed | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005090 | PS5-61-IK-0001-CA04 |  | B | T | PS005-E&I-COW-2159 - Cable TAG labels to be changed | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005091 | PS5-61-IK-0001-CA05 |  | B | T | PS005-E&I-COW-2160 - Cable TAG labels to be changed | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005092 | PS5-61-IK-0001-CS01 |  | B | E | PS005-E&I-COW-2161 - Cable TAG labels to be changed | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005093 | PS5-61-IK-0001-CS02 |  | B | E | PS005-E&I-COW-2162 - Cable TAG labels to be changed | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005094 | PS5-61-IK-0001-CS03 |  | B | E | PS005-E&I-COW-2163 - Cable TAG labels to be changed | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005095 | PS5-61-IK-0001-CS04 |  | B | E | PS005-E&I-COW-2164 - Cable TAG labels to be changed | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005096 | PS5-61-IK-0001-CS05 |  | B | E | PS005-E&I-COW-2165 - Cable TAG labels to be changed | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005097 | PS5-61-IK-0001-CS06 |  | B | E | PS005-E&I-COW-2166 - Cable TAG labels to be changed | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone A
PL-005098 | PS5-71-IE-0001-CC01 |  | B | I | PS005-E&I-COW-2167 - Cable TAG labels to be changed | EITS | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone H
PL-005099 | PS5-71-IE-0001-CC02 |  | B | I | PS005-E&I-COW-2168 - Cable TAG labels to be changed | EITS | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone H
PL-005100 | PS5-71-IE-0002-CC01 |  | B | I | PS005-E&I-COW-2169 - Cable TAG labels to be changed | EITS | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone H
PL-005101 | PS5-71-IE-0002-CC02 |  | B | I | PS005-E&I-COW-2170 - Cable TAG labels to be changed | EITS | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  | Refer to Job Card BUILD-COW-0309 | 2026-04-07T05:54:40.243 | Thao-my, Alexandre | PS5 - Milestone H
PL-005182 | PS5-01-UV-8700 |  | A | M | Internal piping within the skid to be completed & reinstated | CPP AGI | PS5-01-05 - Foam Skid |  | Originated |  | Internal piping within the skid to be completed & reinstated | 2026-04-13T07:20:30.000 | arun, jabesteen | PS5 - Milestone F
PL-005183 | PS5-01-UV-8700 |  | A | M | OSD points to be cleared and closed | EPS VENDOR | PS5-01-05 - Foam Skid |  | Originated |  | OSD points to be cleared and closed | 2026-04-13T07:22:16.000 | arun, jabesteen | PS5 - Milestone F
PL-005184 | PS5-01-UV-8700 |  | C | M | Touch up painting to be completed | CPP AGI | PS5-01-05 - Foam Skid |  | Originated |  | Touch up painting to be completed | 2026-04-13T07:24:33.000 | arun, jabesteen | PS5 - Milestone F
PL-005252 | PS5-53-TR-4100 |  | A | M | Opening of cage ladder fabricated in the wrong direction. To be corrected as per drawing (requirement) | EPS VENDOR | PS5-53-01 - Utility Water / Storage Tank |  | Originated |  | VENDOR TO RECTIFY | 2026-04-14T06:05:04.000 | THANGARATHINAM, ajikumar | PS5 - Milestone C
PL-005263 | PS5-60-UR-8300A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-35 - Injector Tip Cooling Module A |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-04-17T12:19:51.787 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-005265 | PS5-60-UR-8300B |  | B | P | 10.1:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-36 - Injector Tip Cooling Module B |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-04-17T12:22:27.747 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-005266 | PS5-60-UR-8300C |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-37 - Injector Tip Cooling Module C |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-04-17T12:25:51.313 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-005267 | PS5-60-UR-8300D |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-38 - Injector Tip Cooling Module D |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-04-17T12:27:21.450 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-005268 | PS5-60-UR-8300E |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-39 - Injector Tip Cooling Module E |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-04-17T12:28:55.007 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-005269 | PS5-60-UR-8300F |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-40 - Injector Tip Cooling Module F |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-04-17T12:30:30.900 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-005270 | PS5-60-UR-8300G |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-41 - Injector Tip Cooling Module G |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-04-17T12:32:08.740 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-005299 | PS5-60-VA-5100C |  | B | E | 23.1: EARTHING TO BE DONE | CPP AGI | PS5-60-30 - Air Receiver C & Air Regulator C |  | Originated |  | EARTHING TO BE DONE | 2026-04-21T07:58:44.537 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-005300 | PS5 - CFO AREA_Earthing |  | B | E | 7 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install all earth bosses as per the drawing and proceed with the termination of the earthing cables at the bosses and equipment | 2026-04-21T11:23:42.880 | Mohamed, Amira | PS5 - Milestone A
PL-005308 | PS5-61-IJ-0001-CH01 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-21T12:38:25.000 | Mohamed, Amira | PS5 - Milestone B
PL-005309 | PS5-61-IJ-0001-CH02 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-21T14:21:05.427 | Mohamed, Amira | PS5 - Milestone B
PL-005310 | PS5-61-IJ-0001-CH03 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-01 - Power Generation Package A |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-21T14:23:54.797 | Mohamed, Amira | PS5 - Milestone B
PL-005311 | PS5-61-IJ-0001-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-21T14:25:28.087 | Mohamed, Amira | PS5 - Milestone B
PL-005312 | PS5-61-IJ-0001-CH05 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-21T14:28:49.000 | Mohamed, Amira | PS5 - Milestone B
PL-005313 | PS5-61-IJ-0001-CH06 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-04 - Power Generation Package B |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-21T14:32:16.990 | Mohamed, Amira | PS5 - Milestone B
PL-005314 | PS5-61-IJ-0001-CH07 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-22T06:19:24.473 | Mohamed, Amira | PS5 - Milestone D
PL-005315 | PS5-61-IJ-0001-CH08 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-22T06:22:02.900 | Mohamed, Amira | PS5 - Milestone D
PL-005318 | PS5-61-IJ-0001-CH09 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-07 - Power Generation Package C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-22T08:07:20.090 | Mohamed, Amira | PS5 - Milestone D
PL-005415 | PS5-61-IJ-0001 |  | A | E | PS005-E&I-COW-2194 - CTs and secondary wiring are not installed in side CT Box | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0470 | 2026-04-22T09:53:13.457 | Thao-my, Alexandre | PS5 - Milestone D
PL-005428 | PS5-06-GU-0001-CC03 |  | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-06-GU-0001-CC03 INSTRUMENTATION CABLE | EITS | PS5-06-01 - AC UPS - EITS Building |  | Originated |  | Refer to BUILD-COW-0082 | 2026-04-22T09:53:13.457 | Thao-my, Alexandre | PS5 - Milestone A
PL-005429 | PS5-06-GU-0001-CC04 |  | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-06-GU-0001-CC04 INSTRUMENTATION CABLE | EITS | PS5-06-01 - AC UPS - EITS Building |  | Originated |  | Refer to BUILD-COW-0082 | 2026-04-22T09:53:13.457 | Thao-my, Alexandre | PS5 - Milestone A
PL-005430 | PS5-06-GU-0001-CJ01 |  | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-06-GU-0001-CJ01 INSTRUMENTATION CABLE | EITS | PS5-06-01 - AC UPS - EITS Building |  | Originated |  | Refer to BUILD-COW-0082 | 2026-04-22T09:53:13.457 | Thao-my, Alexandre | PS5 - Milestone A
PL-005431 | PS5-06-GU-0001-CJ02 |  | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-06-GU-0001-CJ02 INSTRUMENTATION CABLE | EITS | PS5-06-01 - AC UPS - EITS Building |  | Originated |  | Refer to BUILD-COW-0082 | 2026-04-22T09:53:13.457 | Thao-my, Alexandre | PS5 - Milestone A
PL-005432 | PS5-08-01IO-1004-CJ01 |  | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-08-01IO-1004-CJ01 (HOLD) INSTRUMENTATION CABLE | EITS | PS5-08-13 - Safety Data Network (SII SP3 SAF) |  | Originated |  | Refer to BUILD-COW-0082 | 2026-04-22T09:53:13.457 | Thao-my, Alexandre | PS5 - Milestone C
PL-005479 | PS5-61-IJ-0001-CH10 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-22T10:24:15.897 | Mohamed, Amira | PS5 - Milestone D
PL-005480 | PS5-61-IJ-0001-CH11 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-22T10:26:59.297 | Mohamed, Amira | PS5 - Milestone D
PL-005481 | PS5-61-IJ-0001-CH12 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-10 - Power Generation Package D |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-22T10:33:23.213 | Mohamed, Amira | PS5 - Milestone D
PL-005484 | PS5-74-UB-5100 |  | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-74-01 - N2 Generation Skid |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-04-23T08:50:52.790 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-005485 | PS5-61-IJ-0001-CH13 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-13 - Power Generation Package E |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-23T10:26:55.773 | Mohamed, Amira | PS5 - Milestone D
PL-005487 | PS5-74-UB-5100 |  | A | M | 10.1: BROKEN SPOOL TO BE REPLACED | CPP AGI | PS5-74-01 - N2 Generation Skid |  | Originated |  | BROKEN SPOOL TO BE REPLACED | 2026-04-23T10:38:29.827 | THANGARATHINAM, ajikumar | PS5 - Milestone F
PL-005488 | PS5-61-IJ-0001-CH14 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-13 - Power Generation Package E |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-23T10:38:51.317 | Mohamed, Amira | PS5 - Milestone D
PL-005489 | PS5-61-IJ-0001-CH15 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-13 - Power Generation Package E |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-23T10:41:24.167 | Mohamed, Amira | PS5 - Milestone D
PL-005490 | PS5-61-IJ-0001-CH16 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-16 - Power Generation Package F |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-23T10:42:50.107 | Mohamed, Amira | PS5 - Milestone D
PL-005491 | PS5-61-IJ-0001-CH17 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-16 - Power Generation Package F |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-23T10:48:28.460 | Mohamed, Amira | PS5 - Milestone D
PL-005492 | PS5-61-IJ-0001-CH18 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-16 - Power Generation Package F |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-23T10:51:32.810 | Mohamed, Amira | PS5 - Milestone D
PL-005493 | PS5-61-IJ-0001-CH19 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-23T10:53:00.127 | Mohamed, Amira | PS5 - Milestone E
PL-005494 | PS5-61-IJ-0001-CH20 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-23T10:54:23.153 | Mohamed, Amira | PS5 - Milestone E
PL-005495 | PS5-61-IJ-0001-CH21 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-60-19 - Power Generation Package G |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-23T10:55:43.433 | Mohamed, Amira | PS5 - Milestone E
PL-005535 | PS5-25-DM-3100A-CH01 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T11:01:19.523 | Mohamed, Amira | PS5 - Milestone H
PL-005536 | PS5-25-DM-3100A-CH02 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T11:02:52.650 | Mohamed, Amira | PS5 - Milestone H
PL-005537 | PS5-25-DM-3100A-CH03 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T11:04:52.903 | Mohamed, Amira | PS5 - Milestone H
PL-005538 | PS5-25-DM-3100A-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T11:06:16.940 | Mohamed, Amira | PS5 - Milestone H
PL-005539 | PS5-25-DM-3100A-CH05 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T11:07:36.717 | Mohamed, Amira | PS5 - Milestone H
PL-005540 | PS5-25-DM-3100A-CH06 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T11:08:45.220 | Mohamed, Amira | PS5 - Milestone H
PL-005541 | PS5-25-DM-3100B-CH01 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T11:56:44.023 | Mohamed, Amira | PS5 - Milestone H
PL-005542 | PS5-25-DM-3100B-CH02 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T11:58:31.710 | Mohamed, Amira | PS5 - Milestone H
PL-005543 | PS5-25-DM-3100B-CH03 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-24T12:00:15.990 | Mohamed, Amira | PS5 - Milestone H
PL-005545 | PS5-28-PA-3600A |  | A | M | CPP USE 15W40 FOR BEARING LUBRICATION INSTEAD OF vg32 | EACOP | PS5-28-08 - Open Drain Sump and Pumps |  | Originated |  | THE OIL MUST BE FLUSHED BEFORE COMMISSIONING | 2026-04-24T13:43:05.000 | arun, jabesteen | PS5 - Milestone G
PL-005546 | PS5-28-PA-3600B |  | A | M | CPP USE 15W40 FOR BEARING LUBRICATION INSTEAD OF vg32 | EACOP | PS5-28-08 - Open Drain Sump and Pumps |  | Originated |  | THE OIL MUST BE FLUSHED BEFORE COMMISSIONING | 2026-04-24T13:45:20.000 | arun, jabesteen | PS5 - Milestone G
PL-005547 | PS5-28-PA-3500 |  | A | M | CPP USE 15W40 FOR BEARING LUBRICATION INSTEAD OF vg32 | EACOP | PS5-28-08 - Open Drain Sump and Pumps |  | Originated |  | THE OIL MUST BE FLUSHED BEFORE COMMISSIONING | 2026-04-24T13:47:09.000 | arun, jabesteen | PS5 - Milestone G
PL-005558 | PS5-25-DM-3100B-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-25T11:14:03.777 | Mohamed, Amira | PS5 - Milestone H
PL-005559 | PS5-25-DM-3100B-CH05 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing | 2026-04-25T11:15:46.913 | Mohamed, Amira | PS5 - Milestone H
PL-005560 | PS5-25-DM-3100B-CH06 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-25T11:17:03.910 | Mohamed, Amira | PS5 - Milestone H
PL-005561 | PS5-25-DM-3100C-CH01 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-25T11:18:20.940 | Mohamed, Amira | PS5 - Milestone H
PL-005562 | PS5-25-DM-3100C-CH02 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-25T11:19:42.323 | Mohamed, Amira | PS5 - Milestone H
PL-005563 | PS5-25-DM-3100C-CH03 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-25T11:21:30.170 | Mohamed, Amira | PS5 - Milestone H
PL-005564 | PS5-25-DM-3100C-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-25T11:23:38.707 | Mohamed, Amira | PS5 - Milestone H
PL-005565 | PS5-25-DM-3100C-CH05 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-25T11:26:43.300 | Mohamed, Amira | PS5 - Milestone H
PL-005566 | PS5-25-DM-3100C-CH06 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-04-25T11:28:02.603 | Mohamed, Amira | PS5 - Milestone H
PL-005571 | PS5-83-OB-0001_Installation |  | A | E | Leveling and cleaning of the floor and cable trays/ladders | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | Level and clean the floor surface beneath the cable trays to ensure a stable and even installation, with no contact between the supports and the ground. | 2026-04-27T07:03:10.967 | Mohamed, Amira | PS5 - Milestone A
PL-005572 | PS5-83-OB-0001_Installation |  | B | E | Corrosion need to be removed | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | Remove all corrosion from cable trays and ladders and treat the affected areas with appropriate anti-corrosion protection | 2026-04-27T07:06:51.970 | Mohamed, Amira | PS5 - Milestone A
PL-005574 | PS5-83-OB-0001_Installation |  | A | E | Hold down Clamp not Installed yet | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | Install the hold-down clamps once they become available on site, in accordance with the approved drawings. | 2026-04-27T07:10:03.210 | Mohamed, Amira | PS5 - Milestone A
PL-005575 | PS5-83-OB-0001_Installation |  | B | E | Earth jumper not installed completely | CPP AGI | PS5-83-01 - EITS Building |  | Originated |  | Complete the installation of all earth jumpers in accordance with the approved drawings and ensure proper earthing continuity | 2026-04-27T07:13:07.333 | Mohamed, Amira | PS5 - Milestone A
PL-005751 | PS5-09-LB-0001 |  | B | H | PS005-E&I-ALL-PL-2596 - HVAC UCP is unable to read PDT-0004/0005 value correctly dut to oversized scale 0-300psi. (current value: High: 62210 Pa, Low:-62210Pa, Low alarm: 50 Pa) | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | PLC/HMI program updated, refer to BUILD-COW-0451 for new PLC/HMI program upload | 2026-04-28T05:08:51.687 | Thao-my, Alexandre | PS5 - Milestone A
PL-005752 | PS5-09-LB-0001 |  | B | H | PS005-HVA-ALL-PL-2595 - Temporary banner for "Force run time" to be deleted | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | PLC/HMI program updated, refer to BUILD-COW-0451 for new PLC/HMI program upload | 2026-04-28T05:08:51.687 | Thao-my, Alexandre | PS5 - Milestone A
PL-005753 | PS5-09-LB-0001 |  | B | H | PS005-HVA-ALL-PL-2597 - The latested PLC program to be implemented and to be performed demonstration on site | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | PLC/HMI program updated, refer to BUILD-COW-0451 for new PLC/HMI program upload | 2026-04-28T05:08:51.687 | Thao-my, Alexandre | PS5 - Milestone A
PL-005754 | PS5-09-LB-0001 |  | B | H | PS005-HVA-ALL-PL-2599 - TSH alarm tag to be provided | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | PLC/HMI program updated, refer to BUILD-COW-0451 for new PLC/HMI program upload | 2026-04-28T05:08:51.687 | Thao-my, Alexandre | PS5 - Milestone A
PL-005755 | PS5-09-LB-0001 |  | B | H | PS005-HVA-ALL-PL-2600 - Extract Fan PDT-0003/0004 High / Low Set point to be validated and set accordingly | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | PLC/HMI program updated, refer to BUILD-COW-0451 for new PLC/HMI program upload | 2026-04-28T05:08:51.687 | Thao-my, Alexandre | PS5 - Milestone A
PL-005756 | PS5-09-LB-0001 |  | B | H | PS005-HVA-ALL-PL-2602 - HVAC UCP Heater function to be demonstrated (2.3 Pre iFAT Power up tests and checks) | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | Part of HVAC System SAT Procedure, the punch must be closed after the demonstration during the SAT | 2026-04-28T05:08:51.687 | Thao-my, Alexandre | PS5 - Milestone A
PL-005769 | PS5-28-VK-1200 |  | B | M | 4:The relief drum tag number is not correct to be rectified(Required PS5-28-VK-1200 but received as PS4-28-VK-1200) | EPS VENDOR | PS5-28-06 - Relief Drum and Pump |  | Originated |  |  | 2026-04-28T07:53:04.237 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-006055 | PS5-61-IK-0003-CG07 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-07T05:35:47.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-07T12:55:32.933 | Mohamed, Amira | PS5 - Milestone C
PL-006056 | PS5-25-ESDV-0021-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-01 - Export Pipeline Pig Receiver | 2026-06-14T08:34:46.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-07T13:41:30.610 | Mohamed, Amira | PS5 - Milestone H
PL-006058 | PS5-25-ESDV-0023-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-07 - Export Pipeline Pig Launcher | 2026-06-14T08:35:37.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-07T14:24:50.787 | Mohamed, Amira | PS5 - Milestone H
PL-006061 | PS5-25-FCV-0003A-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-02 - Crude Oil Export Pump A | 2026-06-14T08:36:11.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-08T08:18:17.823 | Mohamed, Amira | PS5 - Milestone H
PL-006062 | PS5-25-FCV-0003B-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-03 - Crude Oil Export Pump B | 2026-06-14T08:36:53.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-08T08:37:27.640 | Mohamed, Amira | PS5 - Milestone H
PL-006063 | PS5-25-FCV-0003C-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-04 - Crude Oil Export Pump C | 2026-06-14T08:39:04.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-08T09:20:11.503 | Mohamed, Amira | PS5 - Milestone H
PL-006064 | PS5-25-SDV-0054A-CL01 |  | A | E | Cable to be connected . | CPP AGI | PS5-25-02 - Crude Oil Export Pump A | 2026-06-14T08:40:15.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-08T09:28:01.973 | Mohamed, Amira | PS5 - Milestone H
PL-006065 | PS5-25-SDV-0054B-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-03 - Crude Oil Export Pump B | 2026-06-14T08:41:45.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-08T09:33:27.343 | Mohamed, Amira | PS5 - Milestone H
PL-006066 | PS5-25-SDV-0054C-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-04 - Crude Oil Export Pump C | 2026-06-08T10:13:09.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-08T10:58:40.997 | Mohamed, Amira | PS5 - Milestone H
PL-006067 | PS5-28-SDV-0053A-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-28-13 - Seal Oil Drain Drum & Pump A | 2026-06-14T08:42:32.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-08T11:02:25.860 | Mohamed, Amira | PS5 - Milestone H
PL-006068 | PS5-61-IK-0006-CL19 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:43:08.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-08T11:10:54.700 | Mohamed, Amira | PS5 - Milestone D
PL-006069 | PS5-61-IK-0006-CL20 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:45:54.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-08T11:22:54.237 | Mohamed, Amira | PS5 - Milestone D
PL-006070 | PS5-61-IK-0006-CL21 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:46:07.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-08T11:33:22.627 | Mohamed, Amira | PS5 - Milestone D
PL-006071 | PS5-61-IK-0006-CL22 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:46:21.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-08T11:40:03.963 | Mohamed, Amira | PS5 - Milestone D
PL-006072 | PS5-62-IE-0001-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-62-01 - Lighting Control Panel - PS5-62-IE-0001 | 2026-06-14T08:46:33.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-08T11:45:56.457 | Mohamed, Amira | PS5 - Milestone G
PL-006073 | PS5-71-HE-2400A-CL01 |  | A | E | Cable to be connected . | CPP AGI | PS5-71-01 - CFO Storage Tank Feed Heater | 2026-06-14T08:46:46.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-08T11:59:15.173 | Mohamed, Amira | PS5 - Milestone H
PL-006074 | PS5-71-HE-2400A-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-71-01 - CFO Storage Tank Feed Heater | 2026-06-14T08:46:57.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-08T12:04:47.010 | Mohamed, Amira | PS5 - Milestone H
PL-006090 | PS5-25-DM-3100A-CD01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-02 - Crude Oil Export Pump A | 2026-06-14T08:47:26.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-09T08:46:31.927 | Mohamed, Amira | PS5 - Milestone H
PL-006091 | PS5-25-DM-3100B-CD01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-03 - Crude Oil Export Pump B | 2026-06-14T08:47:43.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-09T10:15:46.883 | Mohamed, Amira | PS5 - Milestone H
PL-006092 | PS5-25-DM-3100C-CD01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-04 - Crude Oil Export Pump C | 2026-06-14T08:47:56.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-09T10:23:16.057 | Mohamed, Amira | PS5 - Milestone H
PL-006093 | PS5-62-IE-0001-CD01 |  | A | E | Cable to be connected | CPP AGI | PS5-62-01 - Lighting Control Panel - PS5-62-IE-0001 | 2026-06-14T08:48:09.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-09T10:34:03.573 | Mohamed, Amira | PS5 - Milestone G
PL-006094 | PS5-61-IDH-3100A-CD03 |  | A | E | Cable to be connected | CPP AGI | PS5-25-02 - Crude Oil Export Pump A | 2026-06-14T08:48:22.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-09T10:47:12.270 | Mohamed, Amira | PS5 - Milestone H
PL-006097 | PS5-61-IDH-3100B-CD03 |  | A | E | Cable to be connected | CPP AGI | PS5-25-03 - Crude Oil Export Pump B | 2026-06-14T08:48:35.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-09T10:55:04.610 | Mohamed, Amira | PS5 - Milestone H
PL-006100 | PS5-61-IDH-3100C-CD03 |  | A | E | Cable to be connected | CPP AGI | PS5-25-04 - Crude Oil Export Pump C | 2026-06-14T08:49:01.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-09T11:00:37.977 | Mohamed, Amira | PS5 - Milestone H
PL-006142 | PS5-71-TR-4200 |  | A | M | Platform structure middle member of cfo service tank is not matching with gratings and connected drawing. To be modified | EPS VENDOR | PS5-71-12 - CFO Service Tank |  | Originated |  | vendor to rectify | 2026-05-11T10:00:52.000 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-006193 | PS5-25-DM-3100B-CG01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-03 - Crude Oil Export Pump B | 2026-06-14T08:49:13.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-12T07:03:32.610 | Mohamed, Amira | PS5 - Milestone H
PL-006215 | PS5-61-IJ-0001 |  | B | E | PS005-E&I-COW-1126 - ALL CUBICLES: FINAL PROTECTION SETTINGS ARE NOT SET. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0011 | 2026-05-12T09:31:34.577 | Thao-my, Alexandre | PS5 - Milestone D
PL-006253 | PS5-61-IK-0001 |  | B | E | PS005-E&I-COW-1172 - INCOMERS: FINAL PROTECTION SETTINGS ARE NOT SET. | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0146 | 2026-05-12T09:31:34.577 | Thao-my, Alexandre | PS5 - Milestone A
PL-006281 | PS5-25-DM-3100B-CG02 |  | A | E | cable to be connected | CPP AGI | PS5-25-03 - Crude Oil Export Pump B | 2026-06-14T08:49:39.000 | Closed |  | cable must be connected glanded and terminated | 2026-05-14T06:49:11.467 | Mohamed, Amira | PS5 - Milestone H
PL-006282 | PS5-25-DM-3100C-CG01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-04 - Crude Oil Export Pump C | 2026-06-14T08:49:51.000 | Closed |  | Cable must be connected, and terminated. | 2026-05-14T07:11:01.577 | Mohamed, Amira | PS5 - Milestone H
PL-006283 | PS5-60-TCV-0001A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2026-05-14T07:55:31.963 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-006284 | PS5-60-TCV-0001A |  | C | P | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2026-05-14T07:56:39.673 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-006285 | PS5-60-TCV-0001B |  | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2026-05-14T07:59:41.020 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-006286 | PS5-60-TCV-0001B |  | C | P | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2026-05-14T08:00:18.030 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-006287 | PS5-60-TCV-0001D |  | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2026-05-14T08:02:18.983 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006288 | PS5-60-TCV-0001D |  | C | M | 10.1: TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2026-05-14T08:02:52.650 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006289 | PS5-60-TCV-0001F |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2026-05-14T08:04:51.790 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006290 | PS5-60-TCV-0001F |  | C | P | 10.1: TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2026-05-14T08:05:48.017 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006291 | PS5-60-TCV-0001G |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2026-05-14T08:07:50.040 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-006292 | PS5-60-TCV-0001G |  | C | P | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2026-05-14T08:08:22.723 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-006293 | PS5-60-TCV-0002A |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2026-05-14T08:11:22.737 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-006294 | PS5-60-TCV-0002A |  | C | P | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-70 - Engine A Cooling system |  | Originated |  |  | 2026-05-14T08:11:53.697 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-006295 | PS5-60-TCV-0002B |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2026-05-14T08:14:06.440 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-006296 | PS5-60-TCV-0002B |  | C | P | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-71 - Engine B Cooling system |  | Originated |  |  | 2026-05-14T08:14:45.553 | THANGARATHINAM, ajikumar | PS5 - Milestone B
PL-006297 | PS5-60-TCV-0002C |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  |  | 2026-05-14T08:16:27.783 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006298 | PS5-60-TCV-0002C |  | C | P | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  |  | 2026-05-14T08:17:07.970 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006299 | PS5-60-TCV-0002D |  | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2026-05-14T08:20:05.270 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006300 | PS5-60-TCV-0002D |  | C | P | 10.1:touch up painting to be done | CPP AGI | PS5-60-73 - Engine D Cooling system |  | Originated |  |  | 2026-05-14T08:20:36.130 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006301 | PS5-60-TCV-0002E |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  |  | 2026-05-14T08:22:22.650 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006302 | PS5-60-TCV-0002E |  | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  |  | 2026-05-14T08:22:59.843 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006303 | PS5-60-TCV-0002F |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2026-05-14T08:25:41.170 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006304 | PS5-60-TCV-0002F |  | C | P | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-75 - Engine F Cooling system |  | Originated |  |  | 2026-05-14T08:26:15.573 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006305 | PS5-60-TCV-0002G |  | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2026-05-14T08:28:13.333 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-006306 | PS5-60-TCV-0002G |  | C | P | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-76 - Engine G Cooling system |  | Originated |  |  | 2026-05-14T08:28:45.423 | THANGARATHINAM, ajikumar | PS5 - Milestone E
PL-006313 | PS5-25-DM-3100C-CG02 |  | A | E | Cable to be connected | CPP AGI | PS5-25-04 - Crude Oil Export Pump C | 2026-06-14T08:50:23.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-14T10:54:37.353 | Mohamed, Amira | PS5 - Milestone H
PL-006314 | PS5-79-BH-0002-CH01 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-05-14T11:13:36.770 | Mohamed, Amira | PS5 - Milestone G
PL-006315 | PS5-79-BH-0002-CH02 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-05-14T11:42:45.970 | Mohamed, Amira | PS5 - Milestone G
PL-006316 | PS5-79-BH-0002-CH03 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | CPP AGI | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  | Provide trefoil cleats to properly clamp and secure the cables on the cable tray, ensuring proper cable dressing. | 2026-05-14T11:59:34.407 | Mohamed, Amira | PS5 - Milestone G
PL-006317 | PS5-04-PMC-0001 |  | A | B | PS005-E&I-M4-PL-1286 - Terminal to be update on termination drawing by enginnering (mark up drawing) (PS5-04-PMC-0001-CS01) | EITS | PS5-04-04 - 33kV PCS System | 2026-05-19T15:37:29.000 | Closed |  | Document update | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A
PL-006318 | PS5-09-ACU-0007B-CD02 |  | A | E | PS005-E&I-M4-PL-2369 - Cable One Side Termination (COW) | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A
PL-006332 |  | PS5-06-GB-0001A | B | E | PS005-E&I-COW-1876 - Ensure that the battery connector is compatible with the cable’s rigidity and cross-sectional characteristics. Modify the battery interconnection cables so that the positive and negative terminals are routed from the left side of the rack. | EITS | PS5-06-01 - AC UPS - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0415 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A
PL-006333 |  | PS5-06-GB-0001B | B | E | PS005-E&I-COW-1877 - Ensure that the battery connector is compatible with the cable’s rigidity and cross-sectional characteristics. Modify the battery interconnection cables so that the positive and negative terminals are routed from the left side of the rack. | EITS | PS5-06-01 - AC UPS - EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0415 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A
PL-006391 | PS5-61-IK-0001 |  | B | E | PS005-E&I-COW-2175 - CUBICLE : CABLE SUPPORT MISSING AND CABLE ARRANGMENT TO BE REWORKED - PS4-61-IK-0001-C01 | EITS | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Refer to Job Card BUILD-COW-0131 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A
PL-006400 | PS5-04-PNC-0001 |  | A | I | PS005-E&I-COW-2279 - Additional Icotek frames to be added to Network cabinet for CAT6/FO cables | EITS | PS5-04-03 - 33kV ICSS System |  | Originated |  | Refer to Job Card BUILD-COW-0003 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A
PL-006429 | PS5-04-PMC-0003-CN01 |  | A | T | PS005-E&I-COW-2329 - New cable to be added | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0304 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A
PL-006430 | PS5-04-PMC-0003-CN02 |  | A | T | PS005-E&I-COW-2330 - New cable to be added | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0304 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A
PL-006431 | PS5-04-PSC-0001 |  | A | I | PS005-E&I-M3-PL-2591 - AGI NEW 4 SWITCHES TO BE INSTALLED AND WIRE | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Refer to Job Card BUILD-COW-0406 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A
PL-006449 | PS5-08-86IO-1002-CC01 |  | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-08-86IO-1002-CC01 (HOLD) INSTRUMENTATION CABLE | EITS | PS5-08-15 - Security Data Network (SII SP3 SEC) |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone C
PL-006450 | PS5-09-ACU-0007A-CP01 |  | A | E | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-09-ACU-0007A-CP01 POWER CABLE | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A
PL-006451 | PS5-09-ACU-0007B-CP01 |  | A | E | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-09-ACU-0007B-CP01 POWER CABLE | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  | Refer to Job Card BUILD-COW-0082 | 2026-05-15T06:47:21.613 | Thao-my, Alexandre | PS5 - Milestone A
PL-006488 | PS5-61-IK-0003-CL13 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:50:38.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-16T05:53:28.157 | Mohamed, Amira | PS5 - Milestone B
PL-006489 | PS5-61-IK-0003-CL14 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:50:52.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-16T07:48:45.267 | Mohamed, Amira | PS5 - Milestone B
PL-006490 | PS5-61-IK-0003-CL15 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:51:32.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T08:02:09.513 | Mohamed, Amira | PS5 - Milestone B
PL-006491 | PS5-61-IK-0003-CL16 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:51:44.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T08:34:07.590 | Mohamed, Amira | PS5 - Milestone B
PL-006492 | PS5-61-IK-0003-CL17 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:51:58.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T10:27:26.020 | Mohamed, Amira | PS5 - Milestone B
PL-006493 | PS5-61-IK-0003-CL36 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:52:11.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T10:52:36.223 | Mohamed, Amira | PS5 - Milestone B
PL-006494 | PS5-61-IK-0003-CL18 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:52:27.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T10:54:10.883 | Mohamed, Amira | PS5 - Milestone B
PL-006495 | PS5-61-IK-0003-CL35 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:52:43.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:00:20.333 | Mohamed, Amira | PS5 - Milestone B
PL-006496 | PS5-61-IK-0003-CL34 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:52:57.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:08:23.987 | Mohamed, Amira | PS5 - Milestone B
PL-006497 | PS5-61-IK-0003-CL19 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:53:10.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:08:38.967 | Mohamed, Amira | PS5 - Milestone B
PL-006498 | PS5-61-IK-0003-CL20 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:53:23.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:14:26.040 | Mohamed, Amira | PS5 - Milestone B
PL-006499 | PS5-61-IK-0003-CL33 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:53:36.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:14:34.963 | Mohamed, Amira | PS5 - Milestone B
PL-006500 | PS5-61-IK-0003-CL32 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:53:48.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:21:05.020 | Mohamed, Amira | PS5 - Milestone B
PL-006501 | PS5-61-IK-0003-CL21 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:54:57.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:22:01.893 | Mohamed, Amira | PS5 - Milestone B
PL-006502 | PS5-61-IK-0003-CL31 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:55:12.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:28:53.467 | Mohamed, Amira | PS5 - Milestone B
PL-006503 | PS5-61-IK-0003-CL22 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:55:26.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:32:41.743 | Mohamed, Amira | PS5 - Milestone B
PL-006504 | PS5-61-IK-0003-CL30 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:55:45.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:40:18.477 | Mohamed, Amira | PS5 - Milestone B
PL-006505 | PS5-61-IK-0003-CL23 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:56:00.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:40:55.070 | Mohamed, Amira | PS5 - Milestone B
PL-006506 | PS5-61-IK-0006-CL10 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:56:16.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:46:05.713 | Mohamed, Amira | PS5 - Milestone D
PL-006507 | PS5-61-IK-0003-CL24 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:56:34.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:49:55.427 | Mohamed, Amira | PS5 - Milestone B
PL-006508 | PS5-61-IK-0006-CL11 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:57:01.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T11:56:25.787 | Mohamed, Amira | PS5 - Milestone D
PL-006509 | PS5-61-IK-0006-CL12 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:57:16.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T12:04:44.560 | Mohamed, Amira | PS5 - Milestone D
PL-006510 | PS5-61-IK-0006-CL13 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:57:29.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T12:06:29.503 | Mohamed, Amira | PS5 - Milestone D
PL-006512 | PS5-61-IK-0006-CL16 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:57:57.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T12:11:25.530 | Mohamed, Amira | PS5 - Milestone D
PL-006513 | PS5-61-IK-0006-CL17 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:58:09.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T12:29:50.740 | Mohamed, Amira | PS5 - Milestone D
PL-006514 | PS5-61-IK-0006-CL18 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:58:21.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T12:39:34.300 | Mohamed, Amira | PS5 - Milestone D
PL-006515 | PS5-61-IK-0006-CL14 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:58:34.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-16T13:00:24.507 | Mohamed, Amira | PS5 - Milestone D
PL-006516 | PS5-61-IK-0006-CL15 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:58:45.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-16T13:07:46.140 | Mohamed, Amira | PS5 - Milestone D
PL-006559 | PS5-61-IV-0002A |  | B | M | 4:Quality of welding in the transformer is not upto the standard. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T12:47:14.887 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006560 | PS5-61-IV-0002A |  | B | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T12:48:54.633 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006561 | PS5-61-IV-0002A |  | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T12:50:20.720 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006562 | PS5-61-IV-0002A |  | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T12:51:56.177 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006563 | PS5-61-IV-0002A |  | A | E | 4.4:Flexible conduit routing over the enclosure is improperly installed or broken | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T12:54:36.423 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006564 | PS5-61-IV-0002A |  | B | E | 4.5:Earthing cable not connected, poor cable management, improper stripping, and improper glanding | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T12:56:26.260 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006565 | PS5-61-IV-0002A |  | B | E | 4.6:Internal wiring and cable entry inside the enclosure are poorly installed and not properly managed, unused openings are covered by rubber plugs | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T12:57:46.530 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006566 | PS5-61-IV-0002A |  | B | E | 4.7:The opening has been temporarily sealed using plastic tape. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T12:59:12.617 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006567 | PS5-61-IV-0002A |  | A | E | 4.8:Flexible conduit not properly terminated into the cable gland. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T13:00:18.810 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006568 | PS5-61-IV-0002A |  | A | E | 4.9:All cable entries are not properly tightened and cables are not properly sealed in cable glands. Applicable for all transformers. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T13:02:15.380 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006569 | PS5-61-IV-0002A |  | A | E | 4.10:64. No heat-shrink sleeves are installed on the cable inside the main panel. Applicable for all transformers. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T13:03:03.237 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006570 | PS5-61-IV-0002A |  | A | E | 4.11:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). Applicable for all transformers. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T13:04:24.403 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006571 | PS5-61-IV-0002A |  | B | E | 4.12: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. Applicable for all transformers. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T13:05:25.943 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006572 | PS5-61-IV-0002A |  | B | E | 4.13:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc) | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T13:06:57.170 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006573 | PS5-61-IV-0002A |  | A | E | 4.14:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T13:07:45.823 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006574 | PS5-61-IV-0002A |  | B | E | 4.15:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-18T13:09:47.487 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006576 | PS5-61-IV-0002B |  | B | M | 4:Quality of welding in the transformer is not upto the standard. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:21:41.363 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006577 | PS5-61-IV-0002B |  | C | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:24:10.287 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006578 | PS5-61-IV-0002B |  | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:29:51.177 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006579 | PS5-61-IV-0002B |  | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:31:24.010 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006580 | PS5-61-IV-0002B |  | B | E | 4.4:Internal wiring and cable entry inside the enclosure are poorly installed and not properly managed, unused openings are covered by rubber plugs | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:34:41.410 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006581 | PS5-61-IV-0002B |  | B | E | 4.5:The opening has been temporarily sealed using plastic tape. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:35:49.003 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006582 | PS5-61-IV-0002B |  | A | E | 4.6:Cable entry is improperly installed. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:37:58.283 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006583 | PS5-61-IV-0002B |  | A | E | 4.7:All cable entries are not properly tightened and cables are not properly sealed in cable glands.. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:39:35.727 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006584 | PS5-61-IV-0002B |  | A | E | 4.8:64. No heat-shrink sleeves are installed on the cable inside the main panel. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:51:02.470 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006585 | PS5-61-IV-0002B |  | B | E | 4.9:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:51:50.320 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006586 | PS5-61-IV-0002B |  | B | E | 4.10: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. . | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:53:31.830 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006587 | PS5-61-IV-0002B |  | B | E | 4.11:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc).. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:54:21.477 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006588 | PS5-61-IV-0002B |  | A | E | 4.12:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:55:46.333 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006590 | PS5-61-IV-0002B |  | A | E | 4.13:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T05:56:34.757 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006591 | PS5-61-IV-0007A |  | B | M | 4:Quality of welding in the transformer is not upto the standard. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:25:57.213 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006592 | PS5-61-IV-0007A |  | C | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:28:11.897 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006593 | PS5-61-IV-0007A |  | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:29:09.663 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006594 | PS5-61-IV-0007A |  | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:30:44.923 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006595 | PS5-61-IV-0007A |  | B | E | 4.4:Improper termination of earthing conductor | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:32:11.487 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006596 | PS5-61-IV-0007A |  | A | E | 4.5:Earthing cable not connected, poor cable management, improper stripping, and improper glanding. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:42:15.790 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006597 | PS5-61-IV-0007A |  | A | E | 4.6:Improper installation of copper bonding/earthing strap | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:43:40.663 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006598 | PS5-61-IV-0007A |  | B | E | 4.7:Unused gland plate sealed with rubber instead of stopping plug. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:44:36.830 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006599 | PS5-61-IV-0007A |  | B | E | 4.8:The opening has been temporarily sealed using plastic tape | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:46:47.453 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006600 | PS5-61-IV-0007A |  | A | E | 4.9:Cable entry at the bottom of the enclosure is improperly installed. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:47:46.997 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006601 | PS5-61-IV-0007A |  | A | M | 4.10:Oil Leakage found at the oil level gauge weld area. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:49:14.923 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006602 | PS5-61-IV-0007A |  | A | E | 4.11:All cable entries are not properly tightened and cables are not properly sealed in cable glands.. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:51:20.993 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006603 | PS5-61-IV-0007A |  | A | M | 4.12:64. No heat-shrink sleeves are installed on the cable inside the main panel. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:52:09.650 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006604 | PS5-61-IV-0007A |  | B | M | 4.13:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:53:36.467 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006605 | PS5-61-IV-0007A |  | B | E | 4.14: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. . | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:54:33.773 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006606 | PS5-61-IV-0007A |  | B | E | 4.15:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc).. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:56:18.253 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006607 | PS5-61-IV-0007A |  | A | E | 4.16:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:57:00.673 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006608 | PS5-61-IV-0007A |  | A | E | 4.17:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T06:58:28.123 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006609 | PS5-61-IV-0007B |  | B | M | 4:Quality of welding in the transformer is not upto the standard. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:15:28.513 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006610 | PS5-61-IV-0007B |  | C | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:17:04.393 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006611 | PS5-61-IV-0007B |  | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:18:30.613 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006612 | PS5-61-IV-0007B |  | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:20:06.177 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006613 | PS5-61-IV-0007B |  | A | M | 4.4:Temperature sensor not sealed properly | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:21:00.077 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006614 | PS5-61-IV-0007B |  | B | E | 4.5:loose bolt for 1U & 1W. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:26:24.223 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006615 | PS5-61-IV-0007B |  | A | M | 4.6:Internal wiring and cable entry inside the enclosure are poorly installed and not properly managed, unused openings are covered by rubber plugs | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:27:32.567 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006616 | PS5-61-IV-0007B |  | B | E | 4.7:Unused gland plate sealed with rubber instead of stopping plug | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:29:33.423 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006617 | PS5-61-IV-0007B |  | A | E | 4.8:Cable entry is improperly installed. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:30:19.970 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006618 | PS5-61-IV-0007B |  | A | M | 4.9:Oil Leakage found at the weld area. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:32:05.480 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006619 | PS5-61-IV-0007B |  | A | E | 4.10:All cable entries are not properly tightened and cables are not properly sealed in cable glands.. | CPP AGI | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:33:28.617 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006620 | PS5-61-IV-0007B |  | A | E | 4.11:64. No heat-shrink sleeves are installed on the cable inside the main panel. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:37:40.113 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006621 | PS5-61-IV-0007B |  | B | E | 4.12:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:38:26.853 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006622 | PS5-61-IV-0007B |  | B | E | 4.13: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. . | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:39:43.767 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006623 | PS5-61-IV-0007B |  | B | M | 4.14:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc).. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:40:23.323 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006624 | PS5-61-IV-0007B |  | A | E | 4.15:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:41:30.810 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006625 | PS5-61-IV-0007B |  | A | E | 4.16:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | EPS VENDOR | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  |  | 2026-05-19T07:42:14.747 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-006626 | PS5-61-IV-0001A |  | B | M | 4:Quality of welding in the transformer is not upto the standard. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T07:50:27.033 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006627 | PS5-61-IV-0001A |  | C | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T07:52:20.300 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006628 | PS5-61-IV-0001A |  | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T07:53:11.440 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006629 | PS5-61-IV-0001A |  | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T07:54:46.970 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006630 | PS5-61-IV-0001A |  | B | M | 4.4:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T07:55:43.780 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006631 | PS5-61-IV-0001A |  | A | E | 4.5:Cable entry is improperly installed. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T07:59:48.210 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006632 | PS5-61-IV-0001A |  | B | E | 4.6:Unused gland plate sealed with rubber instead of stopping plug. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:02:47.510 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006633 | PS5-61-IV-0001A |  | B | E | 4.7:loose bolt for 1W. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:03:37.340 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006634 | PS5-61-IV-0001A |  | B | E | 4.8:Poor cable management, improper stripping and glanding. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:07:01.020 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006635 | PS5-61-IV-0001A |  | A | E | 4.9:Cable glanding not properly tightened and sealed | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:08:53.287 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006636 | PS5-61-IV-0001A |  | B | E | 4.10:Cable entry temporarily sealed using plastic tape | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:11:18.603 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006637 | PS5-61-IV-0001A |  | A | E | 4.11:All cable entries are not properly tightened and cables are not properly sealed in cable glands.. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:12:37.737 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006638 | PS5-61-IV-0001A |  | A | M | 4.12:64. No heat-shrink sleeves are installed on the cable inside the main panel. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:24:49.750 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006639 | PS5-61-IV-0001A |  | B | E | 4.13:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:25:27.220 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006640 | PS5-61-IV-0001A |  | B | E | 4.14: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. . | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:26:54.213 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006641 | PS5-61-IV-0001A |  | B | E | 4.15:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc).. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:27:49.297 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006642 | PS5-61-IV-0001A |  | A | E | 4.16:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:29:12.513 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006643 | PS5-61-IV-0001A |  | A | E | 4.17:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T08:30:08.660 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006653 | PS5-61-IV-0001B |  | B | M | 4:Quality of welding in the transformer is not upto the standard. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:08:14.693 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006655 | PS5-61-IV-0001B |  | C | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:09:53.167 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006656 | PS5-61-IV-0001B |  | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:10:47.477 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006657 | PS5-61-IV-0001B |  | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:12:50.333 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006658 | PS5-61-IV-0001B |  | A | M | 4.4:Oil Leakage found at the oil level gauge weld area. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:13:56.710 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006659 | PS5-61-IV-0001B |  | A | M | 4.5:Oil Leakage found at the weld area. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:16:18.023 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006660 | PS5-61-IV-0001B |  | A | M | 4.6:Oil Leakage found. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:17:06.253 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006661 | PS5-61-IV-0001B |  | A | M | 4.7:Oil Leakage found at the weld area. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:18:18.720 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006662 | PS5-61-IV-0001B |  | A | M | 4.8:Oil Leakage found at the weld area. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:19:15.140 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006663 | PS5-61-IV-0001B |  | A | E | 4.9:internal wiring and cable entry inside the enclosure are poorly installed and not properly managed; unused openings are covered with rubber plugs | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:20:45.867 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006664 | PS5-61-IV-0001B |  | B | E | 4.10:poor cable management, improper stripping, and improper glanding | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:21:47.130 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006665 | PS5-61-IV-0001B |  | A | E | 4.11:flexible conduit routing over the enclosure is improperly installed. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:24:00.727 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006666 | PS5-61-IV-0001B |  | B | E | 4.12:unused gland plate is sealed with rubber instead of a stopping plug. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:24:51.633 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006667 | PS5-61-IV-0001B |  | A | E | 4.13:cable entry at the bottom of the enclosure is improperly installed. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:26:12.610 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006668 | PS5-61-IV-0001B |  | A | E | 4.14:temperature sensor is not properly sealed. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:27:14.903 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006669 | PS5-61-IV-0001B |  | A | E | 4.15:All cable entries are not properly tightened and cables are not properly sealed in cable glands.. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:31:06.080 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006670 | PS5-61-IV-0001B |  | A | E | 4.16:64. No heat-shrink sleeves are installed on the cable inside the main panel. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:31:53.783 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006671 | PS5-61-IV-0001B |  | B | E | 4.17:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:33:13.060 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006672 | PS5-61-IV-0001B |  | B | E | 4.18: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. . | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:33:57.573 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006673 | PS5-61-IV-0001B |  | B | E | 4.19:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc).. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:35:08.877 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006674 | PS5-61-IV-0001B |  | A | E | 4.20:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:36:31.693 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006675 | PS5-61-IV-0001B |  | A | E | 4.21:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | EPS VENDOR | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  |  | 2026-05-19T12:37:19.473 | THANGARATHINAM, ajikumar | PS5 - Milestone A
PL-006681 | PS5-61-IK-0003-CL41 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:59:18.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-20T11:59:12.357 | Gawad, Mohamed | PS5 - Milestone B
PL-006683 | PS5-61-IK-0003-CL42 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T08:59:32.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-20T12:17:17.127 | Gawad, Mohamed | PS5 - Milestone B
PL-006685 | PS5-61-IK-0006-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T08:59:48.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-20T12:41:37.250 | Gawad, Mohamed | PS5 - Milestone D
PL-006691 | PS5-03-SFMC-0012-CD01 (Reconnection) |  | B | E | core 5,6,7,8 as spare to be terminated to PE at PS5-03-SFMC-0012 side | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-20T13:51:49.000 | Silaban, Junardi | PS5 - Milestone A
PL-006692 | PS5-09-ACU-0007A-CP01 |  | B | E | To be installed cable tray for cable laying at PS5-09-ACU-0007A to protecting that cable from damage | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  |  | 2026-05-20T14:04:11.000 | Silaban, Junardi | PS5 - Milestone A
PL-006693 | PS5-03-SFMC-0005-CC01 |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC01/TBA08/3/PR02/WH, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-20T14:10:42.000 | Silaban, Junardi | PS5 - Milestone A
PL-006694 | PS5-61-IK-0006-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:00:21.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-20T17:19:41.150 | Gawad, Mohamed | PS5 - Milestone D
PL-006695 | PS5-61-IK-0006-CL03 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:00:35.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T04:37:17.950 | Gawad, Mohamed | PS5 - Milestone D
PL-006697 | PS5-61-IK-0006-CL05 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:00:48.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T05:02:49.410 | Gawad, Mohamed | PS5 - Milestone D
PL-006698 | PS5-03-SFMC-0005-CC01 |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC02/TBA09/3/PR02/WH, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-21T05:18:05.000 | Silaban, Junardi | PS5 - Milestone A
PL-006699 | PS5-61-IK-0006-CL06 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:01:01.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T05:22:43.313 | Gawad, Mohamed | PS5 - Milestone D
PL-006700 | PS5-03-SFMC-0005-CC03 (Reconnection) |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC03/TBA10/4/PR02/BK, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-21T05:25:46.000 | Silaban, Junardi | PS5 - Milestone A
PL-006701 | PS5-61-IK-0006-CL07 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:01:23.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T05:30:33.757 | Gawad, Mohamed | PS5 - Milestone D
PL-006702 | PS5-03-SFMC-0005-CC05 (Reconnection) |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC05/TBA12/1/PR01/WH ; /2/PR01/WH and /3/PR02/BK, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-21T05:33:57.000 | Silaban, Junardi | PS5 - Milestone A
PL-006703 | PS5-03-SFMC-0005-CC06 (Reconnection) |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC06/TBA13/1/PR01/WH ; to be replaced wire marker PS5-03-SFMC-0005-CC06/TBA13/2/PR01/BK, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-21T05:37:46.000 | Silaban, Junardi | PS5 - Milestone A
PL-006704 | PS5-03-SFMC-0005-CC07 (Reconnection) |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC07/TBA14/1/PR01/WH, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-21T05:40:03.000 | Silaban, Junardi | PS5 - Milestone A
PL-006705 | PS5-61-IK-0006-CL08 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:01:34.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T05:40:08.650 | Gawad, Mohamed | PS5 - Milestone D
PL-006706 | PS5-03-SFMC-0005-CC08 (Reconnection) |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC08/TBA15/1/PR01/WH, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-21T05:42:54.000 | Silaban, Junardi | PS5 - Milestone A
PL-006707 | PS5-03-SFMC-0005-CC09 (Reconnection) |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC09/TBA16/1/PR01/WH, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-21T05:45:17.000 | Silaban, Junardi | PS5 - Milestone A
PL-006708 | PS5-03-SFMC-0005-CC18 (Reconnection) |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC18/TBA01/1/PR01/WH and /3/PR02/WH, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-21T05:49:07.000 | Silaban, Junardi | PS5 - Milestone A
PL-006709 | PS5-03-SFMC-0005-CC19 (Reconnection) |  | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBA03 to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-21T05:53:39.000 | Silaban, Junardi | PS5 - Milestone A
PL-006710 | PS5-61-IK-0006-CL09 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:01:51.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T05:54:45.987 | Gawad, Mohamed | PS5 - Milestone D
PL-006711 | PS5-03-SFMC-0005-CC20 (Reconnection) |  | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC20/TBA06/1/PR01/WH, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-21T05:57:20.000 | Silaban, Junardi | PS5 - Milestone A
PL-006741 | PS5-61-IK-0003-CL07 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:02:21.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T07:48:39.903 | Gawad, Mohamed | PS5 - Milestone B
PL-006748 | PS5-61-IK-0003-CL12 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:02:34.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T07:56:35.460 | Gawad, Mohamed | PS5 - Milestone B
PL-006754 | PS5-61-IK-0003-CL08 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:03:05.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T08:04:44.260 | Gawad, Mohamed | PS5 - Milestone B
PL-006755 | PS5-61-IK-0003-CL11 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:03:22.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T08:04:54.373 | Gawad, Mohamed | PS5 - Milestone B
PL-006759 | PS5-61-IK-0003-CL09 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:03:34.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T08:13:57.850 | Gawad, Mohamed | PS5 - Milestone B
PL-006760 | PS5-61-IK-0003-CL10 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:04:45.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T08:14:53.353 | Gawad, Mohamed | PS5 - Milestone B
PL-006761 | PS5-03-SFMC-0005-CC23 (Reconnection) |  | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBA02 to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Yes | 2026-05-21T08:22:40.000 | Silaban, Junardi | PS5 - Milestone A
PL-006762 | PS5-61-IK-0003-CL37 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:04:58.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T08:26:39.973 | Gawad, Mohamed | PS5 - Milestone B
PL-006764 | PS5-61-IK-0003-CL38 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:05:11.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T08:34:45.850 | Gawad, Mohamed | PS5 - Milestone B
PL-006765 | PS5-61-IK-0003-CL39 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:05:24.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T08:49:48.203 | Gawad, Mohamed | PS5 - Milestone B
PL-006766 | PS5-03-SFMC-0005-CC24 (Reconnection) |  | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBA05 to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Yes | 2026-05-21T09:10:10.000 | Silaban, Junardi | PS5 - Milestone A
PL-006767 | PS5-03-SFMC-0005-CC27 (Reconnection) |  | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBD11 to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Yes | 2026-05-21T09:16:00.000 | Silaban, Junardi | PS5 - Milestone A
PL-006772 | PS5-03-SFMC-0005-CC32 (Reconnection) |  | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBD10 to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-21T10:11:02.000 | Silaban, Junardi | PS5 - Milestone A
PL-006776 | PS5-03-SFMC-0005-CC34 (Reconnection) |  | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBD06 to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-21T10:13:34.000 | Silaban, Junardi | PS5 - Milestone A
PL-006777 | PS5-61-IK-0003-CL40 |  | A | E | Cable to be connected | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 2026-06-14T09:05:56.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T10:13:45.370 | Gawad, Mohamed | PS5 - Milestone B
PL-006780 | PS5-03-SFMC-0005-CC41 (Reconnection) |  | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBA07 to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-21T10:16:08.000 | Silaban, Junardi | PS5 - Milestone A
PL-006781 | PS5-03-SFMC-0006-CC01 (Reconnection) |  | A |  | Ferulle for PS5-03-SFMC-0006-CC01/TBD09/1/PR01/WH to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-21T10:17:58.000 | Silaban, Junardi | PS5 - Milestone A
PL-006785 | PS5-03-SFMC-0006-CC02 (Reconnection) |  | A | I | Ferulle for PS5-03-SFMC-0006-CC02/TBD10/3/PR02/WH to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  |  | 2026-05-21T10:20:03.000 | Silaban, Junardi | PS5 - Milestone A
PL-006787 | PS5-61-IK-0003-CL43 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:06:08.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T10:21:14.757 | Gawad, Mohamed | PS5 - Milestone C
PL-006790 | PS5-04-PMC-0008-CC07 (Reconnection) |  | A | I | All ferulles on PS5-04-PMC-0008-CC07/TBD15 to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  |  | 2026-05-21T10:22:22.000 | Silaban, Junardi | PS5 - Milestone A
PL-006791 | PS5-04-PMC-0008-CC26 (Reconnection) |  | A | I | Core marker for PS5-04-PMC-0008-CC26/TBA12/1/PR01/WH to be installed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  |  | 2026-05-21T10:24:54.000 | Silaban, Junardi | PS5 - Milestone A
PL-006792 | PS5-04-PMC-0008-CC30 (Reconnection) |  | A | I | Core marker for PS5-04-PMC-0008-CC30/TBD23/4/PR01/BK to be installed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  |  | 2026-05-21T10:28:57.000 | Silaban, Junardi | PS5 - Milestone A
PL-006793 | PS5-61-IK-0003-CL45 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:06:46.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T10:29:14.950 | Gawad, Mohamed | PS5 - Milestone C
PL-006794 | PS5-04-PMC-0008-CC39 (Reconnection) |  | B | I | Terminal Blok Name TBA16/04-PMC-0008-CC39 to be installed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  |  | 2026-05-21T10:32:31.000 | Silaban, Junardi | PS5 - Milestone A
PL-006795 | PS5-04-PMC-0008-CC40 (Reconnection) |  | A | I | All ferrules on PS5-04-PMC-0008-CC40/TBD25 to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  |  | 2026-05-21T10:36:07.000 | Silaban, Junardi | PS5 - Milestone A
PL-006796 | PS5-04-PMC-0008-CC41 (Reconnection) |  | A | I | Ferulle for PS5-04-PMC-0008-CC41/TBD08/1/PR01/WH to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  |  | 2026-05-21T10:42:34.000 | Silaban, Junardi | PS5 - Milestone A
PL-006797 | PS5-61-IK-0003-CL46 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:06:58.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T10:49:59.877 | Gawad, Mohamed | PS5 - Milestone C
PL-006798 | PS5-61-IK-0003-CL47 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:07:16.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T11:00:51.480 | Gawad, Mohamed | PS5 - Milestone C
PL-006799 | PS5-61-IK-0003-CL48 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:07:29.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T11:08:47.883 | Gawad, Mohamed | PS5 - Milestone C
PL-006801 | PS5-61-IK-0003-CL50 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:08:07.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T11:30:20.457 | Gawad, Mohamed | PS5 - Milestone C
PL-006809 | PS5-61-IK-0003-CL51 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:08:21.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T12:44:23.840 | Gawad, Mohamed | PS5 - Milestone C
PL-006810 | PS5-61-IK-0001-CL01 |  | B | E | Cable dressing not completed at both ends | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Completed |  | Complete cable dressing at both ends. Ensure proper cable ties, cleats, and bending radius are maintained as per project specification | 2026-05-21T12:49:49.783 | Gawad, Mohamed | PS5 - Milestone A
PL-006811 | PS5-61-IK-0003-CL52 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:08:52.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T12:55:41.280 | Gawad, Mohamed | PS5 - Milestone C
PL-006812 | PS5-61-IK-0001-CL01 |  | B | E | Trench backfilled at Transformer side without installation of Red Protection Tiles and Warning Tape over LV Power Cable | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Completed |  | Excavate trench at Transformer side, install Red Protection Tiles and Warning Tape at correct depth above cable as per project civil/electrical specification, then re-backfill and compact properly. | 2026-05-21T13:15:09.640 | Gawad, Mohamed | PS5 - Milestone A
PL-006813 | PS5-61-IK-0003-CL53 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:09:06.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-21T13:17:14.973 | Gawad, Mohamed | PS5 - Milestone C
PL-006832 | PS5-04-PMC-0008-CC12 (Reconnection) |  | A | I | All ferulles on PS5-04-PMC-0008-CC12/TBD18 to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  |  | 2026-05-21T14:20:28.000 | Silaban, Junardi | PS5 - Milestone A
PL-006834 | PS5-04-PMC-0008-CC25 (Reconnection) |  | A | I | All ferulles on PS5-04-PMC-0008-CC25/TBA11 to be changed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  |  | 2026-05-21T14:23:03.000 | Silaban, Junardi | PS5 - Milestone A
PL-006861 | PS5-04-PMC-0008-CC24 (Reconnection) |  | B | I | Ferulle for PS5-04-PMC-0008-CC24/TBA07/4/PR02/BK to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T04:38:58.000 | Silaban, Junardi | PS5 - Milestone A
PL-006862 | PS5-61-IK-0003-CL54 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:09:37.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T04:39:14.563 | Gawad, Mohamed | PS5 - Milestone C
PL-006863 | PS5-04-PMC-0008-CC20 (Reconnection) |  | A | I | Ferulle for PS5-04-PMC-0008-CC20/TBD07/1/PR01/WH to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T04:41:22.000 | Silaban, Junardi | PS5 - Milestone A
PL-006864 | PS5-04-PMC-0008-CC28 (Reconnection) |  | A | I | Ferulle for PS5-04-PMC-0008-CC28/TBD21/1/PR01/WH and PS5-04-PMC-0008-CC28/TBD21/2/PR01/BK to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T04:44:00.000 | Silaban, Junardi | PS5 - Milestone A
PL-006865 | PS5-04-PMC-0008-CC31 (Reconnection) |  | A | I | Ferulle for PS5-04-PMC-0008-CC31/TBD24/1/PR01/WH and PS5-04-PMC-0008-CC31/TBD24/2/PR01/BK to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T04:47:22.000 | Silaban, Junardi | PS5 - Milestone A
PL-006866 | PS5-04-PMC-0008-CC17 (Reconnection) |  | A | I | Ferulle for PS5-04-PMC-0008-CC17/TBA09/1/PR01/WH and PS5-04-PMC-0008-CC17/TBA09/2/PR01/BK to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T04:49:32.000 | Silaban, Junardi | PS5 - Milestone A
PL-006867 | PS5-04-PMC-0008-CC13 (Reconnection) |  | B | I | Ferulle for PS5-04-PMC-0008-CC13/TBD19/4/PR02/BK to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T04:52:36.000 | Silaban, Junardi | PS5 - Milestone A
PL-006868 | PS5-04-PMC-0008-CC11 (Reconnection) |  | B | I | Ferulle for PS5-04-PMC-0008-CC11/TBD17/3/PR02/WH and PS5-04-PMC-0008-CC11/TBD17/4/PR02/BK to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T04:55:16.000 | Silaban, Junardi | PS5 - Milestone A
PL-006869 | PS5-04-PMC-0008-CC10 (Reconnection) |  | A | I | Ferulle for PS5-04-PMC-0008-CC10/TBD16/1/PR01/WH to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T04:57:15.000 | Silaban, Junardi | PS5 - Milestone A
PL-006870 | PS5-04-PMC-0008-CC09 (Reconnection) |  | A | I | Ferulle for PS5-04-PMC-0008-CC09/TBA02/1/PR01/WH to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T04:59:20.000 | Silaban, Junardi | PS5 - Milestone A
PL-006871 | PS5-04-PMC-0008-CC47 (Reconnection) |  | A | I | Ferulle for PS5-04-PMC-0008-CC47/TBA18/1/PR01/WH and PS5-04-PMC-0008-CC47/TBA18/4/PR02/BK to be changed, wire exposed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T05:03:05.000 | Silaban, Junardi | PS5 - Milestone A
PL-006872 | PS5-09-PDT-0004-CJ01 (Reconnection) |  | B | I | Missing terminal block name XAI inside Panel PS5-09-LB-0001, to be provided | EITS | PS5-09-05 - HVAC for EITS Building |  | Originated |  |  | 2026-05-22T05:06:13.000 | Silaban, Junardi | PS5 - Milestone A
PL-006873 | PS5-04-PMC-0002-CS03 (Reconnection) |  | A | E | Wrong core marker at Panel PS5-04-PMC-0002 side, to be replaced. PS5-04-PMC-0002-CS03,,, instead PS5-04-PMC-002-CS03,,, | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T05:19:07.000 | Silaban, Junardi | PS5 - Milestone A
PL-006874 | PS5-04-PMC-0008-CC48 (Reconnection) |  | B | I | to be changed terminal number on the drawing No. TZ-MID-68-SSF1-160014 page 288 of 952 due to actual number inside of panel is 1,2,3,4 | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T05:28:21.000 | Silaban, Junardi | PS5 - Milestone A
PL-006875 | PS5-61-IJ-0011-CD01 (Reconnection) |  | B | E | Terminal Blok Name XDI13 at Panel PS5-61-IE-0002 is not available, to be provided | EITS | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) |  | Originated |  | Yes | 2026-05-22T05:38:33.000 | Silaban, Junardi | PS5 - Milestone G
PL-006876 | PS5-04-PMC-0008-CC35 (Reconnection) |  | A | I | to provided core marker for PS5-04-PMC-0008-CC35/TBA10/7/PR04/WH at PS5-04-PMC-0008 side | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T05:42:12.000 | Silaban, Junardi | PS5 - Milestone A
PL-006877 | PS5-03-SFMC-0005-CC33 (Reconnection) |  | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBD08 to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Yes | 2026-05-22T05:45:03.000 | Silaban, Junardi | PS5 - Milestone A
PL-006878 | PS5-04-PMC-0008-CC57 (Reconnection) |  | B | I | Ferulle for PS5-04-PMC-0008-CC57/TBD32/3/PR02/WH and PS5-04-PMC-0008-CC57/TBD32/4/PR02/BK to be changed, wire exposed | EITS | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  | Yes | 2026-05-22T05:50:17.000 | Silaban, Junardi | PS5 - Milestone H
PL-006879 | PS5-06-GU-0001-CC03 (Reconnection) |  | A | I | Ferulle for PS5-06-GU-0001-CC03/TBA01/1/PR01/WH and PS5-06-GU-0001-CC03/TBA01/1/PR01/BK to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Yes | 2026-05-22T05:52:40.000 | Silaban, Junardi | PS5 - Milestone A
PL-006880 | PS5-06-GU-0001-CC04 (Reconnection) |  | A | I | All ferulles at PS5-03-SFMC-0003/TBA01 to be changed,wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Yes | 2026-05-22T05:55:17.000 | Silaban, Junardi | PS5 - Milestone A
PL-006881 | PS5-61-IJ-0001-CC01 (Reconnection) |  | A |  | All ferulles at PS5-04-PMC-0006/TBA05 to be changed, wire exposed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Yes | 2026-05-22T05:57:49.000 | Silaban, Junardi | PS5 - Milestone D
PL-006882 | PS5-61-IJ-0001-CC02 (Reconnection) |  | A | I | All ferulles at PS5-04-PMC-0006/TBA06 to be changed,wire exposed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Yes | 2026-05-22T06:00:14.000 | Silaban, Junardi | PS5 - Milestone D
PL-006883 | PS5-61-IJ-0001-CC03 (Reconnection) |  | A | I | All ferulles at PS5-04-PMC-0006/TBA07 to be changed, wire exposed | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Yes | 2026-05-22T06:02:06.000 | Silaban, Junardi | PS5 - Milestone D
PL-006884 | PS5-61-IK-0001-CC15 (Reconnection) |  | A | I | to be changed ferulle for PS5-61-IK-0001-CC15/TBA02/1/PR01/WH; /3/PR02/WH and /5/PR03/WH, wire exposed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T06:04:28.000 | Silaban, Junardi | PS5 - Milestone A
PL-006885 | PS5-61-IK-0001-CC40 (Reconnection) |  | A | I | to be changed ferulle for PS5-61-0001-CC40/TBD01/1/PR01/WH and PS5-61-0001-CC40/TBD01/8/PR04/BK, wire exposed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T06:06:13.000 | Silaban, Junardi | PS5 - Milestone A
PL-006886 | PS5-61-IK-0001-CC43 (Reconnection) |  | A | I | to be changed ferulle for PS5-61-0001-CC43/TBD03/1/PR01/WH ; /2/PR01/BK and PS5-61-0001-CC43/TBD02/3/PR02/WH; /4/PR02/BK , wire exposed | EITS | PS5-04-04 - 33kV PCS System |  | Originated |  | Yes | 2026-05-22T06:07:44.000 | Silaban, Junardi | PS5 - Milestone A
PL-006887 | PS5-03-SFMC-0006-CC57 (Reconnection) |  | A | I | Ferulle for PS5-03-SFMC-0006-CC57/TBD07/1/PR01/WH and PS5-03-SFMC-0006-CC57/TBD07/4/PR02/BK to be changed, wire exposed | EITS | PS5-71-01 - CFO Storage Tank Feed Heater |  | Originated |  | Yes | 2026-05-22T06:09:51.000 | Silaban, Junardi | PS5 - Milestone H
PL-006888 | PS5-03-SFMC-0006-CC45 (Reconnection) |  | A | I | Ferulle for PS5-03-SFMC-0006-CC45/TBD02/1/PR01/WH and PS5-03-SFMC-0006-CC45/TBD02/3/PR02/WH to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Yes | 2026-05-22T06:11:54.000 | Silaban, Junardi | PS5 - Milestone A
PL-006889 | PS5-03-SFMC-0006-CC38 (Reconnection) |  | B | I | Ferulle for PS5-03-SFMC-0006-CC02/TBA12/4/PR02/BK to be changed, wire exposed | EITS | PS5-04-05 - 33kV SIS/FGS System |  | Originated |  | Yes | 2026-05-22T06:13:19.000 | Silaban, Junardi | PS5 - Milestone A
PL-006894 | PS5-05-BE-0001-CG01 |  | A | E | Earth boss and Termination missing | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  | Install all earth bosses as per the drawing and proceed with the termination of the earthing cables at the bosses and equipment | 2026-05-22T08:39:27.993 | Gawad, Mohamed | PS5 - Milestone C
PL-006895 | PS5-05-BE-0001-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:10:07.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T10:18:15.737 | Gawad, Mohamed | PS5 - Milestone C
PL-006896 | PS5-05-BE-0001-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:10:29.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T10:31:11.680 | Gawad, Mohamed | PS5 - Milestone C
PL-006897 | PS5-05-BE-0001-CL03 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:10:42.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T10:39:21.130 | Gawad, Mohamed | PS5 - Milestone C
PL-006898 | PS5-05-BE-0001-CL04 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:10:56.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T10:45:15.300 | Gawad, Mohamed | PS5 - Milestone C
PL-006899 | PS5-05-BE-0001-CL05 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:11:10.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-22T10:52:00.140 | Gawad, Mohamed | PS5 - Milestone C
PL-006900 | PS5-05-BE-0001-CL06 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:11:57.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T11:00:11.213 | Gawad, Mohamed | PS5 - Milestone C
PL-006901 | PS5-61-IK-0003-CL56 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:12:10.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T11:05:50.120 | Gawad, Mohamed | PS5 - Milestone C
PL-006903 | PS5-61-IK-0003-CL55 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:12:22.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T11:13:18.980 | Gawad, Mohamed | PS5 - Milestone C
PL-006904 | PS5-05-BE-0001-CL08 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:12:36.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T11:16:02.703 | Gawad, Mohamed | PS5 - Milestone C
PL-006905 | PS5-05-BE-0001-CL09 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:12:48.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-22T11:23:07.127 | Gawad, Mohamed | PS5 - Milestone C
PL-006906 | PS5-05-BE-0001-CL11 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:13:02.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T11:24:30.343 | Gawad, Mohamed | PS5 - Milestone C
PL-006907 | PS5-05-BE-0001-CL10 |  | A | E | Cable to be connected | CPP AGI | PS5-05-01 - Emergency Diesel Generator Package | 2026-06-14T09:13:17.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-22T11:30:00.780 | Gawad, Mohamed | PS5 - Milestone C
PL-006926 | PS5-87-IRF-0001-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-53-01 - Utility Water / Storage Tank | 2026-06-14T09:14:15.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T08:26:16.377 | Gawad, Mohamed | PS5 - Milestone C
PL-006927 | PS5-74-LB-5101-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-74-02 - N2 Generation Skid (UCP) | 2026-06-14T09:14:28.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T08:36:06.897 | Gawad, Mohamed | PS5 - Milestone F
PL-006928 | PS5-71-XV-0092-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank | 2026-06-14T09:14:41.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T08:44:09.940 | Gawad, Mohamed | PS5 - Milestone B
PL-006929 | PS5-28-SDV-0053B-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-28-14 - Seal Oil Drain Drum & Pump B | 2026-06-14T09:14:55.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-23T09:03:17.360 | Gawad, Mohamed | PS5 - Milestone H
PL-006930 | PS5-28-SDV-0053C-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-28-15 - Seal Oil Drain Drum & Pump C | 2026-06-14T09:18:12.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:02:48.387 | Gawad, Mohamed | PS5 - Milestone H
PL-006931 | PS5-71-XV-0090-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-12 - CFO Service Tank | 2026-06-14T09:18:32.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:04:46.427 | Gawad, Mohamed | PS5 - Milestone H
PL-006932 | PS5-71-XV-0089-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-04 - CFO Storage Tank | 2026-06-14T09:18:49.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:10:23.600 | Gawad, Mohamed | PS5 - Milestone H
PL-006933 | PS5-71-SDV-0039-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-12 - CFO Service Tank | 2026-06-14T09:19:04.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:18:39.977 | Gawad, Mohamed | PS5 - Milestone H
PL-006934 | PS5-71-SDV-0001-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-20 - Diesel Fuel Day Tank | 2026-06-14T09:19:16.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:26:37.613 | Gawad, Mohamed | PS5 - Milestone B
PL-006939 | PS5-62-IE-0002-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-62-02 - Lighting Control Panel - PS5-62-IE-0002 | 2026-06-14T09:19:29.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:40:22.937 | Gawad, Mohamed | PS5 - Milestone G
PL-006940 | PS5-61-IV-0007B-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:20:05.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:40:24.420 | Gawad, Mohamed | PS5 - Milestone D
PL-006943 | PS5-71-FCV-0019-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-21 - Diesel Transfer Pump A/B | 2026-06-14T09:20:16.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:47:07.603 | Gawad, Mohamed | PS5 - Milestone B
PL-006947 | PS5-61-IV-0007A-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:20:28.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:57:40.177 | Gawad, Mohamed | PS5 - Milestone D
PL-006948 | PS5-71-FCV-0020-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-05 - CFO Transfer Pump A/B | 2026-06-14T09:20:40.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T10:59:33.527 | Gawad, Mohamed | PS5 - Milestone H
PL-006949 | PS5-71-HE-2200-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-71-12 - CFO Service Tank | 2026-06-14T09:20:52.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T11:18:39.080 | Gawad, Mohamed | PS5 - Milestone H
PL-006950 | PS5-71-LCV-4101-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-04 - CFO Storage Tank | 2026-06-14T09:21:29.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T11:23:17.423 | Gawad, Mohamed | PS5 - Milestone H
PL-006951 | PS5-61-BI-0001-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-60-01 - Power Generation Package A | 2026-06-14T09:21:54.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T11:31:52.130 | Gawad, Mohamed | PS5 - Milestone B
PL-006952 | PS5-61-BI-0002-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-60-04 - Power Generation Package B | 2026-06-14T09:22:06.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T11:35:58.607 | Gawad, Mohamed | PS5 - Milestone B
PL-006953 | PS5-61-IK-0006-CL34 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:22:18.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T11:48:47.420 | Gawad, Mohamed | PS5 - Milestone D
PL-006954 | PS5-71-HE-2200 |  | C | M | 4:During the inspection, the tag number and nameplate were not found. | EPS VENDOR | PS5-71-12 - CFO Service Tank |  | Originated |  |  | 2026-05-23T12:19:09.930 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-006955 | PS5-71-HE-2200 |  | C | M | 4.1:Two gaskets arrived without a packing list. | EPS VENDOR | PS5-71-12 - CFO Service Tank |  | Originated |  |  | 2026-05-23T12:19:57.060 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-006956 | PS5-71-HE-2200 |  | A | M | 4.2:The duplex RTD 3-wire was found improperly aligned and extending outside the heater bundle | EPS VENDOR | PS5-71-12 - CFO Service Tank |  | Originated |  |  | 2026-05-23T12:21:06.913 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-006957 | PS5-71-HE-2300 |  | C | M | 4:During the inspection, the tag number and nameplate were not found. | EPS VENDOR | PS5-71-04 - CFO Storage Tank |  | Originated |  |  | 2026-05-23T12:22:57.200 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-006958 | PS5-71-HE-2300 |  | C | M | 4.1:Two gaskets arrived without a packing list. | EPS VENDOR | PS5-71-04 - CFO Storage Tank |  | Originated |  |  | 2026-05-23T12:23:53.917 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-006959 | PS5-71-HE-2300 |  | A | M | 4.2:The duplex RTD 3-wire was found improperly aligned and extending outside the heater bundle | EPS VENDOR | PS5-71-04 - CFO Storage Tank |  | Originated |  |  | 2026-05-23T12:24:44.540 | THANGARATHINAM, ajikumar | PS5 - Milestone H
PL-006960 | PS5-61-IK-0006-CL33 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:23:13.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T12:40:36.300 | Gawad, Mohamed | PS5 - Milestone D
PL-006961 | PS5-61-IK-0006-CL28 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:23:28.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T12:51:58.850 | Gawad, Mohamed | PS5 - Milestone D
PL-006962 | PS5-61-IK-0006-CL27 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:23:41.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T13:04:37.107 | Gawad, Mohamed | PS5 - Milestone D
PL-006963 | PS5-61-IK-0006-CL26 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:23:52.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T13:11:22.007 | Gawad, Mohamed | PS5 - Milestone D
PL-006964 | PS5-61-BI-0007-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-60-19 - Power Generation Package G | 2026-06-14T09:24:07.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-23T13:18:43.630 | Gawad, Mohamed | PS5 - Milestone E
PL-006967 | PS5-28-HE-2100-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-28-03 - Closed Drain Drum and Pump 01 | 2026-06-14T09:24:19.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T05:44:25.933 | Gawad, Mohamed | PS5 - Milestone G
PL-006968 | PS5-28-BE-0002B-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-28-17 - Reinjection Pump | 2026-06-14T09:24:31.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T05:49:29.183 | Gawad, Mohamed | PS5 - Milestone H
PL-006969 | PS5-28-BE-0002A-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-28-17 - Reinjection Pump | 2026-06-14T09:24:44.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T05:58:48.983 | Gawad, Mohamed | PS5 - Milestone H
PL-006970 | PS5-25-MOV-0008-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-07 - Export Pipeline Pig Launcher | 2026-06-14T09:26:45.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T06:15:33.847 | Gawad, Mohamed | PS5 - Milestone H
PL-006971 | PS5-25-MOV-0025-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-01 - Export Pipeline Pig Receiver | 2026-06-14T09:26:58.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T06:29:11.673 | Gawad, Mohamed | PS5 - Milestone H
PL-006972 | PS5-25-MOV-0026-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-01 - Export Pipeline Pig Receiver | 2026-06-14T09:27:11.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T06:36:27.230 | Gawad, Mohamed | PS5 - Milestone H
PL-006973 | PS5-25-SDV-0046-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-05 - Crude Oil Export Pumps Bypass | 2026-06-14T09:27:32.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T07:15:26.360 | Gawad, Mohamed | PS5 - Milestone H
PL-006974 | PS5-25-DM-3100A-CG01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-02 - Crude Oil Export Pump A | 2026-06-14T09:27:48.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T07:41:23.083 | Gawad, Mohamed | PS5 - Milestone H
PL-006975 | PS5-25-DM-3100A-CG02 |  | A | E | Cable to be connected | CPP AGI | PS5-25-02 - Crude Oil Export Pump A | 2026-06-14T09:28:00.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T07:48:34.160 | Gawad, Mohamed | PS5 - Milestone H
PL-006976 | PS5-01-BE-0001-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100) | 2026-06-14T09:28:12.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-24T07:59:41.013 | Gawad, Mohamed | PS5 - Milestone F
PL-007094 | PS5-01-FCV-0003A-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-01-02 - Fire Water Pump A | 2026-06-14T09:28:39.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-26T10:23:56.360 | Anwar, Zeeshan | PS5 - Milestone C
PL-007095 | PS5-61-IU-3100A-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | : Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T10:25:54.270 | Gawad, Mohamed | PS5 - Milestone H
PL-007096 | PS5-61-IU-3100C-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:19:01.280 | Gawad, Mohamed | PS5 - Milestone H
PL-007097 | PS5-61-IU-3100B-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:21:24.180 | Gawad, Mohamed | PS5 - Milestone H
PL-007099 | PS5-61-IDH-3100A-CH01 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:23:38.863 | Gawad, Mohamed | PS5 - Milestone H
PL-007100 | PS5-61-IDH-3100A-CH02 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:25:34.943 | Gawad, Mohamed | PS5 - Milestone H
PL-007101 | PS5-61-IDH-3100A-CH03 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:27:53.930 | Gawad, Mohamed | PS5 - Milestone H
PL-007102 | PS5-61-IDH-3100A-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:29:35.067 | Gawad, Mohamed | PS5 - Milestone H
PL-007103 | PS5-61-IDH-3100A-CH05 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:31:19.660 | Gawad, Mohamed | PS5 - Milestone H
PL-007104 | PS5-61-IDH-3100A-CH06 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:32:36.020 | Gawad, Mohamed | PS5 - Milestone H
PL-007105 | PS5-61-IDH-3100A-CH07 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:34:19.290 | Gawad, Mohamed | PS5 - Milestone H
PL-007106 | PS5-61-IDH-3100A-CH08 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:37:40.647 | Gawad, Mohamed | PS5 - Milestone H
PL-007107 | PS5-61-IDH-3100A-CH09 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:39:16.740 | Gawad, Mohamed | PS5 - Milestone H
PL-007108 | PS5-61-IDH-3100A-CH10 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:40:46.563 | Gawad, Mohamed | PS5 - Milestone H
PL-007109 | PS5-61-IDH-3100A-CH11 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:42:30.157 | Gawad, Mohamed | PS5 - Milestone H
PL-007110 | PS5-61-IDH-3100A-CH12 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:44:07.907 | Gawad, Mohamed | PS5 - Milestone H
PL-007111 | PS5-61-IDH-3100B-CH01 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:45:31.667 | Gawad, Mohamed | PS5 - Milestone H
PL-007112 | PS5-61-IDH-3100B-CH02 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:50:08.377 | Gawad, Mohamed | PS5 - Milestone H
PL-007113 | PS5-61-IDH-3100B-CH03 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:53:20.510 | Gawad, Mohamed | PS5 - Milestone H
PL-007114 | PS5-61-IDH-3100B-CH04 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:54:58.720 | Gawad, Mohamed | PS5 - Milestone H
PL-007115 | PS5-61-IDH-3100B-CH05 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:56:32.710 | Gawad, Mohamed | PS5 - Milestone H
PL-007117 | PS5-61-IDH-3100B-CH07 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T11:59:26.417 | Gawad, Mohamed | PS5 - Milestone H
PL-007118 | PS5-61-IDH-3100B-CH08 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T12:02:02.193 | Gawad, Mohamed | PS5 - Milestone H
PL-007119 | PS5-61-IDH-3100B-CH09 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T12:03:33.743 | Gawad, Mohamed | PS5 - Milestone H
PL-007120 | PS5-61-IDH-3100B-CH10 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T12:05:29.840 | Gawad, Mohamed | PS5 - Milestone H
PL-007121 | PS5-61-IDH-3100B-CH11 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T12:06:54.703 | Gawad, Mohamed | PS5 - Milestone H
PL-007122 | PS5-61-IDH-3100B-CH12 |  | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Replace temporary cable ties with permanent trefoil cleats upon material availability. | 2026-05-26T12:08:40.483 | Gawad, Mohamed | PS5 - Milestone H
PL-007173 | PS5-61-IK-0006-CL25 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:29:05.000 | Closed |  | Cable to be connected | 2026-05-28T08:12:17.430 | Gawad, Mohamed | PS5 - Milestone D
PL-007176 | PS5-61-BI-0003-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-60-07 - Power Generation Package C | 2026-06-14T09:29:20.000 | Closed |  | Cable must be connected, glanded, and terminated | 2026-05-28T08:48:17.607 | Gawad, Mohamed | PS5 - Milestone D
PL-007177 | PS5-61-BI-0004-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-60-10 - Power Generation Package D | 2026-06-14T09:29:43.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-28T09:13:51.000 | Gawad, Mohamed | PS5 - Milestone D
PL-007178 | PS5-61-BI-0005-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-60-13 - Power Generation Package E | 2026-06-14T09:29:56.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-28T09:28:03.787 | Gawad, Mohamed | PS5 - Milestone D
PL-007179 | PS5-61-BI-0006-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-60-16 - Power Generation Package F | 2026-06-14T09:30:13.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-28T09:40:06.420 | Gawad, Mohamed | PS5 - Milestone D
PL-007180 | PS5-61-IK-0006-CL23 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:30:43.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-28T10:42:01.260 | Gawad, Mohamed | PS5 - Milestone D
PL-007181 | PS5-61-IK-0006-CL24 |  | A | E | Cable to be connected | CPP AGI | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 2026-06-14T09:30:57.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-28T10:52:21.093 | Gawad, Mohamed | PS5 - Milestone D
PL-007192 | PS5-06-GB-0003-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:31:28.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:03:05.363 | Anwar, Zeeshan | PS5 - Milestone B
PL-007193 | PS5-06-GB-0003-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:31:39.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:13:07.740 | Anwar, Zeeshan | PS5 - Milestone B
PL-007194 | PS5-74-LB-5101-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-74-02 - N2 Generation Skid (UCP) | 2026-06-14T09:31:52.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:16:14.453 | Gawad, Mohamed | PS5 - Milestone F
PL-007195 | PS5-06-GB-0003-CL03 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:32:06.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:17:33.417 | Anwar, Zeeshan | PS5 - Milestone B
PL-007196 | PS5-06-GB-0003-CL04 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:32:18.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:23:35.477 | Anwar, Zeeshan | PS5 - Milestone B
PL-007197 | PS5-06-GB-0003-CL05 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:32:31.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:28:34.650 | Anwar, Zeeshan | PS5 - Milestone B
PL-007198 | PS5-06-GB-0003-CL06 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:32:45.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:33:54.523 | Anwar, Zeeshan | PS5 - Milestone B
PL-007199 | PS5-06-IG-0004B-CL04 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:33:02.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:36:26.817 | Gawad, Mohamed | PS5 - Milestone B
PL-007200 | PS5-06-GU-0003A-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:33:32.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:39:03.543 | Anwar, Zeeshan | PS5 - Milestone B
PL-007201 | PS5-06-GU-0003B-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:33:43.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:45:35.833 | Anwar, Zeeshan | PS5 - Milestone B
PL-007202 | PS5-06-GU-0003C-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:33:55.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:52:59.927 | Anwar, Zeeshan | PS5 - Milestone B
PL-007203 | PS5-06-IG-0004A-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:34:07.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T05:55:57.857 | Anwar, Zeeshan | PS5 - Milestone B
PL-007204 | PS5-06-IG-0004A-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:34:20.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T06:02:18.770 | Anwar, Zeeshan | PS5 - Milestone B
PL-007205 | PS5-06-IG-0004A-CL03 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:34:32.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T06:07:48.803 | Anwar, Zeeshan | PS5 - Milestone B
PL-007206 | PS5-06-IG-0004A-CL04 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:34:44.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T07:01:35.143 | Anwar, Zeeshan | PS5 - Milestone B
PL-007207 | PS5-06-IG-0004B-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:34:57.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T07:23:52.217 | Anwar, Zeeshan | PS5 - Milestone B
PL-007211 | PS5-06-IG-0004B-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:35:29.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T10:58:14.283 | Anwar, Zeeshan | PS5 - Milestone B
PL-007212 | PS5-06-IG-0004B-CL03 |  | A | E | Cable to be connected | CPP AGI | PS5-06-02 - AC UPS - Power Generator Building | 2026-06-14T09:35:46.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-05-29T11:03:58.807 | Anwar, Zeeshan | PS5 - Milestone B
PL-007231 | PS5-60-TCV-0001C |  | C | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-05-30T06:08:03.527 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-007232 | PS5-60-TCV-0001C |  | C | M | 10.1: TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-72 - Engine C Cooling system |  | Originated |  | TOUCH UP PAINTING TO BE DONE | 2026-05-30T06:09:27.880 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-007233 | PS5-60-TCV-0001E |  | C | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | 2026-05-30T06:12:31.480 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-007234 | PS5-60-TCV-0001E |  | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | CPP AGI | PS5-60-74 - Engine E Cooling system |  | Originated |  | TOUCH UP PAINTING TO BE DONE | 2026-05-30T06:13:30.947 | THANGARATHINAM, ajikumar | PS5 - Milestone D
PL-007305 | PS5-61-IDH-3100C-CH01 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T14:21:42.287 | Gawad, Mohamed | PS5 - Milestone H
PL-007306 | PS5-61-IDH-3100C-CH02 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T14:26:04.707 | Gawad, Mohamed | PS5 - Milestone H
PL-007307 | PS5-61-IDH-3100C-CH03 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T14:27:53.310 | Gawad, Mohamed | PS5 - Milestone H
PL-007308 | PS5-61-IDH-3100C-CH04 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T14:29:29.227 | Gawad, Mohamed | PS5 - Milestone H
PL-007309 | PS5-61-IDH-3100C-CH05 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T14:30:57.493 | Gawad, Mohamed | PS5 - Milestone H
PL-007310 | PS5-61-IDH-3100C-CH06 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T14:32:31.760 | Gawad, Mohamed | PS5 - Milestone H
PL-007311 | PS5-61-IDH-3100C-CH07 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T15:40:13.450 | Gawad, Mohamed | PS5 - Milestone H
PL-007312 | PS5-61-IDH-3100C-CH08 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T15:55:48.937 | Gawad, Mohamed | PS5 - Milestone H
PL-007313 | PS5-61-IDH-3100C-CH09 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T15:57:22.227 | Gawad, Mohamed | PS5 - Milestone H
PL-007314 | PS5-61-IDH-3100C-CH10 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T15:58:49.440 | Gawad, Mohamed | PS5 - Milestone H
PL-007315 | PS5-61-IDH-3100C-CH11 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T16:01:03.407 | Gawad, Mohamed | PS5 - Milestone H
PL-007316 | PS5-61-IDH-3100C-CH12 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T16:03:27.373 | Gawad, Mohamed | PS5 - Milestone H
PL-007317 | PS5-61-IV-0002A-CH03 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T16:04:59.563 | Gawad, Mohamed | PS5 - Milestone B
PL-007318 | PS5-61-IV-0002B-CH01 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T16:07:23.277 | Gawad, Mohamed | PS5 - Milestone B
PL-007319 | PS5-61-IV-0002B-CH02 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-05-30T16:08:50.690 | Gawad, Mohamed | PS5 - Milestone B
PL-007333 | PS5-71-FCV-0018-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-13 - CFO Service Pump A/B | 2026-06-14T09:36:13.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-06-01T09:22:58.710 | Gawad, Mohamed | PS5 - Milestone H
PL-007334 | PS5-71-HE-2300-CL02 |  | A | E | Cable to be connected | CPP AGI | PS5-71-04 - CFO Storage Tank | 2026-06-14T09:36:28.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-06-01T09:31:56.200 | Gawad, Mohamed | PS5 - Milestone H
PL-007709 | PS5-25-XV-0053-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-25-05 - Crude Oil Export Pumps Bypass | 2026-06-14T09:37:48.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-06-04T06:26:41.367 | Gawad, Mohamed | PS5 - Milestone H
PL-007710 | PS5-60-MOV-0005-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-12 - CFO Service Tank | 2026-06-14T09:38:02.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-06-04T06:31:04.173 | Gawad, Mohamed | PS5 - Milestone H
PL-007711 | PS5-60-MOV-0006-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-12 - CFO Service Tank | 2026-06-14T09:38:15.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-06-04T06:34:25.537 | Gawad, Mohamed | PS5 - Milestone H
PL-007713 | PS5-60-MOV-0011-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-12 - CFO Service Tank | 2026-06-14T09:38:30.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-06-04T06:40:19.920 | Gawad, Mohamed | PS5 - Milestone H
PL-007715 | PS5-60-MOV-0012-CL01 |  | A | E | Cable to be connected | CPP AGI | PS5-71-12 - CFO Service Tank | 2026-06-14T09:38:46.000 | Closed |  | Cable must be connected, glanded, and terminated. | 2026-06-04T06:44:45.967 | Gawad, Mohamed | PS5 - Milestone H
PL-007805 | PS5-75-UI-6100 |  | A | M | 4:The welding quality on the skid is not up to the required standard, and cracks were observed in the weld areas throughout the skid. (All welded areas). | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:11:00.470 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007806 | PS5-75-UI-6100 |  | A | M | 4.1:During inspection, the U-clamp was found missing | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:12:45.880 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007807 | PS5-75-UI-6100 |  | B | M | 4.2:During inspection, the U-clamp was found to be improperly installed | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:13:50.493 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007808 | PS5-75-UI-6100 |  | A | M | 4.3:During the inspection, oil leakage was observed from the diaphragm pump. (PS5-75-PB-3200A). | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:15:04.780 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007809 | PS5-75-UI-6100 |  | A | M | 4.4:During the inspection, oil leakage was observed from the diaphragm pump (PS5-75-PB-3200B). | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:16:24.617 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007810 | PS5-75-UI-6100 |  | C | M | 4.5:As per the packing list, Canopy Tag No. 3300A & 3300B but received Tag No. 3200A & 3200B. | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:17:08.580 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007811 | PS5-75-UI-6100 |  | A | M | 4.6:During inspection After welding the pad plate, the vent holes were required to be sealed. but no one vent hole was didnt sealed,. | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:18:15.537 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007812 | PS5-75-UI-6100 |  | B | M | 4.7:During the inspection, some diaphragm pump support bolts were found loose, and some bolts were missing. (PS5-75-PB-3200A/B) | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:19:02.503 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007813 | PS5-75-UI-6100 |  | A | M | 4.8:During the inspection, the support bracing was found missing. | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:20:56.643 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007814 | PS5-75-UI-6100 |  | A | M | 4.9:"During the inspection, the diaphragm valve was found broken (PS5-75-BAV-1024)" | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:21:45.620 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007815 | PS5-75-UI-6100 |  | B | E | 4.10:"During Inspection, unproper Glanding Cable Gland for Cable Tag PS5-75-LIT-4202A-CJ01" | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:22:47.653 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007816 | PS5-75-UI-6100 |  | B | E | 4.11:SS Hanging Tagging for all General Transmitteri is Missing | EPS VENDOR | PS5-75-02 - Biocide Injection Package |  | Originated |  |  | 2026-06-05T08:23:39.187 | THANGARATHINAM, ajikumar | PS5 - Milestone G
PL-007853 | PS5-61-ISR-0102 |  | C | E | 20: CP261 Pressure relay for main tank indicator was found without glass as manufactured from factory. | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Vendor to clarify | 2026-06-06T07:06:02.493 | gregory, dismas | PS5 - Milestone D
PL-007854 | PS5-61-ISR-0102 |  | B | E | 20.1: BR321 Gas collection pipe for gas sampling have small diameter compared to its coupling point on the Bucholz relay | EITS | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) |  | Originated |  | Vendor to supply BR321 Gas collection pipe for gas sampling with correct diameter as coupling point on Bucholz relay | 2026-06-06T07:55:47.963 | gregory, dismas | PS5 - Milestone D
PL-008229 | PS5-25-PDIT-0034A |  | A | I | instrument to be replaced once the new transmitters arrive at site. | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | The instruments currently available at site will be used only for hydro test purposes on a temporary basis. | 2026-06-10T05:04:58.957 | Thao-my, Alexandre | PS5 - Milestone H
PL-008230 | PS5-25-PDIT-0034B |  | A | I | instrument to be replaced once the new transmitters arrive at site. | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | The instruments currently available at site will be used only for hydro test purposes on a temporary basis. | 2026-06-10T05:04:58.957 | Thao-my, Alexandre | PS5 - Milestone H
PL-008231 | PS5-25-PDIT-0034C |  | A | I | instrument to be replaced once the new transmitters arrive at site. | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | The instruments currently available at site will be used only for hydro test purposes on a temporary basis. | 2026-06-10T05:04:58.957 | Thao-my, Alexandre | PS5 - Milestone H
PL-008468 |  | EACOP-PS5-25-01-0050 | B | P | 18: Paint touchup to be done | CPP AGI | PS5-25-01 - Export Pipeline Pig Receiver |  | Originated |  | EACOP-PS5-25-01-0050 Paint touchup to be done | 2026-06-13T06:53:54.780 | Bhagavath, sangeeth | PS5 - Milestone H
PL-008469 |  | EACOP-PS5-25-07-0068 | B | P | 18: Paint touchup to be done | CPP AGI | PS5-25-07 - Export Pipeline Pig Launcher |  | Originated |  | EACOP-PS5-25-07-0068 Paint touchup to be done | 2026-06-13T07:07:40.273 | Bhagavath, sangeeth | PS5 - Milestone H
PL-008493 | PS5-05-BE-0001 |  | B | E | EDG PJB - Anti-condensation heater circuit is missing | EACOP | PS5-05-01 - Emergency Diesel Generator Package |  | Originated |  | Anti-condensation heater circuit (terminals, thermostat, heater, wiring) to be installed on DIN rail once received at site | 2026-06-15T11:32:05.000 | Dujancourt, Alban | PS5 - Milestone C
PL-008540 | PS5 - DIESEL FUEL STORAGE AND PUMP AREA_Earthing |  | B | E | 4 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 4 earthing points must be terminated per approved drawings. | 2026-06-16T06:16:15.000 | Gawad, Mohamed | PS5 - Milestone A
PL-008548 | PS5 - CHEMICAL AND WASTE STORAGE AREA_Earthing |  | B | E | 9 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 9 earthing points must be terminated per approved drawings. | 2026-06-16T06:36:32.647 | Gawad, Mohamed | PS5 - Milestone A
PL-008553 | PS5 - POWER DISTRIBUTION AREA_Earthing |  | B | E | 5 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 5 earthing points must be terminated per approved drawings. | 2026-06-16T06:54:36.810 | Gawad, Mohamed | PS5 - Milestone A
PL-008564 | PS5-84-OB-0003_Earthing |  | B | E | 2 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 2 earthing points must be terminated per approved drawings. | 2026-06-16T08:02:31.803 | Gawad, Mohamed | PS5 - Milestone A
PL-008567 | PS5-84-OB-0004_Earthing |  | B | E | 2 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 2 earthing points must be terminated per approved drawings. | 2026-06-16T08:05:10.067 | Gawad, Mohamed | PS5 - Milestone A
PL-008569 | PS5 - EXPORT PUMP VSD AREA_Earthing |  | B | E | 7 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | earthing points must be terminated per approved drawings. | 2026-06-16T08:43:41.160 | Gawad, Mohamed | PS5 - Milestone A
PL-008570 | PS5 - LAUNCHER/RECEIVER AREA_Earthing |  | B | E | 10 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 10 earthing points must be terminated per approved drawings. | 2026-06-16T08:51:27.787 | Gawad, Mohamed | PS5 - Milestone A
PL-008571 | PS5 - EXPORT LOADING PUMP AREA_Earthing |  | B | E | 6 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 6 earthing points must be terminated per approved drawings. | 2026-06-16T08:54:30.243 | Gawad, Mohamed | PS5 - Milestone A
PL-008572 | PS5 - POWER GENERATION BUILDING AREA_Earthing |  | B | E | 4 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 4 earthing points must be terminated per approved drawings. | 2026-06-16T09:11:02.223 | Gawad, Mohamed | PS5 - Milestone A
PL-008573 | PS5 - CLOSED DRAIN DRUM AREA_Earthing |  | B | E | 7points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 7 earthing points must be terminated per approved drawings. | 2026-06-16T09:14:14.680 | Gawad, Mohamed | PS5 - Milestone A
PL-008574 | PS5 - POWER GENERATION COOLING TOWER AREA_Earthing |  | B | E | 20 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 20 earthing points must be terminated per approved drawings. | 2026-06-16T09:17:32.840 | Gawad, Mohamed | PS5 - Milestone A
PL-008591 | PS5 - CFO AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection | 2026-06-17T04:27:16.410 | Gawad, Mohamed | PS5 - Milestone A
PL-008592 | PS5 - CFO AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag | 2026-06-17T04:41:33.910 | Gawad, Mohamed | PS5 - Milestone A
PL-008593 | PS5 - CFO AREA_Earthing |  | C | E | Earthing chamber tag installed | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag | 2026-06-17T04:43:23.163 | Gawad, Mohamed | PS5 - Milestone A
PL-008600 | PS5 - CHEMICAL AND WASTE STORAGE AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T12:26:36.510 | Gawad, Mohamed | PS5 - Milestone A
PL-008601 | PS5 - CHEMICAL AND WASTE STORAGE AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag | 2026-06-17T12:29:01.473 | Gawad, Mohamed | PS5 - Milestone A
PL-008602 | PS5 - CLOSED DRAIN DRUM AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection | 2026-06-17T12:36:33.393 | Gawad, Mohamed | PS5 - Milestone A
PL-008603 | PS5 - CLOSED DRAIN DRUM AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T12:37:32.347 | Gawad, Mohamed | PS5 - Milestone A
PL-008605 | PS5 - DIESEL FUEL STORAGE AND PUMP AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection | 2026-06-17T12:40:25.600 | Gawad, Mohamed | PS5 - Milestone A
PL-008607 | PS5 - DIESEL FUEL STORAGE AND PUMP AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag | 2026-06-17T12:42:54.893 | Gawad, Mohamed | PS5 - Milestone A
PL-008608 | PS5 - DIESEL FUEL STORAGE AND PUMP AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T12:43:35.390 | Gawad, Mohamed | PS5 - Milestone A
PL-008609 | PS5 - EXPORT PUMP VSD AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T12:45:45.890 | Gawad, Mohamed | PS5 - Milestone A
PL-008610 | PS5 - EXPORT PUMP VSD AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T12:46:20.530 | Gawad, Mohamed | PS5 - Milestone A
PL-008611 | PS5 - EXPORT PUMP VSD AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T12:47:47.830 | Gawad, Mohamed | PS5 - Milestone A
PL-008612 | PS5 - EXPORT LOADING PUMP AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T12:53:48.533 | Gawad, Mohamed | PS5 - Milestone A
PL-008613 | PS5 - EXPORT LOADING PUMP AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T12:54:07.627 | Gawad, Mohamed | PS5 - Milestone A
PL-008614 | PS5 - EXPORT LOADING PUMP AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T12:54:25.473 | Gawad, Mohamed | PS5 - Milestone A
PL-008615 | PS5 - FENCE WEST AREA_Earthing |  | B | E | 10 connections are not completed | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 10 earthing points must be terminated per approved drawings. | 2026-06-17T12:56:49.100 | Gawad, Mohamed | PS5 - Milestone A
PL-008616 | PS5 - FENCE WEST AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T13:00:01.383 | Gawad, Mohamed | PS5 - Milestone A
PL-008617 | PS5 - LAUNCHER/RECEIVER AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T13:29:05.313 | Gawad, Mohamed | PS5 - Milestone A
PL-008618 | PS5 - LAUNCHER/RECEIVER AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T13:29:33.733 | Gawad, Mohamed | PS5 - Milestone A
PL-008623 | PS5 - POWER DISTRIBUTION AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T14:17:37.033 | Gawad, Mohamed | PS5 - Milestone A
PL-008624 | PS5 - POWER DISTRIBUTION AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T14:18:22.593 | Gawad, Mohamed | PS5 - Milestone A
PL-008625 | PS5 - POWER DISTRIBUTION AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T14:18:49.853 | Gawad, Mohamed | PS5 - Milestone A
PL-008640 | PS5 - POWER GENERATION BUILDING AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T16:48:34.100 | Gawad, Mohamed | PS5 - Milestone A
PL-008641 | PS5 - POWER GENERATION BUILDING AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T16:56:50.527 | Gawad, Mohamed | PS5 - Milestone A
PL-008642 | PS5 - POWER GENERATION BUILDING AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T16:58:29.610 | Gawad, Mohamed | PS5 - Milestone A
PL-008643 | PS5 - POWER GENERATION COOLING TOWER AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T17:04:52.413 | Gawad, Mohamed | PS5 - Milestone A
PL-008644 | PS5 - POWER GENERATION COOLING TOWER AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T17:05:28.917 | Gawad, Mohamed | PS5 - Milestone A
PL-008645 | PS5 - POWER GENERATION COOLING TOWER AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T17:06:11.257 | Gawad, Mohamed | PS5 - Milestone A
PL-008646 | PS5 - UTILITY AREA_Earthing |  | B | E | 4 points are not terminated | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 4 earthing points must be terminated per approved drawings. | 2026-06-17T17:17:55.620 | Gawad, Mohamed | PS5 - Milestone A
PL-008647 | PS5 - UTILITY AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T17:19:05.120 | Gawad, Mohamed | PS5 - Milestone A
PL-008648 | PS5 - UTILITY AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T17:23:40.910 | Gawad, Mohamed | PS5 - Milestone A
PL-008649 | PS5 - UTILITY AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T17:24:24.860 | Gawad, Mohamed | PS5 - Milestone A
PL-008650 | PS5 - UTILITY/FIRE WATER STORAGE TANK AREA_Earthing |  | B | E | 7 points are not terminated. | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | 7earthing points must be terminated per approved drawings. | 2026-06-17T17:29:28.523 | Gawad, Mohamed | PS5 - Milestone A
PL-008651 | PS5 - UTILITY/FIRE WATER STORAGE TANK AREA_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T17:30:59.733 | Gawad, Mohamed | PS5 - Milestone A
PL-008652 | PS5 - UTILITY/FIRE WATER STORAGE TANK AREA_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T17:32:09.880 | Gawad, Mohamed | PS5 - Milestone A
PL-008653 | PS5 - UTILITY/FIRE WATER STORAGE TANK AREA_Earthing |  | C | E | earthing chamber tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing chamber tag. | 2026-06-17T17:32:51.080 | Gawad, Mohamed | PS5 - Milestone A
PL-008654 | PS5-84-OB-0003_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T17:35:21.410 | Gawad, Mohamed | PS5 - Milestone A
PL-008655 | PS5-84-OB-0003_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T17:36:09.993 | Gawad, Mohamed | PS5 - Milestone A
PL-008656 | PS5-84-OB-0004_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T17:41:53.783 | Gawad, Mohamed | PS5 - Milestone A
PL-008657 | PS5-84-OB-0004_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T17:44:04.253 | Gawad, Mohamed | PS5 - Milestone A
PL-008658 | PS5-84-OB-0006_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T17:50:03.987 | Gawad, Mohamed | PS5 - Milestone A
PL-008659 | PS5-84-OB-0006_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T17:57:44.797 | Gawad, Mohamed | PS5 - Milestone A
PL-008660 | PS5-84-OB-0007_Earthing |  | B | E | anticorrosive grease is not applied | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Apply anticorrosive grease to the earthing connection. | 2026-06-17T18:02:57.587 | Gawad, Mohamed | PS5 - Milestone A
PL-008661 | PS5-84-OB-0007_Earthing |  | C | E | earthing busbar tag is missing | CPP AGI | PS5-63-01 - Electrical Earthing |  | Originated |  | Install earthing busbar tag. | 2026-06-17T18:03:51.427 | Gawad, Mohamed | PS5 - Milestone A
PL-008674 | PS5-61-IV-0001A-CH01 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-06-18T11:50:36.900 | Gawad, Mohamed | PS5 - Milestone A
PL-008675 | PS5-61-IV-0001A-CH02 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-06-18T11:52:31.660 | Gawad, Mohamed | PS5 - Milestone A
PL-008676 | PS5-61-IV-0001A-CH03 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-06-18T11:54:30.143 | Gawad, Mohamed | PS5 - Milestone A
PL-008677 | PS5-61-IV-0001B-CH01 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-06-18T11:55:44.487 | Gawad, Mohamed | PS5 - Milestone A
PL-008678 | PS5-61-IV-0001B-CH02 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-06-18T11:57:24.583 | Gawad, Mohamed | PS5 - Milestone A
PL-008679 | PS5-61-IV-0001B-CH03 |  | A | E | trefoil cable cleats to be installed | CPP AGI | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) |  | Originated |  | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | 2026-06-18T11:58:42.733 | Gawad, Mohamed | PS5 - Milestone A
PL-008773 | PS5-25-IES-3200A-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T12:35:07.710 | Gawad, Mohamed | PS5 - Milestone H
PL-008774 | PS5-25-IES-3200A-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T12:42:34.493 | Gawad, Mohamed | PS5 - Milestone H
PL-008775 | PS5-25-IES-3200B-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T12:46:58.940 | Gawad, Mohamed | PS5 - Milestone H
PL-008776 | PS5-25-IES-3200B-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T12:47:38.230 | Gawad, Mohamed | PS5 - Milestone H
PL-008780 | PS5-25-IES-3300A-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T13:15:28.743 | Gawad, Mohamed | PS5 - Milestone H
PL-008782 | PS5-25-IES-3300A-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T13:16:10.960 | Gawad, Mohamed | PS5 - Milestone H
PL-008787 | PS5-25-IES-3300B-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T13:22:39.630 | Gawad, Mohamed | PS5 - Milestone H
PL-008788 | PS5-25-IES-3300B-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T13:23:00.713 | Gawad, Mohamed | PS5 - Milestone H
PL-008793 | PS5-25-IES-3400B-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T13:50:56.303 | Gawad, Mohamed | PS5 - Milestone H
PL-008794 | PS5-25-IES-3400B-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T13:51:18.297 | Gawad, Mohamed | PS5 - Milestone H
PL-008795 | PS5-25-IES-6400A-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T13:55:39.793 | Gawad, Mohamed | PS5 - Milestone H
PL-008796 | PS5-25-IES-6400A-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T13:55:56.950 | Gawad, Mohamed | PS5 - Milestone H
PL-008797 | PS5-25-IES-6400B-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T14:02:48.717 | Gawad, Mohamed | PS5 - Milestone H
PL-008798 | PS5-25-IES-6400B-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-02 - Crude Oil Export Pump A |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T14:18:22.100 | Gawad, Mohamed | PS5 - Milestone H
PL-008799 | PS5-25-IES-6500B-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T14:25:37.237 | Gawad, Mohamed | PS5 - Milestone H
PL-008800 | PS5-25-IES-6500B-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T14:26:02.663 | Gawad, Mohamed | PS5 - Milestone H
PL-008801 | PS5-25-IES-6600A-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T14:29:00.230 | Gawad, Mohamed | PS5 - Milestone H
PL-008802 | PS5-25-IES-6600A-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T14:29:16.993 | Gawad, Mohamed | PS5 - Milestone H
PL-008803 | PS5-25-IES-6600B-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T14:32:20.330 | Gawad, Mohamed | PS5 - Milestone H
PL-008804 | PS5-25-IES-6600B-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T14:32:37.817 | Gawad, Mohamed | PS5 - Milestone H
PL-008805 | PS5-25-IES-3400A-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T16:38:37.953 | Gawad, Mohamed | PS5 - Milestone H
PL-008806 | PS5-25-IES-3400A-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-04 - Crude Oil Export Pump C |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T16:39:04.270 | Gawad, Mohamed | PS5 - Milestone H
PL-008807 | PS5-25-IES-6500A-CD01 |  | B | E | Cable gland earthing not yet installed | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Install and connect earthing, verify by continuity test before closure | 2026-06-20T16:47:32.170 | Gawad, Mohamed | PS5 - Milestone H
PL-008808 | PS5-25-IES-6500A-CD01 |  | B | E | Wire dressing not yet done properly | CPP AGI | PS5-25-03 - Crude Oil Export Pump B |  | Originated |  | Re-dress and secure wiring per specification | 2026-06-20T16:48:08.693 | Gawad, Mohamed | PS5 - Milestone H