## 3 · BLOCKING – REMARKS
PS5 COMPLETION PLATFORM ¦ BLOCKERS - sorted by blocking count
SUB SYSTEM | PRIO | TOTAL % | CPP-1 | EIT | EACOP | REMARK EACOP | REMARK CPP-EIT | REMARK CPP-1 | WALKDOWN | ● | MY REMARKS
PS5-71-07 - Crude Fuel Separation Module (UCP) | 1.1 | 17% | 0 | 0 | 54 | cable drum not available for 27 cables, added in Rev09of cable schedule. |  | No | No
PS5-63-01 - Electrical Earthing | 1 | 23% | 0 | 40 | 0 |  | 18 ITRs for lightning, 22 ITRs for grounding cannot be closed due to material issues. | Yes | Yes
PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room | 1 | 21% | 0 | 0 | 24 | 3 manual call point not arrived yet PS5-03-RMAC-1409~1411 8 Smake detectors not arrived yet PS5-03-RDOS-1401~1408 11 cables for RMAC/RDOS not arrived yet 1P X 1.0 OS FR 275m cable PS5-60-SEA-0001-CC02 6P X 0.75 OS FL |  | Yes | Yes
PS5-71-06 - Crude Fuel Separation Module | 1.1 | 43% | 0 | 0 | 22 | PS5-71-BI-0001A-CC01 12P X 0.75 OS FL RTD 20m PS5-71-BI-0001B-CC01 12P X 0.75 OS FL RTD 20m PS5-71-BI-0008B-CC01 12P X 0.75 IS/OS FL RTD 170 PS5-71-BI-0008B-CC02 12P X 0.75 IS/OS FL RTD 170 PS5-71-BI-0011A-CC01 6T X 2.5 OS FL RTD 20 PS5-71-BI-0011A-CC02 6T X 2.5 OS FL RTD 20 PS5-71-BI-0011A-CC03 6P X 0.75 OS FL RTD 20 PS5-71-BI-0011A-CC05 6T X 2.5 OS FL RTD 20 PS5-71-BI-0011B-CC01 6T X 2.5 OS FL RTD 20 PS5-71-BI-0011B-CC02 6T X 2.5 OS FL RTD 20 PS5-71-BI-0011B-CC05 6T X 2.5 OS FL RTD 20 |  | No | No
PS5-61-04 - 0.4kV Switchboard Office & Facilities Building (PS5-61-IK-0005) | 1 | 0% | 0 | 18 | 0 |  | all the cables cannot be laid due to pending excavation to office/building area. | No | No
PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | 1 | 37% | 0 | 0 | 16 | Cannot terminate the cables due to busbar panel issues and cannot close the static/conformity ITRs of the panel. |  | Yes | Yes
PS5-01-11 - Inergen for Power Gen Building | 1.1 | 3% | 0 | 0 | 14 | PS5-01-BI-0007-CC01 6P X 0.75 IS/OS FR 65 PS5-01-BI-0008-CC01 6P X 0.75 IS/OS FR 65 PS5-01-BI-0009-CC01 24P X 0.75 OS FR 65 PS5-01-LB-6101A-CC01 6P X 0.75 OS FR 35 PS5-01-LB-6102A-CC01 6P X 0.75 OS FR 35 PS5-01-LB-6103A-CC01 6P X 0.75 OS FR 35 PS5-01-LB-6104A-CC01 6P X 0.75 OS FR 35 |  | Yes | Yes
PS5-71-19 - Diesel Separator Module (UCP) | 1 | 29% | 0 | 0 | 8 | PS5-71-BE-0005-CL01 4C+E 16 210m , PS5-71-BE-0005-CL02 2C+E 2.5 210m , PS5-71-BE-0005-CL03 4C+E 6 210m PS5-71-BE-0005-CL04 2C+E 2.5 210m. These cables were added in latest revision, not available. |  | Yes | Yes
PS5-03-15 - FZ-15 - Power Generation Building - Generator Room 1 | 1 | 0% | 0 | 0 | 6 | PS5-03-RDOS-1501/1502/1503 not arrived |  | Yes | Yes
PS5-03-16 - FZ-16 - Power Generation Building - Generator Room 2 | 1.1 | 0% | 0 | 0 | 6 | PS5-03-RDOS-1601/1602/1603 not arrived yet |  | Yes | Yes
PS5-03-19 - FZ-19 - Power Generation Building - Battery Room | 1 | 0% | 0 | 0 | 6 | PS5-03-RDH-1901/1902/1903 not arrived |  | Yes | Yes
PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs | 1 | 49% | 0 | 3 | 3 | CPP will execute the job as per SI for telecom , waiting material from CPY | M40/M20 Reducer not available,Grounding cable missing 1x240mm2 | Yes | Yes
PS5-60-22 - Power Gen Master UCP | 1 | 43% | 0 | 0 | 6 | CPP will execute the job as per SI for telecom , waiting material from CPY |  | Yes | Yes
PS5-71-20 - Diesel Fuel Day Tank | 1 | 69% | 0 | 0 | 6 | 6 ITRS pending due to LIT 1201/1202 (not arrived yet) |  | Yes | Yes
PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs | 1 | 48% | 0 | 2 | 3 | CPP will execute the job as per SI for telecom , waiting material from CPY | 1x240mm2 cable not available.CPP Supply | Yes | Yes
PS5-71-21 - Diesel Transfer Pump A/B | 1 | 66% | 0 | 2 | 3 | PS5-71-21-0331 - Test Package - CPP Item Nipple and 1/2 Flange not available at site. CPY/EPS Supply Item PS5-71-FIT-0019 – SRN-01997, awaiting collection from vendor by MLC (airfreight). PS5-71-FIT-0019 not arrived. | 2 PDG tubing cannot be completed due to tubing clamps. | Yes | Yes
PS5-28-04 - Closed Drain Drum and Pump 02 | 1.1 | 38% | 0 | 0 | 4 | PS5-28-TW-1401/1402 not available |  | Yes | Yes
PS5-60-05 - Power Gen Package B (UCP) | 1 | 71% | 0 | 0 | 4 | CPP will execute the job as per SI for telecom , waiting material from CPY |  | Yes | Yes
PS5-60-10 - Power Generation Package D | 1.1 | 57% | 0 | 2 | 2 | Transformer top up oil to be completed PS5-60-BI-0016D-CCO4 6T X 0.75 IS/OS FL RTD 121m |  | Yes | Yes
PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) | 1 | 63% | 0 | 0 | 4 | PS5-61-IV-0005A/5B Not arrived. |  | Yes | Yes
PS5-71-18 - Diesel Separator Module | 1 | 46% | 0 | 0 | 4 | PS5-71-BI-0002-CC01, 155m ,Cable type:12P X 0.75 OS FL RTD PS5-71-BI-0009-CC01, 175m, Cable type:6T X 2.5 IS/OS FR |  | Yes | Yes
PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP) | 1 | 51% | 0 | 0 | 4 | CPP will execute the job as per SI for telecom , waiting material from CPY PS5-71-BI-0005-CC01 12P X 0.75 OS FL RTD cable not available PS5-71-BI-0005-CC02 Engineering Issue |  | Yes | Yes
PS5-09-05 - HVAC for EITS Building | 1 | 94% | 0 | 0 | 3 | HVAC METERIAL ARIVED-17-08-26 |  | Yes | Yes
PS5-60-24 - Cooling Water Tank & Pump | 1 | 75% | 0 | 0 | 3 | PS5-60-LIT-4301 not arrived. |  | Yes | Yes
PS5-60-25 - Cooling Water Maintenance Tank & Return Pump | 1 | 74% | 0 | 0 | 3 | PS5-60-LIT-4401 not arrived |  | Yes | Yes
PS5-60-57 - Fuel Conditioning Module PS5-60-UZ-8900A (UCP) | 1 | 73% | 0 | 2 | 1 | CPP will execute the job as per SI for telecom , waiting material from CPY | 1x25mm2 cable not available.CPP Supply | Yes | Yes
PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP) | 1 | 73% | 0 | 2 | 1 | CPP will execute the job as per SI for telecom , waiting material from CPY | 1x25mm2 cable not available.CPP Supply | Yes | Yes
PS5-60-61 - Fuel Conditioning Module PS5-60-UZ-8900C (UCP) | 1.1 | 61% | 0 | 2 | 1 | CPP will execute the job as per SI for telecom , waiting material from CPY | PS5-60-IN-0002C-CG01 1X25mm2 grounding cable 130m | Yes | Yes
PS5-60-63 - Fuel Conditioning Module PS5-60-UZ-8900D (UCP) | 1.1 | 32% | 0 | 2 | 1 | CPP will execute the job as per SI for telecom , waiting material from CPY | PS5-60-IN-0002D-CG01 1x25mm2 grounding cable 120m | Yes | Yes
PS5-71-08 - CFO Pre-Pressure Modules | 1.1 | 58% | 0 | 0 | 3 | PS5-71-BI-0003-CC04 6P X 0.75 OS FL RTD 20m PS5-71-BI-0003-CC01 engineering issue. |  | No | No
PS5-60-01 - Power Generation Package A | 1 | 76% | 0 | 2 | 0 |  | Transformer top up oil to be completed | Yes | Yes
PS5-60-07 - Power Generation Package C | 1.1 | 59% | 0 | 0 | 2 | PS5-60-BI-0016C-CCO4 6T X 0.75 IS/OS FL RTD 131m |  | Yes | Yes
PS5-60-08 - Power Gen Package C (UCP) | 1.1 | 34% | 0 | 0 | 2 | PS5-60-IE-0003C-CC05 6P X 0.75 IS/OS FL RTD 115m. |  | Yes | Yes
PS5-60-09 - Power Gen Package C Generator Auxiliary MCCs & DBs | 1.1 | 31% | 0 | 2 | 0 | CPP WILL EXECUTE THE JOB AS PER SI FOR TELECOM,WAITING METERIAL FROM CPY | PS5-60-IH-0001C-CG01 1x240mm2 grounding cable 40m | Yes | Yes
PS5-60-11 - Power Gen Package D (UCP) | 1.1 | 34% | 0 | 0 | 2 | PS5-60-IE-0003D-CC11 12P X 0.75 OS FL RTD 50m |  | Yes | Yes
PS5-60-12 - Power Gen Package D Generator Auxiliary MCCs & DBs | 1.1 | 48% | 0 | 2 | 0 | CPP WILL EXECUTE THE JOB AS PER SI FOR TELECOM,WAITING METERIAL FROM CPY | PS5-60-IH-0001D-CG01 1x240mm2 grounding cable, 35m | Yes | Yes
PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A | 1 | 82% | 0 | 0 | 2 | Cables pending due to PIT location issue, colliding with pipes |  | Yes | Yes
PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B | 1 | 86% | 0 | 0 | 2 | Cables pending due to PIT location issue, colliding with pipes |  | Yes | Yes
PS5-63-03 - Electrical Earthing - Generator Building | 1 | 40% | 0 | 2 | 0 |  | lightning cannot be completed due to materials | Yes | Yes
PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A | 1 | 75% | 0 | 0 | 1 | CPP will execute the job as per SI for telecom , waiting material from CPY |  | Yes | Yes
PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B | 1 | 75% | 0 | 0 | 1 | CPP will execute the job as per SI for telecom , waiting material from CPY |  | Yes | Yes
PS5-01-01 - Fire Water Jockey Pump A/B | 1.1 | 30% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-01-02 - Fire Water Pump A | 1.1 | 43% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-01-03 - Fire Water Pump B | 1.1 | 41% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-01-04 - Fire Water Pump Mini Flow Recycle | 1.1 | 30% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-01-05 - Foam Skid | 2 | 23% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-01-06 - Foam Concentrate Distribution | 2 | 50% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-01-07 - Fire Water Ring Main & Distribution | 2 | 41% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100) | 2 | 29% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-01-09 - Inergen for EITS Building | 1 | 100% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-01-10 - Water Mist Package | 1.1 | 34% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-02-01 - Miscellaneous Safety equipment | 3 | 11% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-02-02 - Portable Fire Fighting Equipments | 3 | 8% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-03-01 - FZ-01 - Process Area | 2 | 18% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-03-03 - FZ-03 - Buildings Area | 5 | 4% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-03-04 - FZ-04 - Utilities - Diesel and Firewater Pumps Areas | 1.1 | 25% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-03-06 - FZ-06 - Transformer Area | 2 | 17% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-03-07 - FZ-07 - Pretreatment Area | 2 | 3% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-03-08 - FZ-08 - Utilities - Power Generation Area - External | 2 | 12% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-03-09 - FZ-09 - Power Generation Building - Engine Bay 1 | 1 | 41% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-03-10 - FZ-10 - Power Generation Building - Engine Bay 2 | 1.1 | 12% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-03-11 - FZ-11 - Power Generation Building - Engine Bay 3 | 2 | 2% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-03-12 - FZ-12 - Power Generation Building - Engine Bay 4 | 2 | 4% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-03-13 - FZ-13 - Power Generation Building - Instrument Air Room | 1.1 | 0% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-03-17 - FZ-17 - Power Generation Building - Generator Room 3 | 2 | 0% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-03-18 - FZ-18 - Power Generation Building - Generator Room 4 | 2 | 0% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure | 1 | 82% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-03-21 - FZ-21 - Power Generation Building - Air Handling Unit | 3 | 0% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-03-22 - FZ-G1 - Guard House | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-03-23 - FZ-E1 to E3 - EITS Building |  | 99% | 0 | 0 | 0
PS5-03-24 - FZ - Office and Facilities Building | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-03-25 - FZ - Workshop & Warehouse | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-04-01 - Office Building PCS System |  | 0% | 0 | 0 | 0
PS5-04-02 - Office Building SIS/FGS System | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-04-03 - 33kV ICSS System |  | 93% | 0 | 0 | 0
PS5-04-04 - 33kV PCS System |  | 95% | 0 | 0 | 0
PS5-04-05 - 33kV SIS/FGS System |  | 88% | 0 | 0 | 0
PS5-05-01 - Emergency Diesel Generator Package | 1 | 88% | 0 | 0 | 0 | WALDOWN COMPLETED ON 17-08-2026 | 1 ELECTRICAL ITR BALANCE | Yes | Yes
PS5-05-02 - Emergency Diesel Generator Package (UCP) | 1 | 86% | 0 | 0 | 0 | WALKDOWN COMPLETED ON 17-08-2026 |  | Yes | Yes
PS5-06-01 - AC UPS - EITS Building |  | 70% | 0 | 0 | 0
PS5-06-02 - AC UPS - Power Generator Building | 1 | 72% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-06-03 - AC UPS - Office & Facilities Building | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-06-04 - AC UPS - Guard House | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-06-05 - AC UPS - Workshop & Warehouse | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-08-01 - PAGA | 3 | 8% | 0 | 0 | 0 |  |  | Partially | Partially
PS5-08-03 - Telephone | 4 | 2% | 0 | 0 | 0 |  |  | No | No
PS5-08-04 - Hotline |  | 0% | 0 | 0 | 0
PS5-08-07 - Multi-Channel Voice Recorder |  | 0% | 0 | 0 | 0
PS5-08-11 - Corporate LAN (SIE) | 3 | 62% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-08-12 - Corporate Wireless LAN (SIE) | 3 | 4% | 0 | 0 | 0 |  |  | No | No
PS5-08-13 - Safety Data Network (SII SP3 SAF) | 3 | 70% | 0 | 0 | 0 |  |  | No | No
PS5-08-14 - Industrial Data Network (SII SP1) | 4 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-08-15 - Security Data Network (SII SP3 SEC) | 4 | 50% | 0 | 0 | 0 |  |  | No | No
PS5-08-23 - VHF Trunk Radio System | 4 | 12% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-08-34 - Satphone | 4 | 0% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-08-35 - Optical Transport Network |  | 80% | 0 | 0 | 0
PS5-08-36 - Pipeline FO Cable & EPRS | 3 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-08-51 - Entertainment | 4 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-08-52 - Process & Security CCTV | 4 | 10% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-08-55 - Videoconference |  | 0% | 0 | 0 | 0
PS5-08-61 - Meteocean | 4 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-08-71 - Structured Cabling (CAT6) | 4 | 9% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-08-72 - Structured Cabling (FO) | 3 | 25% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-08-81 - Guard tour |  | 0% | 0 | 0 | 0
PS5-08-82 - Key Management |  | 0% | 0 | 0 | 0
PS5-08-83 - Perimeter & Pipeline intrusion detection system | 4 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-08-85 - Access Control, POB & e-Mustering | 4 | 12% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-08-86 - Integrated Security Management System |  | 0% | 0 | 0 | 0
PS5-08-92 - Telecom Mast |  | 0% | 0 | 0 | 0
PS5-08-93 - Telecom Monitoring System | 4 | 33% | 0 | 0 | 0 |  |  | No | No
PS5-09-01 - HVAC for Office and Facilities building | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-09-02 - HVAC for Guard House | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-09-03 - HVAC for Generator Building | 2 | 2% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-09-04 - HVAC for Workshop & Warehouse | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-0H-01 - HIPPS |  | 71% | 0 | 0 | 0
PS5-25-01 - Export Pipeline Pig Receiver | 3 | 35% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-25-02 - Crude Oil Export Pump A | 3 | 37% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-25-03 - Crude Oil Export Pump B | 3 | 34% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-25-04 - Crude Oil Export Pump C | 3 | 33% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-25-05 - Crude Oil Export Pumps Bypass | 3 | 28% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-25-06 - Crude Oil Export Pumps Discharge | 3 | 29% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-25-07 - Export Pipeline Pig Launcher | 3 | 30% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-28-01 - Closed Drain Header 1 | 3 | 47% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-28-02 - Closed Drain Header 2 | 1.1 | 40% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-28-03 - Closed Drain Drum and Pump 01 | 3 | 42% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-28-05 - HP Relief Header | 2 | 24% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-28-06 - Relief Drum and Pump | 2 | 40% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-28-07 - Open Drains (OD2) | 3 | 61% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-28-08 - Open Drain Sump and Pumps | 2 | 26% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-28-09 - Observation Basin | 3 | 60% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-28-10 - Oil Skimmer Package | 3 | 5% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-28-11 - Open Drain Interceptor | 3 | 25% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-28-12 - Open Drains (OD3) | 3 | 61% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-28-13 - Seal Oil Drain Drum & Pump A | 3 | 33% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-28-14 - Seal Oil Drain Drum & Pump B | 3 | 33% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-28-15 - Seal Oil Drain Drum & Pump C | 3 | 33% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-28-16 - LP Relief Header | 2 | 29% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-28-17 - Reinjection Pump | 2 | 30% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-50-01 - Water Well Submersible Pumps (3100) | 4 | 24% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-50-02 - Water Well Submersible Pumps (3200) | 4 | 24% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-50-03 - Water Pre-Treatment Package | 2 | 23% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-53-01 - Utility Water / Storage Tank | 2 | 41% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-53-02 - Water Distribution Pump A/B | 2 | 23% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-53-03 - Water Softener Package | 2 | 19% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-53-04 - Water Treatment Purification Package | 2 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-53-05 - Water Distribution Header | 2 | 66% | 0 | 0 | 0 |  |  | No | No
PS5-53-06 - Water Distribution Consumers | 4 | 62% | 0 | 0 | 0 |  |  | No | No
PS5-60-02 - Power Gen Package A (UCP) | 1 | 78% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-04 - Power Generation Package B | 1 | 77% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-13 - Power Generation Package E | 2 | 42% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-14 - Power Gen Package E (UCP) | 2 | 21% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-15 - Power Gen Package E Generator Auxiliary MCCs & DBs | 2 | 29% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-16 - Power Generation Package F | 2 | 41% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-17 - Power Gen Package F (UCP) | 2 | 27% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-18 - Power Gen Package F Generator Auxiliary MCCs & DBs | 2 | 15% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-19 - Power Generation Package G | 2 | 40% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-20 - Power Gen Package G (UCP) | 2 | 25% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-21 - Power Gen Package G Generator Auxiliary MCCs & DBs | 2 | 20% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-23 - Instrument Air Distribution lines | 1 | 64% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-26 - Instrument Air Compressor Skid | 1 | 65% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-27 - Compressed Air Starting Skid | 1 | 60% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-28 - Air Receiver A & Air Regulator A | 1 | 71% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-29 - Air Receiver B & Air Regulator B | 1 | 71% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-30 - Air Receiver C & Air Regulator C | 1.1 | 71% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-31 - Air Receiver D & Air Regulator D | 1.1 | 71% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-32 - Air Receiver E & Air Regulator E | 2 | 35% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-33 - Air Receiver F & Air Regulator F | 2 | 35% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-34 - Air Receiver G & Air Regulator G | 2 | 41% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-35 - Injector Tip Cooling Module A | 1 | 72% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-36 - Injector Tip Cooling Module B | 1 | 81% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-37 - Injector Tip Cooling Module C | 1.1 | 70% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-38 - Injector Tip Cooling Module D | 1.1 | 70% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-39 - Injector Tip Cooling Module E | 2 | 50% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-40 - Injector Tip Cooling Module F | 2 | 49% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-41 - Injector Tip Cooling Module G | 2 | 44% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A | 1 | 83% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B | 1 | 85% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C | 1.1 | 71% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D | 1.1 | 71% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-46 - Oil Mist Separator Skid PS5-60-VS-9100E | 2 | 59% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-47 - Oil Mist Separator Skid PS5-60-VS-9100F | 2 | 59% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-48 - Oil Mist Separator Skid PS5-60-VS-9100G | 2 | 56% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C | 1.1 | 57% | 0 | 0 | 0 | Cables pending due to PIT location issue, colliding with pipes |  | Yes | Yes
PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D | 1.1 | 57% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-53 - Lube Oil Separator Module PS5-60-UO-81100E | 2 | 48% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-54 - Lube Oil Separator Module PS5-60-UO-81100F | 2 | 48% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-55 - Lube Oil Separator Module PS5-60-UO-81100G | 2 | 41% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C | 1.1 | 52% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D | 1.1 | 52% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E | 2 | 41% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-65 - Fuel Conditioning Module PS5-60-UZ-8900E (UCP) | 2 | 22% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F | 2 | 37% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-67 - Fuel Conditioning Module PS5-60-UZ-8900F (UCP) | 2 | 22% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G | 2 | 33% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-69 - Fuel Conditioning Module PS5-60-UZ-8900G (UCP) | 2 | 22% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-70 - Engine A Cooling system | 1 | 77% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-71 - Engine B Cooling system | 1 | 88% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-72 - Engine C Cooling system | 1.1 | 74% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-73 - Engine D Cooling system | 1.1 | 74% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-74 - Engine E Cooling system | 2 | 60% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-75 - Engine F Cooling system | 2 | 59% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-60-76 - Engine G Cooling system | 2 | 41% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010) | 3 | 41% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) | 3 | 38% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | 1 | 74% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) | 2 | 76% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-61-08 - Electrical Control System | 2 | 66% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-61-09 - Outdoor Power Distribution Board - PS5-61-IG-0014 | 2 | 3% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-61-10 - Outdoor Valves Distribution Board - PS5-61-IG-0042 | 2 | 7% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-61-11 - Outdoor Valves Distribution Board - PS5-61-IG-0043 | 1.1 | 7% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-61-12 - EITS 33kV Bld. Normal Auxiliary DP - PS5-61-IG-0008 |  | 32% | 0 | 0 | 0
PS5-61-13 - Power Distribution Board Office Building - PS5-61-IG-0020 | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-61-14 - Power Distribution Board Workshop & Warehouse - PS5-61-IG-0009 | 4 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-62-01 - Lighting Control Panel - PS5-62-IE-0001 | 2 | 4% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-62-02 - Lighting Control Panel - PS5-62-IE-0002 | 2 | 3% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-62-03 - Outdoor Emergency Lighting DB - PS5-05-IG-0004 | 2 | 7% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-62-04 - Outdoor Emergency Lighting DB - PS5-05-IG-0006 | 2 | 4% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-62-05 - Guard House Emergency L&SP DB - PS5-05-IG-0007 | 4 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-62-06 - CRO Generator Building Emergency Lighting DB - PS5-05-IG-0025 | 1.1 | 3% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-62-07 - CRO Generator Electrical Building Emergency Lighting DB - PS5-05-IG-0026 | 1.1 | 6% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-62-08 - Outdoor Normal Lighting DB - PS5-61-IG-0006 | 2 | 2% | 0 | 0 | 0 |  |  | No | No
PS5-62-09 - Outdoor Normal Lighting DB - PS5-61-IG-0007 | 2 | 25% | 0 | 0 | 0 |  |  | No | No
PS5-62-10 - CRO Generator Building Normal L&SP DB - PS5-61-IG-0015 | 1.1 | 1% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-62-11 - CRO Generator Electrical Building Normal L&SP DB - PS5-61-IG-0016 | 1.1 | 3% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-62-12 - EITS 33kV Bld. Emergency L&SP DP - PS5-05-IG-0003 |  | 73% | 0 | 0 | 0
PS5-62-13 - EITS 33kV Bld. Normal L&SP DP - PS5-61-IG-0003 |  | 74% | 0 | 0 | 0
PS5-62-14 - Office Building Emergency L&SP DB - PS5-05-IG-0002 | 5 | 3% | 0 | 0 | 0 |  |  | No | No
PS5-62-15 - Office Building Normal L&SP DB - PS5-61-IG-0002 | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-62-16 - Guard Hut A Normal L&SP DB - PS5-61-IG-0111 | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-62-17 - Guard Hut B Normal L&SP DB - PS5-61-IG-0112 | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-62-18 - Workshop & Warehouse Normal L&SP DB - PS5-61-IG-0004 | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-62-19 - Workshop & Warehouse Emergency L&SP DB - PS5-05-IG-0101 | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-62-20 - Office Building Normal L&SP DB - PS5-61-IG-0010 | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-63-02 - Electrical Earthing - Office and Facilities building | 4 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-63-04 - Electrical Earthing - EITS Building |  | 100% | 0 | 0 | 0
PS5-63-05 - Electrical Earthing - Guard Hut A & B | 4 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-63-06 - Electrical Earthing - Guard House | 4 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-63-07 - Electrical Earthing - Workshop & Warehouse | 4 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-71-01 - CFO Storage Tank Feed Heater | 2 | 35% | 0 | 0 | 0 |  |  | No | No
PS5-71-02 - CFO Allocation Metering Package | 2 | 26% | 0 | 0 | 0 |  |  | No | No
PS5-71-03 - CFO Allocation Metering Package (UCP) |  | 47% | 0 | 0 | 0
PS5-71-04 - CFO Storage Tank | 2 | 32% | 0 | 0 | 0 |  |  | No | No
PS5-71-05 - CFO Transfer Pump A/B | 2 | 26% | 0 | 0 | 0 |  |  | No | No
PS5-71-09 - CFO Pre-Pressure Modules (UCP) | 1.1 | 58% | 0 | 0 | 0 |  |  | No | No
PS5-71-12 - CFO Service Tank | 2 | 32% | 0 | 0 | 0 |  |  | No | No
PS5-71-13 - CFO Service Pump A/B | 2 | 26% | 0 | 0 | 0 |  |  | No | No
PS5-71-14 - Diesel Fuel Transfer and Dispensing Station | 2 | 29% | 0 | 0 | 0 |  |  | No | No
PS5-71-15 - Diesel Fuel Storage Tank | 2 | 40% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-71-16 - Diesel Fuel Supply Pump A/B | 2 | 22% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-71-17 - Diesel Fuel Distribution Header | 2 | 41% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-71-22 - Diesel Fuel Pre Pressure Module | 1 | 72% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-74-01 - N2 Generation Skid | 2 | 17% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-74-02 - N2 Generation Skid (UCP) | 2 | 8% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-74-03 - Nitrogen Receiver | 2 | 37% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-74-04 - Nitrogen Distribution Header | 2 | 18% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-75-01 - DRA Injection Package | 3 | 10% | 0 | 0 | 0 |  |  | No | No
PS5-75-02 - Biocide Injection Package | 3 | 22% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-75-03 - Corrosion Inhibitor Injection Package | 3 | 20% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-78-01 - Lifting and handling equipment | 3 | 63% | 0 | 0 | 0 |  |  | Partially | Partially
PS5-79-01 - Electrical Heat Tracing Transformer/Distribution Board 1 (PS5-79-IG-0001) | 3 | 3% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-79-02 - Electrical Heat Tracing Transformer/Distribution Board 2 (PS5-79-IG-0002) | 3 | 3% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-79-03 - Electrical Heat Tracing Transformer/Distribution Board 3 (PS5-79-IG-0003) | 3 | 3% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-79-04 - Electrical Heat Tracing Transformer/Distribution Board 4 (PS5-79-IG-0004) | 3 | 3% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-79-05 - Electrical Heat Tracing Transformer/Distribution Board 5 (PS5-79-IG-0005) | 3 | 3% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-79-06 - Electrical Heat Tracing Transformer/Distribution Board 6 (PS5-79-IG-0006) | 3 | 3% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-79-07 - Electrical Heat Tracing Transformer/Distribution Board 7 (PS5-79-IG-0007) | 3 | 3% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-79-08 - Electrical Heat Tracing Transformer/Distribution Board 8 (PS5-79-IG-0008) | 3 | 3% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-79-09 - Electrical Heat Tracing Transformer/Distribution Board 9 (PS5-79-IG-0009) | 3 | 3% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-79-10 - Electrical Heat Tracing Transformer/Distribution Board 10 (PS5-79-IG-0010) | 3 | 3% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-79-11 - Electrical Heat Tracing Transformer/Distribution Board 11 (PS5-79-IG-0011) | 3 | 3% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-79-12 - Electrical Heat Tracing Transformer/Distribution Board 12 (PS5-79-IG-0012) | 3 | 1% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-82-01 - Sanitary Sewage Collection | 4 | 58% | 0 | 0 | 0 |  |  | No | No
PS5-82-02 - Sewage Treatment Plant Package | 4 | 6% | 0 | 0 | 0 |  |  | No | No
PS5-82-03 - Sewage Treatment Plant Package (UCP) | 4 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-82-04 - Sewage Treatment Plant Discharge Piping | 4 | 36% | 0 | 0 | 0 |  |  | No | No
PS5-82-05 - Office and Facilities building | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-82-06 - Guard House Building | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-82-07 - Guard Huts | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-83-01 - EITS Building | 2 | 64% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-84-01 - Generator Building | 2 | 0% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-84-02 - Workshop & Warehouse | 5 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-84-03 - Shelters | 4 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-86-01 - Shelters | 4 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-91-01 - Multicore cables & JB | 1 | 75% | 0 | 0 | 0 |  |  | Yes | Yes
PS5-99-01 - Area Completion for Building area | 4 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-99-02 - Area Completion for Utility area | 3 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-99-03 - Area Completion for Power Distribution area | 2 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-99-04 - Area Completion for Process area | 2 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-99-05 - Area Completion for CFO area | 2 | 0% | 0 | 0 | 0 |  |  | No | No
PS5-99-06 - Area Completion for Power Generation area | 2 | 0% | 0 | 0 | 0 |  |  | No | No

## SIDMAP (hidden)
PS5-01-01 - Fire Water Jockey Pump A/B | PS5-01-01
PS5-01-02 - Fire Water Pump A | PS5-01-02
PS5-01-03 - Fire Water Pump B | PS5-01-03
PS5-01-04 - Fire Water Pump Mini Flow Recycle | PS5-01-04
PS5-01-05 - Foam Skid | PS5-01-05
PS5-01-06 - Foam Concentrate Distribution | PS5-01-06
PS5-01-07 - Fire Water Ring Main & Distribution | PS5-01-07
PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100) | PS5-01-08
PS5-01-09 - Inergen for EITS Building | PS5-01-09
PS5-01-10 - Water Mist Package | PS5-01-10
PS5-01-11 - Inergen for Power Gen Building | PS5-01-11
PS5-02-01 - Miscellaneous Safety equipment | PS5-02-01
PS5-02-02 - Portable Fire Fighting Equipments | PS5-02-02
PS5-03-01 - FZ-01 - Process Area | PS5-03-01
PS5-03-03 - FZ-03 - Buildings Area | PS5-03-03
PS5-03-04 - FZ-04 - Utilities - Diesel and Firewater Pumps Areas | PS5-03-04
PS5-03-06 - FZ-06 - Transformer Area | PS5-03-06
PS5-03-07 - FZ-07 - Pretreatment Area | PS5-03-07
PS5-03-08 - FZ-08 - Utilities - Power Generation Area - External | PS5-03-08
PS5-03-09 - FZ-09 - Power Generation Building - Engine Bay 1 | PS5-03-09
PS5-03-10 - FZ-10 - Power Generation Building - Engine Bay 2 | PS5-03-10
PS5-03-11 - FZ-11 - Power Generation Building - Engine Bay 3 | PS5-03-11
PS5-03-12 - FZ-12 - Power Generation Building - Engine Bay 4 | PS5-03-12
PS5-03-13 - FZ-13 - Power Generation Building - Instrument Air Room | PS5-03-13
PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room | PS5-03-14
PS5-03-15 - FZ-15 - Power Generation Building - Generator Room 1 | PS5-03-15
PS5-03-16 - FZ-16 - Power Generation Building - Generator Room 2 | PS5-03-16
PS5-03-17 - FZ-17 - Power Generation Building - Generator Room 3 | PS5-03-17
PS5-03-18 - FZ-18 - Power Generation Building - Generator Room 4 | PS5-03-18
PS5-03-19 - FZ-19 - Power Generation Building - Battery Room | PS5-03-19
PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure | PS5-03-20
PS5-03-21 - FZ-21 - Power Generation Building - Air Handling Unit | PS5-03-21
PS5-03-22 - FZ-G1 - Guard House | PS5-03-22
PS5-03-23 - FZ-E1 to E3 - EITS Building | PS5-03-23
PS5-03-24 - FZ - Office and Facilities Building | PS5-03-24
PS5-03-25 - FZ - Workshop & Warehouse | PS5-03-25
PS5-04-01 - Office Building PCS System | PS5-04-01
PS5-04-02 - Office Building SIS/FGS System | PS5-04-02
PS5-04-03 - 33kV ICSS System | PS5-04-03
PS5-04-04 - 33kV PCS System | PS5-04-04
PS5-04-05 - 33kV SIS/FGS System | PS5-04-05
PS5-05-01 - Emergency Diesel Generator Package | PS5-05-01
PS5-05-02 - Emergency Diesel Generator Package (UCP) | PS5-05-02
PS5-06-01 - AC UPS - EITS Building | PS5-06-01
PS5-06-02 - AC UPS - Power Generator Building | PS5-06-02
PS5-06-03 - AC UPS - Office & Facilities Building | PS5-06-03
PS5-06-04 - AC UPS - Guard House | PS5-06-04
PS5-06-05 - AC UPS - Workshop & Warehouse | PS5-06-05
PS5-08-01 - PAGA | PS5-08-01
PS5-08-03 - Telephone | PS5-08-03
PS5-08-04 - Hotline | PS5-08-04
PS5-08-07 - Multi-Channel Voice Recorder | PS5-08-07
PS5-08-11 - Corporate LAN (SIE) | PS5-08-11
PS5-08-12 - Corporate Wireless LAN (SIE) | PS5-08-12
PS5-08-13 - Safety Data Network (SII SP3 SAF) | PS5-08-13
PS5-08-14 - Industrial Data Network (SII SP1) | PS5-08-14
PS5-08-15 - Security Data Network (SII SP3 SEC) | PS5-08-15
PS5-08-23 - VHF Trunk Radio System | PS5-08-23
PS5-08-34 - Satphone | PS5-08-34
PS5-08-35 - Optical Transport Network | PS5-08-35
PS5-08-36 - Pipeline FO Cable & EPRS | PS5-08-36
PS5-08-51 - Entertainment | PS5-08-51
PS5-08-52 - Process & Security CCTV | PS5-08-52
PS5-08-55 - Videoconference | PS5-08-55
PS5-08-61 - Meteocean | PS5-08-61
PS5-08-71 - Structured Cabling (CAT6) | PS5-08-71
PS5-08-72 - Structured Cabling (FO) | PS5-08-72
PS5-08-81 - Guard tour | PS5-08-81
PS5-08-82 - Key Management | PS5-08-82
PS5-08-83 - Perimeter & Pipeline intrusion detection system | PS5-08-83
PS5-08-85 - Access Control, POB & e-Mustering | PS5-08-85
PS5-08-86 - Integrated Security Management System | PS5-08-86
PS5-08-92 - Telecom Mast | PS5-08-92
PS5-08-93 - Telecom Monitoring System | PS5-08-93
PS5-09-01 - HVAC for Office and Facilities building | PS5-09-01
PS5-09-02 - HVAC for Guard House | PS5-09-02
PS5-09-03 - HVAC for Generator Building | PS5-09-03
PS5-09-04 - HVAC for Workshop & Warehouse | PS5-09-04
PS5-09-05 - HVAC for EITS Building | PS5-09-05
PS5-0H-01 - HIPPS | PS5-0H-01
PS5-25-01 - Export Pipeline Pig Receiver | PS5-25-01
PS5-25-02 - Crude Oil Export Pump A | PS5-25-02
PS5-25-03 - Crude Oil Export Pump B | PS5-25-03
PS5-25-04 - Crude Oil Export Pump C | PS5-25-04
PS5-25-05 - Crude Oil Export Pumps Bypass | PS5-25-05
PS5-25-06 - Crude Oil Export Pumps Discharge | PS5-25-06
PS5-25-07 - Export Pipeline Pig Launcher | PS5-25-07
PS5-28-01 - Closed Drain Header 1 | PS5-28-01
PS5-28-02 - Closed Drain Header 2 | PS5-28-02
PS5-28-03 - Closed Drain Drum and Pump 01 | PS5-28-03
PS5-28-04 - Closed Drain Drum and Pump 02 | PS5-28-04
PS5-28-05 - HP Relief Header | PS5-28-05
PS5-28-06 - Relief Drum and Pump | PS5-28-06
PS5-28-07 - Open Drains (OD2) | PS5-28-07
PS5-28-08 - Open Drain Sump and Pumps | PS5-28-08
PS5-28-09 - Observation Basin | PS5-28-09
PS5-28-10 - Oil Skimmer Package | PS5-28-10
PS5-28-11 - Open Drain Interceptor | PS5-28-11
PS5-28-12 - Open Drains (OD3) | PS5-28-12
PS5-28-13 - Seal Oil Drain Drum & Pump A | PS5-28-13
PS5-28-14 - Seal Oil Drain Drum & Pump B | PS5-28-14
PS5-28-15 - Seal Oil Drain Drum & Pump C | PS5-28-15
PS5-28-16 - LP Relief Header | PS5-28-16
PS5-28-17 - Reinjection Pump | PS5-28-17
PS5-50-01 - Water Well Submersible Pumps (3100) | PS5-50-01
PS5-50-02 - Water Well Submersible Pumps (3200) | PS5-50-02
PS5-50-03 - Water Pre-Treatment Package | PS5-50-03
PS5-53-01 - Utility Water / Storage Tank | PS5-53-01
PS5-53-02 - Water Distribution Pump A/B | PS5-53-02
PS5-53-03 - Water Softener Package | PS5-53-03
PS5-53-04 - Water Treatment Purification Package | PS5-53-04
PS5-53-05 - Water Distribution Header | PS5-53-05
PS5-53-06 - Water Distribution Consumers | PS5-53-06
PS5-60-01 - Power Generation Package A | PS5-60-01
PS5-60-02 - Power Gen Package A (UCP) | PS5-60-02
PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs | PS5-60-03
PS5-60-04 - Power Generation Package B | PS5-60-04
PS5-60-05 - Power Gen Package B (UCP) | PS5-60-05
PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs | PS5-60-06
PS5-60-07 - Power Generation Package C | PS5-60-07
PS5-60-08 - Power Gen Package C (UCP) | PS5-60-08
PS5-60-09 - Power Gen Package C Generator Auxiliary MCCs & DBs | PS5-60-09
PS5-60-10 - Power Generation Package D | PS5-60-10
PS5-60-11 - Power Gen Package D (UCP) | PS5-60-11
PS5-60-12 - Power Gen Package D Generator Auxiliary MCCs & DBs | PS5-60-12
PS5-60-13 - Power Generation Package E | PS5-60-13
PS5-60-14 - Power Gen Package E (UCP) | PS5-60-14
PS5-60-15 - Power Gen Package E Generator Auxiliary MCCs & DBs | PS5-60-15
PS5-60-16 - Power Generation Package F | PS5-60-16
PS5-60-17 - Power Gen Package F (UCP) | PS5-60-17
PS5-60-18 - Power Gen Package F Generator Auxiliary MCCs & DBs | PS5-60-18
PS5-60-19 - Power Generation Package G | PS5-60-19
PS5-60-20 - Power Gen Package G (UCP) | PS5-60-20
PS5-60-21 - Power Gen Package G Generator Auxiliary MCCs & DBs | PS5-60-21
PS5-60-22 - Power Gen Master UCP | PS5-60-22
PS5-60-23 - Instrument Air Distribution lines | PS5-60-23
PS5-60-24 - Cooling Water Tank & Pump | PS5-60-24
PS5-60-25 - Cooling Water Maintenance Tank & Return Pump | PS5-60-25
PS5-60-26 - Instrument Air Compressor Skid | PS5-60-26
PS5-60-27 - Compressed Air Starting Skid | PS5-60-27
PS5-60-28 - Air Receiver A & Air Regulator A | PS5-60-28
PS5-60-29 - Air Receiver B & Air Regulator B | PS5-60-29
PS5-60-30 - Air Receiver C & Air Regulator C | PS5-60-30
PS5-60-31 - Air Receiver D & Air Regulator D | PS5-60-31
PS5-60-32 - Air Receiver E & Air Regulator E | PS5-60-32
PS5-60-33 - Air Receiver F & Air Regulator F | PS5-60-33
PS5-60-34 - Air Receiver G & Air Regulator G | PS5-60-34
PS5-60-35 - Injector Tip Cooling Module A | PS5-60-35
PS5-60-36 - Injector Tip Cooling Module B | PS5-60-36
PS5-60-37 - Injector Tip Cooling Module C | PS5-60-37
PS5-60-38 - Injector Tip Cooling Module D | PS5-60-38
PS5-60-39 - Injector Tip Cooling Module E | PS5-60-39
PS5-60-40 - Injector Tip Cooling Module F | PS5-60-40
PS5-60-41 - Injector Tip Cooling Module G | PS5-60-41
PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A | PS5-60-42
PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B | PS5-60-43
PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C | PS5-60-44
PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D | PS5-60-45
PS5-60-46 - Oil Mist Separator Skid PS5-60-VS-9100E | PS5-60-46
PS5-60-47 - Oil Mist Separator Skid PS5-60-VS-9100F | PS5-60-47
PS5-60-48 - Oil Mist Separator Skid PS5-60-VS-9100G | PS5-60-48
PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A | PS5-60-49
PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B | PS5-60-50
PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C | PS5-60-51
PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D | PS5-60-52
PS5-60-53 - Lube Oil Separator Module PS5-60-UO-81100E | PS5-60-53
PS5-60-54 - Lube Oil Separator Module PS5-60-UO-81100F | PS5-60-54
PS5-60-55 - Lube Oil Separator Module PS5-60-UO-81100G | PS5-60-55
PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A | PS5-60-56
PS5-60-57 - Fuel Conditioning Module PS5-60-UZ-8900A (UCP) | PS5-60-57
PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B | PS5-60-58
PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP) | PS5-60-59
PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C | PS5-60-60
PS5-60-61 - Fuel Conditioning Module PS5-60-UZ-8900C (UCP) | PS5-60-61
PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D | PS5-60-62
PS5-60-63 - Fuel Conditioning Module PS5-60-UZ-8900D (UCP) | PS5-60-63
PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E | PS5-60-64
PS5-60-65 - Fuel Conditioning Module PS5-60-UZ-8900E (UCP) | PS5-60-65
PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F | PS5-60-66
PS5-60-67 - Fuel Conditioning Module PS5-60-UZ-8900F (UCP) | PS5-60-67
PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G | PS5-60-68
PS5-60-69 - Fuel Conditioning Module PS5-60-UZ-8900G (UCP) | PS5-60-69
PS5-60-70 - Engine A Cooling system | PS5-60-70
PS5-60-71 - Engine B Cooling system | PS5-60-71
PS5-60-72 - Engine C Cooling system | PS5-60-72
PS5-60-73 - Engine D Cooling system | PS5-60-73
PS5-60-74 - Engine E Cooling system | PS5-60-74
PS5-60-75 - Engine F Cooling system | PS5-60-75
PS5-60-76 - Engine G Cooling system | PS5-60-76
PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) | PS5-61-01
PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010) | PS5-61-02
PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) | PS5-61-03
PS5-61-04 - 0.4kV Switchboard Office & Facilities Building (PS5-61-IK-0005) | PS5-61-04
PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | PS5-61-05
PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | PS5-61-06
PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) | PS5-61-07
PS5-61-08 - Electrical Control System | PS5-61-08
PS5-61-09 - Outdoor Power Distribution Board - PS5-61-IG-0014 | PS5-61-09
PS5-61-10 - Outdoor Valves Distribution Board - PS5-61-IG-0042 | PS5-61-10
PS5-61-11 - Outdoor Valves Distribution Board - PS5-61-IG-0043 | PS5-61-11
PS5-61-12 - EITS 33kV Bld. Normal Auxiliary DP - PS5-61-IG-0008 | PS5-61-12
PS5-61-13 - Power Distribution Board Office Building - PS5-61-IG-0020 | PS5-61-13
PS5-61-14 - Power Distribution Board Workshop & Warehouse - PS5-61-IG-0009 | PS5-61-14
PS5-62-01 - Lighting Control Panel - PS5-62-IE-0001 | PS5-62-01
PS5-62-02 - Lighting Control Panel - PS5-62-IE-0002 | PS5-62-02
PS5-62-03 - Outdoor Emergency Lighting DB - PS5-05-IG-0004 | PS5-62-03
PS5-62-04 - Outdoor Emergency Lighting DB - PS5-05-IG-0006 | PS5-62-04
PS5-62-05 - Guard House Emergency L&SP DB - PS5-05-IG-0007 | PS5-62-05
PS5-62-06 - CRO Generator Building Emergency Lighting DB - PS5-05-IG-0025 | PS5-62-06
PS5-62-07 - CRO Generator Electrical Building Emergency Lighting DB - PS5-05-IG-0026 | PS5-62-07
PS5-62-08 - Outdoor Normal Lighting DB - PS5-61-IG-0006 | PS5-62-08
PS5-62-09 - Outdoor Normal Lighting DB - PS5-61-IG-0007 | PS5-62-09
PS5-62-10 - CRO Generator Building Normal L&SP DB - PS5-61-IG-0015 | PS5-62-10
PS5-62-11 - CRO Generator Electrical Building Normal L&SP DB - PS5-61-IG-0016 | PS5-62-11
PS5-62-12 - EITS 33kV Bld. Emergency L&SP DP - PS5-05-IG-0003 | PS5-62-12
PS5-62-13 - EITS 33kV Bld. Normal L&SP DP - PS5-61-IG-0003 | PS5-62-13
PS5-62-14 - Office Building Emergency L&SP DB - PS5-05-IG-0002 | PS5-62-14
PS5-62-15 - Office Building Normal L&SP DB - PS5-61-IG-0002 | PS5-62-15
PS5-62-16 - Guard Hut A Normal L&SP DB - PS5-61-IG-0111 | PS5-62-16
PS5-62-17 - Guard Hut B Normal L&SP DB - PS5-61-IG-0112 | PS5-62-17
PS5-62-18 - Workshop & Warehouse Normal L&SP DB - PS5-61-IG-0004 | PS5-62-18
PS5-62-19 - Workshop & Warehouse Emergency L&SP DB - PS5-05-IG-0101 | PS5-62-19
PS5-62-20 - Office Building Normal L&SP DB - PS5-61-IG-0010 | PS5-62-20
PS5-63-01 - Electrical Earthing | PS5-63-01
PS5-63-02 - Electrical Earthing - Office and Facilities building | PS5-63-02
PS5-63-03 - Electrical Earthing - Generator Building | PS5-63-03
PS5-63-04 - Electrical Earthing - EITS Building | PS5-63-04
PS5-63-05 - Electrical Earthing - Guard Hut A & B | PS5-63-05
PS5-63-06 - Electrical Earthing - Guard House | PS5-63-06
PS5-63-07 - Electrical Earthing - Workshop & Warehouse | PS5-63-07
PS5-71-01 - CFO Storage Tank Feed Heater | PS5-71-01
PS5-71-02 - CFO Allocation Metering Package | PS5-71-02
PS5-71-03 - CFO Allocation Metering Package (UCP) | PS5-71-03
PS5-71-04 - CFO Storage Tank | PS5-71-04
PS5-71-05 - CFO Transfer Pump A/B | PS5-71-05
PS5-71-06 - Crude Fuel Separation Module | PS5-71-06
PS5-71-07 - Crude Fuel Separation Module (UCP) | PS5-71-07
PS5-71-08 - CFO Pre-Pressure Modules | PS5-71-08
PS5-71-09 - CFO Pre-Pressure Modules (UCP) | PS5-71-09
PS5-71-12 - CFO Service Tank | PS5-71-12
PS5-71-13 - CFO Service Pump A/B | PS5-71-13
PS5-71-14 - Diesel Fuel Transfer and Dispensing Station | PS5-71-14
PS5-71-15 - Diesel Fuel Storage Tank | PS5-71-15
PS5-71-16 - Diesel Fuel Supply Pump A/B | PS5-71-16
PS5-71-17 - Diesel Fuel Distribution Header | PS5-71-17
PS5-71-18 - Diesel Separator Module | PS5-71-18
PS5-71-19 - Diesel Separator Module (UCP) | PS5-71-19
PS5-71-20 - Diesel Fuel Day Tank | PS5-71-20
PS5-71-21 - Diesel Transfer Pump A/B | PS5-71-21
PS5-71-22 - Diesel Fuel Pre Pressure Module | PS5-71-22
PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP) | PS5-71-23
PS5-74-01 - N2 Generation Skid | PS5-74-01
PS5-74-02 - N2 Generation Skid (UCP) | PS5-74-02
PS5-74-03 - Nitrogen Receiver | PS5-74-03
PS5-74-04 - Nitrogen Distribution Header | PS5-74-04
PS5-75-01 - DRA Injection Package | PS5-75-01
PS5-75-02 - Biocide Injection Package | PS5-75-02
PS5-75-03 - Corrosion Inhibitor Injection Package | PS5-75-03
PS5-78-01 - Lifting and handling equipment | PS5-78-01
PS5-79-01 - Electrical Heat Tracing Transformer/Distribution Board 1 (PS5-79-IG-0001) | PS5-79-01
PS5-79-02 - Electrical Heat Tracing Transformer/Distribution Board 2 (PS5-79-IG-0002) | PS5-79-02
PS5-79-03 - Electrical Heat Tracing Transformer/Distribution Board 3 (PS5-79-IG-0003) | PS5-79-03
PS5-79-04 - Electrical Heat Tracing Transformer/Distribution Board 4 (PS5-79-IG-0004) | PS5-79-04
PS5-79-05 - Electrical Heat Tracing Transformer/Distribution Board 5 (PS5-79-IG-0005) | PS5-79-05
PS5-79-06 - Electrical Heat Tracing Transformer/Distribution Board 6 (PS5-79-IG-0006) | PS5-79-06
PS5-79-07 - Electrical Heat Tracing Transformer/Distribution Board 7 (PS5-79-IG-0007) | PS5-79-07
PS5-79-08 - Electrical Heat Tracing Transformer/Distribution Board 8 (PS5-79-IG-0008) | PS5-79-08
PS5-79-09 - Electrical Heat Tracing Transformer/Distribution Board 9 (PS5-79-IG-0009) | PS5-79-09
PS5-79-10 - Electrical Heat Tracing Transformer/Distribution Board 10 (PS5-79-IG-0010) | PS5-79-10
PS5-79-11 - Electrical Heat Tracing Transformer/Distribution Board 11 (PS5-79-IG-0011) | PS5-79-11
PS5-79-12 - Electrical Heat Tracing Transformer/Distribution Board 12 (PS5-79-IG-0012) | PS5-79-12
PS5-82-01 - Sanitary Sewage Collection | PS5-82-01
PS5-82-02 - Sewage Treatment Plant Package | PS5-82-02
PS5-82-03 - Sewage Treatment Plant Package (UCP) | PS5-82-03
PS5-82-04 - Sewage Treatment Plant Discharge Piping | PS5-82-04
PS5-82-05 - Office and Facilities building | PS5-82-05
PS5-82-06 - Guard House Building | PS5-82-06
PS5-82-07 - Guard Huts | PS5-82-07
PS5-83-01 - EITS Building | PS5-83-01
PS5-84-01 - Generator Building | PS5-84-01
PS5-84-02 - Workshop & Warehouse | PS5-84-02
PS5-84-03 - Shelters | PS5-84-03
PS5-86-01 - Shelters | PS5-86-01
PS5-91-01 - Multicore cables & JB | PS5-91-01
PS5-99-01 - Area Completion for Building area | PS5-99-01
PS5-99-02 - Area Completion for Utility area | PS5-99-02
PS5-99-03 - Area Completion for Power Distribution area | PS5-99-03
PS5-99-04 - Area Completion for Process area | PS5-99-04
PS5-99-05 - Area Completion for CFO area | PS5-99-05
PS5-99-06 - Area Completion for Power Generation area | PS5-99-06