## Trace Heating Cables
Cable No. | Voltage Grade | Type | System Voltage | Cores | Size (mm²) | Volt Drop (V) | Volt Drop (%) | Length (m) | Tag No. | CB No. | North | East | Elevation | Description | Location | Gland Type | Entry Thread | Tag No. | North | East | Elevation | Description | Location | Gland Type | Entry Thread | Cable Routing Drawing | Outer Diameter (mm) | Remarks | Rev | DPS
PS5-79-IG-0001-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,12 | 0,03 | 5 | PS5-79-IV-0001 | - | 244467 | 270700 | 100000 | 63 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0001 | 244467 | 270700 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0002-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,16 | 0,04 | 5 | PS5-79-IV-0002 | - | 236950 | 270400 | 100000 | 100 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0002 | 236950 | 270400 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0003-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,16 | 0,04 | 5 | PS5-79-IV-0003 | - | 181573 | 278351 | 100000 | 63 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0003 | 181573 | 278351 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0004-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,12 | 0,03 | 5 | PS5-79-IV-0004 | - | 181572 | 283768 | 100001 | 63 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0004 | 181572 | 283768 | 100001 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0005-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,08 | 0,02 | 5 | PS5-79-IV-0005 | - | 181573 | 289184 | 100001 | 100 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0005 | 181573 | 289184 | 100001 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0006-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,28 | 0,07 | 5 | PS5-79-IV-0006 | - | 188771 | 235993 | 100000 | 63 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0006 | 188771 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0007-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,24 | 0,06 | 5 | PS5-79-IV-0007 | - | 183354 | 235993 | 100000 | 100 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0007 | 183354 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0008-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,28 | 0,07 | 5 | PS5-79-IV-0008 | - | 177937 | 235993 | 100000 | 100 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0008 | 177937 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0009-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,16 | 0,04 | 5 | PS5-79-IV-0009 | - | 188771 | 231193 | 100000 | 100 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0009 | 188771 | 231193 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0010-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,28 | 0,07 | 5 | PS5-79-IV-0010 | - | 183354 | 231193 | 100000 | 100 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0010 | 183354 | 231193 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0011-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,12 | 0,03 | 5 | PS5-79-IV-0011 | - | 187682 | 327500 | 100150 | 100 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0011 | 187682 | 327500 | 100150 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0012-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,2 | 0,05 | 5 | PS5-79-IV-0012 | - | 237233 | 138100 | 100000 | 100 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0012 | 237233 | 138100 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0001-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0001 | - | 244467 | 270700 | 100000 | 63 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0001 | 244467 | 270700 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0002-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0002 | - | 236950 | 270400 | 100000 | 100 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0002 | 236950 | 270400 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0003-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0003 | - | 181573 | 278351 | 100000 | 63 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0003 | 181573 | 278351 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0004-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0004 | - | 181572 | 283768 | 100001 | 63 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0004 | 181572 | 283768 | 100001 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0005-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0005 | - | 181573 | 289184 | 100001 | 100 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0005 | 181573 | 289184 | 100001 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0006-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0006 | - | 188771 | 235993 | 100000 | 63 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0006 | 188771 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0007-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0007 | - | 183354 | 235993 | 100000 | 100 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0007 | 183354 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0008-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0008 | - | 177937 | 235993 | 100000 | 100 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0008 | 177937 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0009-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0009 | - | 188771 | 231193 | 100000 | 100 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0009 | 188771 | 231193 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0010-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0010 | - | 183354 | 231193 | 100000 | 100 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0010 | 183354 | 231193 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0011-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0011 | - | 187682 | 327500 | 100150 | 100 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0011 | 187682 | 327500 | 100150 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0012-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0012 | - | 237233 | 138100 | 100000 | 100 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0012 | 237233 | 138100 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0001-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0001 | - | 244467 | 270700 | 100000 | 63 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0001 | 244467 | 270700 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0002-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0002 | - | 236950 | 270400 | 100000 | 100 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0002 | 236950 | 270400 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0003-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0003 | - | 181573 | 278351 | 100000 | 63 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0003 | 181573 | 278351 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0004-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0004 | - | 181572 | 283768 | 100001 | 63 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0004 | 181572 | 283768 | 100001 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0005-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0005 | - | 181573 | 289184 | 100001 | 100 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0005 | 181573 | 289184 | 100001 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0006-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0006 | - | 188771 | 235993 | 100000 | 63 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0006 | 188771 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0007-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0007 | - | 183354 | 235993 | 100000 | 100 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0007 | 183354 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0008-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0008 | - | 177937 | 235993 | 100000 | 100 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0008 | 177937 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0009-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0009 | - | 188771 | 231193 | 100000 | 100 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0009 | 188771 | 231193 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0010-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0010 | - | 183354 | 231193 | 100000 | 100 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0010 | 183354 | 231193 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0011-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0011 | - | 187682 | 327500 | 100150 | 100 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0011 | 187682 | 327500 | 100150 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0012-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0012 | - | 237233 | 138100 | 100000 | 100 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0012 | 237233 | 138100 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-BE-0316-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,645 | 1,15 | 88 | PS5-79-IG-0001 | 1 | 244467 | 270700 | 270700 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0316 | 243338 | 219996 | 101197 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0315-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,714 | 1,18 | 87 | PS5-79-IG-0001 | 2 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0315 | 243338 | 223504 | 101197 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0168-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,506 | 0,22 | 84 | PS5-79-IG-0001 | 3 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0168 | 241959 | 220525 | 102519 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0170-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,506 | 0,22 | 84 | PS5-79-IG-0001 | 4 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0170 | 241959 | 223025 | 102519 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0163-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,564 | 0,68 | 76 | PS5-79-IG-0001 | 5 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0163 | 231939 | 222100 | 107461 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0167-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,276 | 0,12 | 84 | PS5-79-IG-0001 | 6 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0167 | 240543 | 220525 | 101466 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-SP-0167-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,28 | 0,12 | 4 | PS5-79-BE-0167 | 6 | 240543 | 220525 | 101466 | Heat Tracing Junction Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0167 | 243286 | 220525 | 102148 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01
PS5-79-BE-0169-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,28 | 0,12 | 83 | PS5-79-IG-0001 | 7 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0169 | 240543 | 223025 | 101466 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-SP-0169-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,28 | 0,12 | 4 | PS5-79-BE-0169 | 7 | 240543 | 223025 | 101466 | Heat Tracing Junction Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0169 | 243286 | 223025 | 102148 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0159-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,28 | 0,99 | 82 | PS5-79-IG-0001 | 8 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0159 | 240568 | 223373 | 102718 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0164-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,19 | 1,82 | 82 | PS5-79-IG-0001 | 9 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0164 | 239353 | 220933 | 102111 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0151-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,02 | 0,88 | 75 | PS5-79-IG-0001 | 10 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0151 | 231939 | 223940 | 107461 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0356-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,48 | 0,21 | 87 | PS5-79-IG-0001 | 11 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0356 | 239409 | 227070 | 101525 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0206-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,52 | 1,53 | 71 | PS5-79-IG-0001 | 12 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0206 | 230410 | 222103 | 105090 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0148-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,23 | 0,97 | 80 | PS5-79-IG-0001 | 13 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0148 | 234264 | 218700 | 100757 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0314-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,33 | 0,58 | 79 | PS5-79-IG-0001 | 14 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0314 | 234664 | 223790 | 100810 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0149-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,17 | 0,51 | 79 | PS5-79-IG-0001 | 15 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0149 | 234664 | 223841 | 100864 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0234-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,45 | 0,63 | 85 | PS5-79-IG-0001 | 16 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0234 | 235900 | 228531 | 101214 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0114-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,44 | 0,19 | 83 | PS5-79-IG-0001 | 17 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0114 | 235643 | 227096 | 101122 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0165-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,41 | 0,18 | 73 | PS5-79-IG-0001 | 18 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0165 | 232390 | 222024 | 105269 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0166-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,30 | 1,00 | 83 | PS5-79-IG-0001 | 19 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0166 | 240568 | 220127 | 102718 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0157-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,41 | 0,18 | 72 | PS5-79-IG-0001 | 20 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0157 | 232390 | 224016 | 105269 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0153-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,16 | 1,81 | 81 | PS5-79-IG-0001 | 21 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0153 | 239353 | 222643 | 102111 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0313-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,02 | 0,88 | 81 | PS5-79-IG-0001 | 22 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0313 | 234664 | 218200 | 100810 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0188-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,88 | 2,99 | 71 | PS5-79-IG-0001 | 23 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0188 | 229077 | 221200 | 103567 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0202-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,58 | 1,99 | 62 | PS5-79-IG-0001 | 24 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0202 | 230815 | 233080 | 101207 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0103-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,35 | 1,02 | 52 | PS5-79-IG-0001 | 25 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0103 | 230928 | 240000 | 103807 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0317-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,66 | 2,46 | 50 | PS5-79-IG-0001 | 26 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0317 | 229998 | 240601 | 103757 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0306-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,13 | 1,36 | 51 | PS5-79-IG-0001 | 27 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0306 | 230663 | 240870 | 103807 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0197-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,06 | 2,20 | 52 | PS5-79-IG-0001 | 28 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0197 | 230924 | 242238 | 101694 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-71-BE-0361-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,31 | 0,57 | 85 | PS5-79-IG-0001 | 31 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-71-BE-0361 | 238800 | 226900 | 101600 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-BE-0181-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,66 | 0,72 | 69 | PS5-79-IG-0002 | 1 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0181 | 240997 | 238208 | 101917 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0184-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,71 | 3,35 | 69 | PS5-79-IG-0002 | 2 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0184 | 240723 | 238999 | 101200 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0302-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,10 | 0,48 | 69 | PS5-79-IG-0002 | 3 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0302 | 241490 | 240340 | 100830 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0185-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,68 | 0,73 | 65 | PS5-79-IG-0002 | 4 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0185 | 240723 | 242400 | 101200 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0182-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,54 | 0,67 | 63 | PS5-79-IG-0002 | 5 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0182 | 240980 | 243177 | 101917 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0303-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,06 | 0,46 | 65 | PS5-79-IG-0002 | 6 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0303 | 241500 | 243740 | 100830 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0304-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,92 | 0,40 | 57 | PS5-79-IG-0002 | 7 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0304 | 241500 | 256840 | 100830 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0325-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,37 | 0,16 | 74 | PS5-79-IG-0002 | 8 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0325 | 241877 | 253180 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0311-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,63 | 0,71 | 73 | PS5-79-IG-0002 | 9 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0311 | 240750 | 252298 | 101265 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0312-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,64 | 0,28 | 71 | PS5-79-IG-0002 | 10 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0312 | 240755 | 251693 | 101207 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0173-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,37 | 0,16 | 62 | PS5-79-IG-0002 | 11 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0173 | 235874 | 240560 | 101330 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0183-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,89 | 0,82 | 59 | PS5-79-IG-0002 | 12 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0183 | 234147 | 242200 | 101086 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0355-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,24 | 1,41 | 68 | PS5-79-IG-0002 | 13 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0355 | 235800 | 250475 | 100957 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0354-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,08 | 0,47 | 69 | PS5-79-IG-0002 | 14 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0354 | 235750 | 250580 | 101012 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0201-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,76 | 2,07 | 43 | PS5-79-IG-0002 | 15 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0201 | 230302 | 252108 | 102757 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0193-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,27 | 1,42 | 37 | PS5-79-IG-0002 | 16 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0193 | 228750 | 256760 | 103807 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0322-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,96 | 1,72 | 38 | PS5-79-IG-0002 | 17 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0322 | 228250 | 257200 | 101810 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0192-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,97 | 1,29 | 53 | PS5-79-IG-0002 | 18 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0192 | 235536 | 253763 | 101394 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0191-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,62 | 0,27 | 53 | PS5-79-IG-0002 | 19 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0191 | 235536 | 253839 | 101480 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0346-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,13 | 0,49 | 52 | PS5-79-IG-0002 | 20 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0346 | 235900 | 255166 | 101413 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0172-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,79 | 0,78 | 59 | PS5-79-IG-0002 | 21 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0172 | 240997 | 254708 | 101917 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0179-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,17 | 0,51 | 56 | PS5-79-IG-0002 | 22 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0179 | 240469 | 255500 | 101201 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0326-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,32 | 0,14 | 75 | PS5-79-IG-0002 | 23 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0326 | 243390 | 253155 | 101352 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0180-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,10 | 0,48 | 53 | PS5-79-IG-0002 | 24 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0180 | 240469 | 258900 | 101201 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0174-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,31 | 0,57 | 54 | PS5-79-IG-0002 | 25 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0174 | 240980 | 259677 | 101917 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0305-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,85 | 0,37 | 53 | PS5-79-IG-0002 | 26 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0305 | 241490 | 260240 | 100830 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0199-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,63 | 0,71 | 16 | PS5-79-IG-0002 | 27 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0199 | 231080 | 267750 | 101207 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0187-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,50 | 0,65 | 13 | PS5-79-IG-0002 | 28 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0187 | 230209 | 271970 | 100932 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0190-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,13 | 0,49 | 12 | PS5-79-IG-0002 | 29 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0190 | 231079 | 272840 | 100932 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-71-BE-0363-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,15 | 0,50 | 74 | PS5-79-IG-0002 | 31 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-71-BE-0363 | 242800 | 253200 | 101400 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-BE-0023-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,85 | 0,37 | 104 | PS5-79-IG-0003 | 1 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0023 | 220640 | 290532 | 101212 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0278-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 6,26 | 2,72 | 108 | PS5-79-IG-0003 | 2 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0278 | 226338 | 289066 | 101180 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0307-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,44 | 1,93 | 104 | PS5-79-IG-0003 | 3 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0307 | 220400 | 290532 | 101469 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0198-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,30 | 1,87 | 103 | PS5-79-IG-0003 | 4 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0198 | 220150 | 290532 | 100989 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0046-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,78 | 0,34 | 103 | PS5-79-IG-0003 | 5 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0046 | 220400 | 290532 | 101212 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0195-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,52 | 1,53 | 102 | PS5-79-IG-0003 | 6 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0195 | 219400 | 290480 | 101188 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0252-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,64 | 0,28 | 95 | PS5-79-IG-0003 | 7 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0252 | 212140 | 290532 | 101212 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0253-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,48 | 0,21 | 95 | PS5-79-IG-0003 | 8 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0253 | 211900 | 290532 | 101212 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0200-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,84 | 0,80 | 90 | PS5-79-IG-0003 | 9 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0200 | 211490 | 288175 | 103157 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0194-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,84 | 0,80 | 90 | PS5-79-IG-0003 | 10 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0194 | 211246 | 288425 | 103262 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0246-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,38 | 0,60 | 89 | PS5-79-IG-0003 | 11 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0246 | 210672 | 288763 | 103144 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0189-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 9,98 | 4,34 | 91 | PS5-79-IG-0003 | 12 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0189 | 204848 | 288289 | 105732 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0210-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,87 | 2,55 | 65 | PS5-79-IG-0003 | 13 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0210 | 196946 | 266438 | 105435 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0186-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 9,48 | 4,12 | 87 | PS5-79-IG-0003 | 14 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0186 | 204405 | 291103 | 105732 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0279-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,22 | 2,27 | 99 | PS5-79-IG-0003 | 15 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0279 | 199010 | 286722 | 100981 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0260-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,92 | 3,01 | 61 | PS5-79-IG-0003 | 16 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0260 | 197783 | 272860 | 100932 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0211-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,08 | 3,08 | 64 | PS5-79-IG-0003 | 17 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0211 | 196845 | 275099 | 105806 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0196-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,43 | 3,23 | 76 | PS5-79-IG-0003 | 18 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0196 | 205676 | 277859 | 101382 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0244-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,34 | 3,19 | 77 | PS5-79-IG-0003 | 19 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0244 | 205976 | 277870 | 101407 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0238-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,03 | 3,49 | 93 | PS5-79-IG-0003 | 20 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0238 | 217399 | 271620 | 100907 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0348-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,71 | 1,18 | 131 | PS5-79-IG-0003 | 21 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0348 | 219346 | 254053 | 102535 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0352-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,66 | 2,46 | 142 | PS5-79-IG-0003 | 22 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0352 | 218159 | 247962 | 108511 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0242-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,37 | 0,16 | 157 | PS5-79-IG-0003 | 23 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0242 | 220056 | 228161 | 101110 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0109-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,31 | 0,57 | 144 | PS5-79-IG-0003 | 24 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0109 | 222085 | 240958 | 100705 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0113-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,62 | 0,27 | 145 | PS5-79-IG-0003 | 25 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0113 | 222086 | 238208 | 101375 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0106-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,84 | 0,80 | 146 | PS5-79-IG-0003 | 26 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0106 | 219440 | 238342 | 102285 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0351-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,68 | 3,34 | 160 | PS5-79-IG-0003 | 27 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0351 | 220339 | 228361 | 110926 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0243-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,35 | 0,15 | 141 | PS5-79-IG-0003 | 28 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0243 | 217157 | 247498 | 101110 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-60-BE-0365-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,31 | 0,57 | 85 | PS5-79-IG-0003 | 31 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0365 | 215500 | 312500 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-BE-0280-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,86 | 3,85 | 79 | PS5-79-IG-0004 | 1 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0280 | 215228 | 299886 | 101181 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0331-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,52 | 0,66 | 75 | PS5-79-IG-0004 | 2 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0331 | 215614 | 303612 | 101575 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0327-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,62 | 0,27 | 73 | PS5-79-IG-0004 | 3 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0327 | 215360 | 304680 | 101934 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0266-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,24 | 0,54 | 73 | PS5-79-IG-0004 | 4 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0266 | 214054 | 304944 | 100997 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0265-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,76 | 0,33 | 72 | PS5-79-IG-0004 | 5 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0265 | 213097 | 303800 | 100793 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0212-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,68 | 0,73 | 16 | PS5-79-IG-0004 | 6 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0212 | 179511 | 288596 | 107559 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0049-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,99 | 0,43 | 76 | PS5-79-IG-0004 | 7 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0049 | 211500 | 298728 | 100859 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0329-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,14 | 0,93 | 67 | PS5-79-IG-0004 | 8 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0329 | 206506 | 308300 | 100862 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0285-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,09 | 1,78 | 65 | PS5-79-IG-0004 | 9 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0285 | 200713 | 300386 | 100981 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0220-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,61 | 0,70 | 58 | PS5-79-IG-0004 | 10 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0220 | 199000 | 309240 | 103413 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0217-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,77 | 0,77 | 65 | PS5-79-IG-0004 | 11 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0217 | 198698 | 316234 | 103413 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0219-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,79 | 0,78 | 54 | PS5-79-IG-0004 | 12 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0219 | 197750 | 306994 | 104165 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0237-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,81 | 0,35 | 52 | PS5-79-IG-0004 | 13 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0237 | 166750 | 305025 | 99503 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-SP-0237-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,81 | 0,35 | 4 | PS5-79-BE-0237 | 13 | 166750 | 305025 | 99503 | Heat Tracing Junction Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0237 | 165225 | 305000 | 99500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0282-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,58 | 1,12 | 43 | PS5-79-IG-0004 | 14 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0282 | 185063 | 304826 | 100981 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0213-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,76 | 0,35 | 34 | PS5-79-IG-0004 | 15 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0213 | 177353 | 299849 | 109584 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0086-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,51 | 0,22 | 48 | PS5-79-IG-0004 | 16 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0086 | 167025 | 303869 | 101940 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0214-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,44 | 1,93 | 48 | PS5-79-IG-0004 | 17 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0214 | 167400 | 304590 | 102299 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0283-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,71 | 1,18 | 44 | PS5-79-IG-0004 | 18 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0283 | 185685 | 305326 | 100981 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0092-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,76 | 0,33 | 68 | PS5-79-IG-0004 | 19 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0092 | 164079 | 303569 | 101944 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0216-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,02 | 0,88 | 67 | PS5-79-IG-0004 | 20 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0216 | 163800 | 304363 | 100526 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0215-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,96 | 0,85 | 68 | PS5-79-IG-0004 | 21 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0215 | 162600 | 304254 | 100526 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0099-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,12 | 2,66 | 71 | PS5-79-IG-0004 | 22 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0099 | 162045 | 301748 | 101355 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0171-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,98 | 0,86 | 74 | PS5-79-IG-0004 | 23 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0171 | 156950 | 304072 | 101055 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0264-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,24 | 0,54 | 73 | PS5-79-IG-0004 | 24 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0264 | 213090 | 303800 | 101027 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0281-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,67 | 0,29 | 22 | PS5-79-IG-0004 | 25 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0281 | 182760 | 297505 | 100999 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0284-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,71 | 0,31 | 24 | PS5-79-IG-0004 | 26 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0284 | 183263 | 298176 | 100999 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-60-BE-0366-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,38 | 0,60 | 90 | PS5-79-IG-0004 | 28 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0366 | 215500 | 321000 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-BE-0332-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,82 | 0,79 | 90 | PS5-79-IG-0005 | 1 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0332 | 215614 | 312112 | 101575 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0330-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,74 | 0,32 | 87 | PS5-79-IG-0005 | 2 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0330 | 215360 | 313180 | 101934 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0269-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,50 | 0,65 | 87 | PS5-79-IG-0005 | 3 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0269 | 214054 | 313444 | 100997 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0267-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,50 | 0,65 | 88 | PS5-79-IG-0005 | 4 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0267 | 213090 | 312300 | 101027 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0268-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,92 | 0,40 | 87 | PS5-79-IG-0005 | 5 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0268 | 213097 | 312300 | 100793 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0334-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,63 | 0,71 | 81 | PS5-79-IG-0005 | 6 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0334 | 215614 | 320612 | 101575 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0333-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,64 | 0,28 | 78 | PS5-79-IG-0005 | 7 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0333 | 215360 | 321680 | 101934 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0272-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,33 | 0,58 | 78 | PS5-79-IG-0005 | 8 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0272 | 214054 | 321944 | 100997 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0270-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,33 | 0,58 | 78 | PS5-79-IG-0005 | 9 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0270 | 213090 | 320800 | 101027 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0271-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,83 | 0,36 | 77 | PS5-79-IG-0005 | 10 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0271 | 213097 | 320800 | 100793 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0335-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,70 | 0,74 | 85 | PS5-79-IG-0005 | 11 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0335 | 215614 | 329112 | 101575 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0339-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,74 | 0,32 | 88 | PS5-79-IG-0005 | 12 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0339 | 215350 | 330180 | 101934 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0275-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,45 | 0,63 | 85 | PS5-79-IG-0005 | 13 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0275 | 214054 | 330444 | 100997 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0273-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,40 | 0,61 | 83 | PS5-79-IG-0005 | 14 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0273 | 213090 | 329300 | 101027 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0274-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,87 | 0,38 | 83 | PS5-79-IG-0005 | 15 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0274 | 213097 | 329300 | 100793 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0328-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,59 | 1,56 | 76 | PS5-79-IG-0005 | 16 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0328 | 206562 | 316800 | 100862 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0061-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,34 | 1,45 | 73 | PS5-79-IG-0005 | 17 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0061 | 206562 | 325300 | 100862 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0218-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,28 | 0,97 | 65 | PS5-79-IG-0005 | 18 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0218 | 197950 | 315225 | 104093 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0229-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,25 | 0,98 | 81 | PS5-79-IG-0005 | 19 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0229 | 199000 | 343304 | 103413 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0223-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,02 | 0,88 | 61 | PS5-79-IG-0005 | 20 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0223 | 197750 | 323994 | 104165 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0224-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,79 | 0,78 | 64 | PS5-79-IG-0005 | 21 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0224 | 199000 | 326304 | 103413 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0221-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,96 | 0,85 | 72 | PS5-79-IG-0005 | 22 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0221 | 198698 | 333234 | 103413 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0235-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,91 | 2,57 | 69 | PS5-79-IG-0005 | 23 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0235 | 197950 | 332136 | 104155 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0222-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,35 | 1,02 | 68 | PS5-79-IG-0005 | 24 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0222 | 197950 | 332225 | 104094 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0350-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,12 | 2,66 | 71 | PS5-79-IG-0005 | 25 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0350 | 197550 | 335000 | 104155 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0228-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,58 | 1,12 | 77 | PS5-79-IG-0005 | 26 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0228 | 197750 | 340995 | 104165 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0236-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,03 | 2,62 | 60 | PS5-79-IG-0005 | 27 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0236 | 197750 | 323405 | 104155 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-60-BE-0367-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,33 | 0,58 | 86 | PS5-79-IG-0005 | 28 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0367 | 500000 | 329500 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-BE-0136-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 5,43 | 2,36 | 111 | PS5-79-IG-0009 | 1 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0136 | 174539 | 160699 | 101299 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0027-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 4,81 | 2,09 | 109 | PS5-79-IG-0009 | 2 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0027 | 183200 | 167000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0039-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,28 | 2,73 | 87 | PS5-79-IG-0009 | 3 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0039 | 183065 | 175000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0037-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,96 | 3,46 | 82 | PS5-79-IG-0009 | 4 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0037 | 188029 | 175000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0025-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 5,29 | 2,30 | 91 | PS5-79-IG-0009 | 5 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0025 | 191636 | 166696 | 101455 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0343-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,91 | 2,57 | 109 | PS5-79-IG-0009 | 6 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0343 | 188000 | 151456 | 100981 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0118-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 6,26 | 2,72 | 96 | PS5-79-IG-0009 | 7 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0118 | 201450 | 160299 | 100932 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0137-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,34 | 3,19 | 89 | PS5-79-IG-0009 | 8 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0137 | 197700 | 163721 | 100831 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0024-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 5,70 | 2,48 | 87 | PS5-79-IG-0009 | 9 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0024 | 196183 | 167000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0150-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,46 | 0,20 | 99 | PS5-79-IG-0009 | 10 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0150 | 172449 | 193420 | 100933 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0203-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,21 | 3,57 | 72 | PS5-79-IG-0009 | 11 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0203 | 197324 | 179771 | 103496 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0204-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,73 | 3,36 | 70 | PS5-79-IG-0009 | 12 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0204 | 197324 | 179771 | 103496 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0262-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,91 | 3,44 | 74 | PS5-79-IG-0009 | 13 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0262 | 198500 | 180769 | 100932 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0102-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,14 | 3,54 | 75 | PS5-79-IG-0009 | 14 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0102 | 201400 | 180806 | 102118 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0081-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,58 | 3,73 | 85 | PS5-79-IG-0009 | 15 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0081 | 202600 | 176506 | 104208 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0036-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 5,57 | 2,42 | 85 | PS5-79-IG-0009 | 16 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0036 | 204700 | 175000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0066-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,18 | 2,25 | 73 | PS5-79-IG-0009 | 17 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0066 | 183217 | 193840 | 101950 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0067-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,30 | 3,61 | 82 | PS5-79-IG-0009 | 18 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0067 | 181159 | 188775 | 102557 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0245-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,79 | 2,95 | 86 | PS5-79-IG-0009 | 19 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0245 | 177292 | 186398 | 100709 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0134-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,31 | 0,57 | 92 | PS5-79-IG-0009 | 20 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0134 | 174474 | 188800 | 101105 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0063-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,72 | 3,79 | 91 | PS5-79-IG-0009 | 21 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0063 | 173422 | 188775 | 102557 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0154-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,97 | 1,29 | 98 | PS5-79-IG-0009 | 22 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0154 | 172689 | 192677 | 101185 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0319-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,18 | 2,25 | 77 | PS5-79-IG-0009 | 23 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0319 | 196925 | 175793 | 103450 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0290-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,16 | 2,68 | 101 | PS5-79-IG-0009 | 24 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0290 | 171233 | 194182 | 100325 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0152-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,44 | 0,19 | 100 | PS5-79-IG-0009 | 25 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0152 | 172176 | 193950 | 100853 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0002-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,40 | 0,61 | 83 | PS5-79-IG-0009 | 26 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0002 | 171084 | 195053 | 101124 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0005-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,53 | 0,23 | 102 | PS5-79-IG-0009 | 27 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0005 | 167902 | 193341 | 101931 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0146-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,70 | 0,74 | 84 | PS5-79-IG-0009 | 28 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0146 | 168255 | 196163 | 101848 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0041-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,30 | 3,61 | 86 | PS5-79-IG-0009 | 29 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0041 | 166404 | 196138 | 101856 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0135-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,63 | 1,58 | 102 | PS5-79-IG-0009 | 30 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0135 | 165955 | 191157 | 101225 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0239-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,12 | 0,05 | 104 | PS5-79-IG-0009 | 31 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0239 | 164054 | 191175 | 100815 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-IP-9901-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 9,82 | 4,27 | 107 | PS5-79-IG-0009 | 40 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9901 | 162500 | 192500 | 103000 | Marshalling Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-IP-9101-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 9,82 | 4,27 | 2 | PS5-79-IP-9901 | 40 | 188770 | 235992 | 100000 | Marshalling Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9101 | 162500 | 192500 | 103000 | ETS-05 | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-IP-9102-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 9,82 | 4,27 | 2 | PS5-79-IP-9901 | 40 | 188770 | 235992 | 100000 | Marshalling Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9102 | 162500 | 192500 | 103000 | ETS-05 | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-BE-0247-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,45 | 1,50 | 62 | PS5-79-IG-0007 | 1 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0247 | 208675 | 209077 | 100981 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0084-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,51 | 2,83 | 63 | PS5-79-IG-0007 | 2 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0084 | 207145 | 202000 | 103808 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0090-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,74 | 2,93 | 59 | PS5-79-IG-0007 | 3 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0090 | 205689 | 204200 | 103858 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0085-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 6,28 | 2,73 | 102 | PS5-79-IG-0007 | 4 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0085 | 209345 | 195451 | 101459 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0082-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,54 | 3,28 | 85 | PS5-79-IG-0007 | 5 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0082 | 202600 | 185283 | 101458 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0101-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,34 | 3,19 | 67 | PS5-79-IG-0007 | 6 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0101 | 201400 | 192750 | 101508 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0156-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,32 | 0,14 | 73 | PS5-79-IG-0007 | 7 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0156 | 172176 | 205950 | 100853 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0107-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,99 | 1,30 | 61 | PS5-79-IG-0007 | 8 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0107 | 202295 | 197899 | 101586 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0020-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,87 | 0,38 | 60 | PS5-79-IG-0007 | 9 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0020 | 202600 | 200539 | 101111 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0147-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,61 | 1,57 | 62 | PS5-79-IG-0007 | 10 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0147 | 200200 | 196749 | 101306 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0043-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,49 | 1,95 | 61 | PS5-79-IG-0007 | 11 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0043 | 200200 | 196748 | 100899 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0344-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,30 | 2,74 | 60 | PS5-79-IG-0007 | 12 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0344 | 199150 | 197250 | 100957 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0019-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,54 | 0,67 | 56 | PS5-79-IG-0007 | 13 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0019 | 200200 | 202140 | 101204 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0100-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,64 | 2,45 | 52 | PS5-79-IG-0007 | 14 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0100 | 201095 | 205400 | 102118 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0112-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,62 | 2,88 | 59 | PS5-79-IG-0007 | 15 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0112 | 196423 | 199581 | 105256 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0068-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,17 | 1,38 | 74 | PS5-79-IG-0007 | 16 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0068 | 187776 | 194297 | 104013 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0042-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,10 | 3,52 | 73 | PS5-79-IG-0007 | 17 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0042 | 188219 | 196139 | 102051 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0121-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,11 | 3,09 | 65 | PS5-79-IG-0007 | 18 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0121 | 187776 | 198775 | 105458 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0072-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,05 | 3,50 | 71 | PS5-79-IG-0007 | 19 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0072 | 181159 | 200776 | 102557 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0116-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,37 | 0,16 | 65 | PS5-79-IG-0007 | 20 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0116 | 186955 | 198357 | 103990 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0145-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,38 | 0,60 | 87 | PS5-79-IG-0007 | 21 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0145 | 174474 | 200800 | 101105 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0155-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,44 | 0,19 | 93 | PS5-79-IG-0007 | 22 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0155 | 172449 | 205420 | 100933 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0071-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,26 | 3,59 | 86 | PS5-79-IG-0007 | 23 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0071 | 173422 | 200775 | 102557 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0083-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,23 | 1,84 | 66 | PS5-79-IG-0007 | 24 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0083 | 202600 | 196129 | 101458 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0291-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,51 | 1,96 | 74 | PS5-79-IG-0007 | 25 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0291 | 171200 | 206167 | 100325 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0003-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,22 | 0,53 | 73 | PS5-79-IG-0007 | 26 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0003 | 171084 | 207053 | 101124 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0143-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,50 | 0,65 | 74 | PS5-79-IG-0007 | 27 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0143 | 168255 | 208165 | 101848 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0059-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,36 | 3,20 | 76 | PS5-79-IG-0007 | 28 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0059 | 166234 | 208140 | 101856 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0006-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,51 | 0,22 | 96 | PS5-79-IG-0007 | 29 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0006 | 167902 | 205341 | 101931 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0144-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,42 | 1,05 | 99 | PS5-79-IG-0007 | 30 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0144 | 165955 | 203157 | 101225 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0240-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,12 | 0,05 | 101 | PS5-79-IG-0007 | 31 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0240 | 164054 | 203175 | 100815 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-IP-9902-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 9,18 | 3,99 | 100 | PS5-79-IG-0007 | 40 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9902 | 162300 | 204500 | 103000 | Marshalling Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-IP-9103-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 9,18 | 3,99 | 2 | PS5-79-IP-9902 | 40 | 162300 | 204500 | 103000 | Marshalling Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9103 | 162300 | 204500 | 103000 | ETS-05 | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-IP-9104-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 9,18 | 3,99 | 2 | PS5-79-IP-9902 | 40 | 162300 | 204500 | 103000 | Marshalling Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9104 | 162300 | 204500 | 103000 | ETS-05 | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-BE-0241-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,09 | 0,04 | 87 | PS5-79-IG-0008 | 1 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0241 | 164054 | 215175 | 100815 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0208-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,34 | 2,32 | 60 | PS5-79-IG-0008 | 2 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0208 | 196823 | 202422 | 103897 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0292-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,44 | 1,93 | 73 | PS5-79-IG-0008 | 3 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0292 | 171157 | 218205 | 100325 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0058-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,45 | 3,24 | 77 | PS5-79-IG-0008 | 4 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0058 | 166404 | 220137 | 101856 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0140-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,52 | 0,66 | 75 | PS5-79-IG-0008 | 5 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0140 | 168255 | 220162 | 101848 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0004-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,22 | 0,53 | 73 | PS5-79-IG-0008 | 6 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0004 | 171084 | 219053 | 101124 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0007-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,48 | 0,21 | 92 | PS5-79-IG-0008 | 7 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0007 | 167902 | 217341 | 101931 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0161-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,30 | 0,13 | 72 | PS5-79-IG-0008 | 8 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0161 | 172176 | 217950 | 100853 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0139-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,82 | 3,40 | 69 | PS5-79-IG-0008 | 9 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0139 | 177600 | 222875 | 100911 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0162-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,29 | 1,43 | 73 | PS5-79-IG-0008 | 10 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0162 | 172689 | 216677 | 101185 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0074-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,18 | 3,12 | 75 | PS5-79-IG-0008 | 11 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0074 | 173422 | 212775 | 102557 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0142-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,20 | 0,52 | 76 | PS5-79-IG-0008 | 12 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0142 | 174474 | 212800 | 101105 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0160-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,35 | 0,15 | 73 | PS5-79-IG-0008 | 13 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0160 | 172449 | 217420 | 100933 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0077-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,71 | 3,35 | 68 | PS5-79-IG-0008 | 14 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0077 | 181161 | 212775 | 102557 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0075-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,44 | 1,93 | 61 | PS5-79-IG-0008 | 15 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0075 | 183067 | 217840 | 101950 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0053-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,10 | 2,65 | 55 | PS5-79-IG-0008 | 16 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0053 | 188219 | 220137 | 102051 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0076-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,34 | 2,32 | 57 | PS5-79-IG-0008 | 17 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0076 | 187776 | 217027 | 104105 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0070-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,61 | 2,44 | 69 | PS5-79-IG-0008 | 18 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0070 | 183217 | 205840 | 101950 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0158-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,59 | 0,69 | 67 | PS5-79-IG-0008 | 19 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0158 | 186955 | 204702 | 103862 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0060-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,99 | 3,04 | 63 | PS5-79-IG-0008 | 20 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0060 | 188220 | 208140 | 102051 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0115-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,98 | 2,60 | 70 | PS5-79-IG-0008 | 21 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0115 | 187470 | 201639 | 105153 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0108-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,35 | 3,63 | 69 | PS5-79-IG-0008 | 22 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0108 | 187775 | 201639 | 105458 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0111-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,45 | 0,63 | 70 | PS5-79-IG-0008 | 23 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0111 | 187776 | 201639 | 105458 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0062-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,92 | 2,14 | 60 | PS5-79-IG-0008 | 24 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0062 | 192099 | 208343 | 104443 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0141-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,16 | 0,94 | 89 | PS5-79-IG-0008 | 25 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0141 | 165955 | 215157 | 101225 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0207-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,18 | 2,25 | 61 | PS5-79-IG-0008 | 26 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0207 | 196925 | 202422 | 103999 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0205-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,10 | 2,65 | 54 | PS5-79-IG-0008 | 27 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0205 | 197324 | 208877 | 104158 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0044-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,06 | 2,20 | 59 | PS5-79-IG-0008 | 28 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0044 | 200200 | 204201 | 101509 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0045-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,80 | 2,52 | 51 | PS5-79-IG-0008 | 29 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0045 | 200200 | 219527 | 101305 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0261-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,89 | 2,56 | 45 | PS5-79-IG-0008 | 30 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0261 | 198500 | 220750 | 100932 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0209-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,73 | 1,62 | 37 | PS5-79-IG-0008 | 31 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0209 | 196947 | 228659 | 104680 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-IP-9903-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,26 | 3,59 | 90 | PS5-79-IG-0008 | 40 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9903 | 162300 | 216500 | 103000 | Marshalling Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-IP-9105-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,26 | 3,59 | 2 | PS5-79-IP-9903 | 40 | 162300 | 216500 | 103000 | Marshalling Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9105 | 162300 | 216500 | 103000 | ETS-05 | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-IP-9106-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,26 | 3,59 | 2 | PS5-79-IP-9903 | 40 | 162300 | 216500 | 103000 | Marshalling Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9106 | 162300 | 216500 | 103000 | ETS-05 | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-BE-0064-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,18 | 3,12 | 127 | PS5-79-IG-0006 | 1 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0064 | 228214 | 165701 | 100715 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0057-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,67 | 1,16 | 129 | PS5-79-IG-0006 | 2 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0057 | 228213 | 165700 | 100689 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0021-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,94 | 3,45 | 119 | PS5-79-IG-0006 | 3 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0021 | 228571 | 167000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0128-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,47 | 1,51 | 128 | PS5-79-IG-0006 | 4 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0128 | 235019 | 171416 | 106386 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0008-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,99 | 0,43 | 123 | PS5-79-IG-0006 | 5 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0008 | 233210 | 167025 | 102000 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-SP-0008-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,99 | 0,43 | 4 | PS5-79-BE-0008 | 5 | 233210 | 167025 | 102000 | Heat Tracing Junction Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0008 | 236800 | 167050 | 101871 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0047-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,04 | 0,45 | 113 | PS5-79-IG-0006 | 6 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0047 | 228548 | 175025 | 101454 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0052-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 8,05 | 3,50 | 127 | PS5-79-IG-0006 | 7 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0052 | 229050 | 163348 | 101261 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0056-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,83 | 0,36 | 129 | PS5-79-IG-0006 | 8 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0056 | 231065 | 163375 | 101264 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0055-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,62 | 0,27 | 130 | PS5-79-IG-0006 | 9 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0055 | 232257 | 163475 | 101061 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0028-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,68 | 3,34 | 111 | PS5-79-IG-0006 | 10 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0028 | 228549 | 175000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0294-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 8,76 | 3,81 | 124 | PS5-79-IG-0006 | 11 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0294 | 234065 | 166653 | 101323 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0293-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 8,56 | 3,72 | 125 | PS5-79-IG-0006 | 12 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0293 | 234273 | 166647 | 101323 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0129-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,99 | 0,43 | 124 | PS5-79-IG-0006 | 13 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0129 | 234844 | 169860 | 104312 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0073-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,15 | 0,50 | 117 | PS5-79-IG-0006 | 14 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0073 | 228570 | 167025 | 101454 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0010-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,27 | 0,55 | 117 | PS5-79-IG-0006 | 15 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0010 | 233958 | 175025 | 102052 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-SP-0010-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,27 | 0,55 | 4 | PS5-79-BE-0010 | 15 | 233958 | 175025 | 102052 | Heat Tracing Junction Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0010 | 235900 | 175050 | 102185 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0124-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,11 | 2,22 | 126 | PS5-79-IG-0006 | 16 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0124 | 238800 | 168373 | 103338 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0295-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 8,12 | 3,53 | 119 | PS5-79-IG-0006 | 17 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0295 | 234437 | 174668 | 101310 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0030-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,31 | 3,18 | 111 | PS5-79-IG-0006 | 18 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0030 | 231955 | 178347 | 101332 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0127-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,12 | 2,66 | 118 | PS5-79-IG-0006 | 19 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0127 | 235418 | 174600 | 103736 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0051-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,25 | 0,98 | 113 | PS5-79-IG-0006 | 20 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0051 | 229877 | 176342 | 100778 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0032-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,64 | 0,28 | 113 | PS5-79-IG-0006 | 21 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0032 | 234577 | 178525 | 101132 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0033-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,76 | 0,33 | 112 | PS5-79-IG-0006 | 22 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0033 | 234421 | 178625 | 101332 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0126-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,87 | 0,38 | 126 | PS5-79-IG-0006 | 23 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0126 | 236689 | 170208 | 104335 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0125-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,06 | 1,33 | 128 | PS5-79-IG-0006 | 24 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0125 | 236600 | 170673 | 106169 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0011-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,70 | 0,74 | 137 | PS5-79-IG-0006 | 25 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0011 | 238298 | 165338 | 101175 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0301-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 8,03 | 3,49 | 118 | PS5-79-IG-0006 | 26 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0301 | 234237 | 174668 | 101310 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0001-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,56 | 0,68 | 127 | PS5-79-IG-0006 | 27 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0001 | 238100 | 168588 | 100857 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0009-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,68 | 0,74 | 121 | PS5-79-IG-0006 | 28 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0009 | 238100 | 173364 | 100857 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0014-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,68 | 0,73 | 122 | PS5-79-IG-0006 | 29 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0014 | 238553 | 174035 | 100955 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0034-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,83 | 3,84 | 110 | PS5-79-IG-0006 | 30 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0034 | 231955 | 178500 | 101484 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0353-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,12 | 0,05 | 116 | PS5-79-IG-0006 | 31 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0353 | 232858 | 175000 | 102038 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-71-BE-0362-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,47 | 0,64 | 96 | PS5-79-IG-0006 | 34 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-71-BE-0362 | 222100 | 238700 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-BE-0132-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,51 | 3,70 | 129 | PS5-79-IG-0010 | 1 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0132 | 224576 | 160480 | 103459 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0131-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,77 | 3,38 | 123 | PS5-79-IG-0010 | 2 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0131 | 224576 | 170627 | 103663 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0040-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,08 | 2,21 | 115 | PS5-79-IG-0010 | 3 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0040 | 226578 | 176343 | 100762 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0233-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 6,58 | 2,83 | 117 | PS5-79-IG-0010 | 4 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0233 | 226574 | 176343 | 100762 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0054-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,54 | 3,28 | 119 | PS5-79-IG-0010 | 5 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0054 | 219480 | 163500 | 103134 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0022-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,75 | 3,37 | 120 | PS5-79-IG-0010 | 6 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0022 | 216500 | 167000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0078-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 6,39 | 2,78 | 115 | PS5-79-IG-0010 | 7 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0078 | 219286 | 169500 | 101859 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0105-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,38 | 3,21 | 112 | PS5-79-IG-0010 | 8 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0105 | 218361 | 172500 | 101859 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0029-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,68 | 3,34 | 112 | PS5-79-IG-0010 | 9 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0029 | 216500 | 175000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0035-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 5,66 | 2,46 | 103 | PS5-79-IG-0010 | 10 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0035 | 220950 | 178500 | 103134 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0094-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 6,10 | 2,65 | 117 | PS5-79-IG-0010 | 11 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0094 | 225400 | 194027 | 101256 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0120-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,22 | 2,27 | 102 | PS5-79-IG-0010 | 12 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0120 | 209307 | 194000 | 100805 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0095-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,27 | 3,16 | 105 | PS5-79-IG-0010 | 13 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0095 | 219302 | 187701 | 101459 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0087-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,71 | 3,35 | 99 | PS5-79-IG-0010 | 14 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0087 | 214800 | 189046 | 103800 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0119-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,47 | 0,64 | 101 | PS5-79-IG-0010 | 15 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0119 | 209319 | 193700 | 100812 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0117-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,24 | 1,41 | 118 | PS5-79-IG-0010 | 16 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0117 | 224091 | 195374 | 100690 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0323-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,75 | 0,76 | 103 | PS5-79-IG-0010 | 17 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0323 | 211053 | 168590 | 100805 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0096-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,30 | 3,61 | 73 | PS5-79-IG-0010 | 18 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0096 | 214800 | 198461 | 101459 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0079-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 5,98 | 2,60 | 98 | PS5-79-IG-0010 | 19 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0079 | 207218 | 169500 | 101859 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0345-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,83 | 2,10 | 96 | PS5-79-IG-0010 | 20 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0345 | 205850 | 169551 | 101550 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0104-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 6,05 | 2,63 | 93 | PS5-79-IG-0010 | 21 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0104 | 205714 | 172500 | 101859 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0230-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,66 | 3,33 | 83 | PS5-79-IG-0010 | 22 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0230 | 224091 | 199276 | 100642 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0093-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,07 | 2,64 | 80 | PS5-79-IG-0010 | 23 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0093 | 225400 | 202887 | 101459 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0088-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,79 | 2,95 | 81 | PS5-79-IG-0010 | 24 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0088 | 219900 | 196571 | 101409 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0089-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,76 | 2,07 | 81 | PS5-79-IG-0010 | 25 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0089 | 219660 | 196571 | 101200 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0091-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,98 | 2,60 | 71 | PS5-79-IG-0010 | 26 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0091 | 217966 | 204200 | 101460 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0097-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,48 | 3,25 | 66 | PS5-79-IG-0010 | 27 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0097 | 214495 | 205400 | 102069 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0321-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,17 | 0,51 | 101 | PS5-79-IG-0010 | 28 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0321 | 209350 | 169769 | 101312 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0227-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,43 | 1,49 | 70 | PS5-79-IG-0010 | 29 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0227 | 223175 | 213949 | 100794 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-60-BE-0364-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,39 | 1,04 | 156 | PS5-79-IG-0010 | 31 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0364 | 215500 | 304000 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-BE-0286-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,46 | 2,81 | 55 | PS5-79-IG-0011 | 1 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0286 | 197748 | 364287 | 100982 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0347-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,98 | 1,73 | 55 | PS5-79-IG-0011 | 2 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0347 | 198049 | 364286 | 100982 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0289-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,14 | 1,80 | 56 | PS5-79-IG-0011 | 3 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0289 | 198150 | 364287 | 100982 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0342-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,53 | 0,23 | 64 | PS5-79-IG-0011 | 4 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0342 | 215350 | 355680 | 101934 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0232-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,73 | 0,75 | 48 | PS5-79-IG-0011 | 5 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0232 | 197950 | 358238 | 104094 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0231-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,52 | 0,66 | 43 | PS5-79-IG-0011 | 6 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0231 | 197750 | 354702 | 104165 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0288-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,10 | 0,48 | 65 | PS5-79-IG-0011 | 7 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0288 | 214054 | 338944 | 100997 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0225-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,08 | 0,47 | 40 | PS5-79-IG-0011 | 8 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0225 | 198698 | 350234 | 103413 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0324-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,13 | 0,49 | 60 | PS5-79-IG-0011 | 9 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0324 | 206562 | 359300 | 100862 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0080-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,94 | 0,41 | 51 | PS5-79-IG-0011 | 10 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0080 | 206562 | 350800 | 100862 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0065-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,99 | 0,43 | 53 | PS5-79-IG-0011 | 11 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0065 | 206562 | 342300 | 100862 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0287-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,94 | 1,28 | 62 | PS5-79-IG-0011 | 12 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0287 | 206562 | 333800 | 100862 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0277-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,69 | 0,30 | 64 | PS5-79-IG-0011 | 13 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0277 | 213097 | 337800 | 100793 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0276-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,10 | 0,48 | 65 | PS5-79-IG-0011 | 14 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0276 | 213090 | 337800 | 101027 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0226-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,27 | 0,55 | 37 | PS5-79-IG-0011 | 15 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0226 | 197950 | 349225 | 104094 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0340-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,48 | 0,21 | 65 | PS5-79-IG-0011 | 16 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0340 | 215350 | 338680 | 101934 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0336-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,38 | 0,60 | 70 | PS5-79-IG-0011 | 17 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0336 | 215614 | 337612 | 101575 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0031-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,58 | 0,25 | 55 | PS5-79-IG-0011 | 18 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0031 | 213097 | 346300 | 100793 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0016-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,94 | 0,41 | 56 | PS5-79-IG-0011 | 19 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0016 | 213090 | 346300 | 101027 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0038-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,97 | 0,42 | 56 | PS5-79-IG-0011 | 20 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0038 | 214054 | 347444 | 100997 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0341-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,46 | 0,21 | 57 | PS5-79-IG-0011 | 21 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0341 | 215350 | 347180 | 101934 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0337-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,20 | 0,52 | 60 | PS5-79-IG-0011 | 22 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0337 | 215614 | 346112 | 101575 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0050-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,64 | 0,28 | 61 | PS5-79-IG-0011 | 23 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0050 | 213097 | 354800 | 100793 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0048-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,06 | 0,46 | 62 | PS5-79-IG-0011 | 24 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0048 | 213090 | 354800 | 101027 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0069-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,08 | 0,47 | 63 | PS5-79-IG-0011 | 25 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0069 | 214054 | 355944 | 100997 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0349-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,05 | 1,76 | 56 | PS5-79-IG-0011 | 26 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0349 | 198249 | 364286 | 100982 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0338-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,27 | 0,56 | 64 | PS5-79-IG-0011 | 27 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0338 | 215614 | 354612 | 101575 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-60-BE-0368-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,06 | 0,46 | 69 | PS5-79-IG-0011 | 28 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0368 | 215500 | 338000 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-60-BE-0369-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,90 | 0,39 | 59 | PS5-79-IG-0011 | 29 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0369 | 215500 | 346500 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-60-BE-0370-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,97 | 0,43 | 64 | PS5-79-IG-0011 | 30 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0370 | 215500 | 355000 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-BE-0251-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,19 | 1,82 | 40 | PS5-79-IG-0012 | 1 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0251 | 239386 | 146336 | 100676 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0297-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,86 | 1,68 | 41 | PS5-79-IG-0012 | 2 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0297 | 239300 | 147040 | 98105 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0296-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,73 | 1,62 | 40 | PS5-79-IG-0012 | 3 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0296 | 239150 | 147040 | 98105 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0012-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,66 | 1,59 | 32 | PS5-79-IG-0012 | 4 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0012 | 216500 | 143608 | 100632 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0259-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,43 | 1,49 | 38 | PS5-79-IG-0012 | 5 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0259 | 238710 | 146783 | 100934 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0257-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,62 | 2,01 | 42 | PS5-79-IG-0012 | 6 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0257 | 208499 | 146301 | 101560 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0258-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,24 | 0,54 | 63 | PS5-79-IG-0012 | 7 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0258 | 203205 | 137535 | 102669 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0098-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,56 | 0,68 | 65 | PS5-79-IG-0012 | 8 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0098 | 201820 | 137480 | 101261 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0300-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,16 | 0,94 | 65 | PS5-79-IG-0012 | 9 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0300 | 203110 | 137410 | 101000 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0123-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,63 | 0,71 | 63 | PS5-79-IG-0012 | 10 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0123 | 201583 | 136497 | 101046 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0248-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,39 | 1,91 | 85 | PS5-79-IG-0012 | 11 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0248 | 189221 | 134450 | 102585 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0254-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,58 | 0,25 | 53 | PS5-79-IG-0012 | 12 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0254 | 198905 | 137199 | 102669 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0310-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,39 | 0,17 | 57 | PS5-79-IG-0012 | 13 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0310 | 197283 | 132705 | 100996 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0263-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,18 | 2,25 | 54 | PS5-79-IG-0012 | 14 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0263 | 196097 | 134965 | 102949 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0122-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,36 | 0,59 | 53 | PS5-79-IG-0012 | 15 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0122 | 197283 | 136497 | 101046 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0110-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,17 | 0,51 | 52 | PS5-79-IG-0012 | 16 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0110 | 197444 | 137480 | 101261 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0256-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,37 | 0,16 | 51 | PS5-79-IG-0012 | 17 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0256 | 195500 | 139465 | 102551 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0320-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,65 | 2,02 | 53 | PS5-79-IG-0012 | 18 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0320 | 196924 | 147901 | 102900 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0255-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,70 | 0,74 | 55 | PS5-79-IG-0012 | 19 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0255 | 195500 | 146339 | 101874 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0017-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,60 | 0,26 | 56 | PS5-79-IG-0012 | 20 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0017 | 195005 | 143600 | 100594 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0250-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,23 | 2,71 | 57 | PS5-79-IG-0012 | 21 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0250 | 194925 | 145853 | 101575 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0249-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,92 | 1,27 | 58 | PS5-79-IG-0012 | 22 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0249 | 193752 | 145650 | 101577 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0318-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,55 | 0,24 | 59 | PS5-79-IG-0012 | 23 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0318 | 193233 | 145878 | 101482 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0309-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,29 | 0,56 | 80 | PS5-79-IG-0012 | 24 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0309 | 188000 | 133775 | 99912 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0018-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,08 | 0,47 | 81 | PS5-79-IG-0012 | 25 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0018 | 188000 | 133475 | 99973 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-SP-0018-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,08 | 0,47 | 4 | PS5-79-BE-0018 | 25 | 188000 | 133475 | 99973 | Heat Tracing Junction Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0018 | 188073 | 132498 | 99903 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0130-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,86 | 0,81 | 88 | PS5-79-IG-0012 | 26 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0130 | 188089 | 130543 | 95737 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0299-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,75 | 0,76 | 53 | PS5-79-IG-0012 | 27 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0299 | 198800 | 137410 | 101000 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0308-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,75 | 2,50 | 85 | PS5-79-IG-0012 | 28 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0308 | 188754 | 130838 | 100908 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0013-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,25 | 0,98 | 42 | PS5-79-IG-0012 | 29 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0013 | 241860 | 146810 | 101037 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0015-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,67 | 0,29 | 44 | PS5-79-IG-0012 | 30 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0015 | 241860 | 148012 | 96662 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0133-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,81 | 0,35 | 40 | PS5-79-IG-0012 | 31 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0133 | 241210 | 147725 | 99988 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-SP-0133-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,81 | 0,35 | 4 | PS5-79-BE-0133 | 31 | 241210 | 147725 | 99988 | Heat Tracing Junction Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0133 | 238238 | 147751 | 99916 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0298-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,35 | 1,89 | 43 | PS5-79-IG-0012 | 32 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0298 | 241325 | 147040 | 98105 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0026-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,39 | 0,17 | 42 | PS5-79-IG-0012 | 33 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0026 | 240420 | 144825 | 101007 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0138-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,23 | 0,97 | 24 | PS5-79-IG-0012 | 34 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0138 | 225604 | 149272 | 100912 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-25-BE-0364-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,28 | 0,99 | 148 | PS5-79-IG-0012 | 37 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-25-BE-0364 | 168700 | 210600 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-TE-0316-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 88 | PS5-79-IG-0001 | 1 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0316 | 238823 | 219996 | 101198 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0315-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0001 | 2 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0315 | 238823 | 223504 | 101198 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0168-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 83 | PS5-79-IG-0001 | 3 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0168 | 241959 | 220752 | 102733 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0170-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 83 | PS5-79-IG-0001 | 4 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0170 | 241959 | 222748 | 102733 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0163-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 76 | PS5-79-IG-0001 | 5 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0163 | 231300 | 222100 | 107460 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0167-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 83 | PS5-79-IG-0001 | 6 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0167 | 240472 | 220525 | 101251 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0169-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 83 | PS5-79-IG-0001 | 7 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0169 | 240472 | 223025 | 101251 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0159-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 82 | PS5-79-IG-0001 | 8 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0159 | 239053 | 223000 | 101408 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0164-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0001 | 9 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0164 | 232390 | 222113 | 107198 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0151-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 75 | PS5-79-IG-0001 | 10 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0151 | 231300 | 223940 | 107460 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0356-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 86 | PS5-79-IG-0001 | 11 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0356 | 239891 | 227070 | 100963 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0206-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 70 | PS5-79-IG-0001 | 12 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0206 | 229610 | 220823 | 105048 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0148-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 79 | PS5-79-IG-0001 | 13 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0148 | 234264 | 219817 | 100758 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0314-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 79 | PS5-79-IG-0001 | 14 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0314 | 234664 | 224790 | 100810 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0149-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 78 | PS5-79-IG-0001 | 15 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0149 | 234914 | 223790 | 101199 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0234-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 84 | PS5-79-IG-0001 | 16 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0234 | 235422 | 230795 | 102252 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0114-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 82 | PS5-79-IG-0001 | 17 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0114 | 235893 | 227070 | 100825 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0165-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0001 | 18 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0165 | 232390 | 221800 | 105270 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0166-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 82 | PS5-79-IG-0001 | 19 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0166 | 239053 | 220500 | 101408 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0157-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 72 | PS5-79-IG-0001 | 20 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0157 | 232390 | 224260 | 105270 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0153-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 71 | PS5-79-IG-0001 | 21 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0153 | 232390 | 223953 | 107198 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0313-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 80 | PS5-79-IG-0001 | 22 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0313 | 234664 | 218529 | 100810 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0188-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 70 | PS5-79-IG-0001 | 23 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0188 | 230850 | 221200 | 103568 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0202-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 61 | PS5-79-IG-0001 | 24 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0202 | 235900 | 228743 | 101262 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0103-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 51 | PS5-79-IG-0001 | 25 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0103 | 230400 | 240000 | 103807 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0317-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 49 | PS5-79-IG-0001 | 26 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0317 | 230150 | 243250 | 101207 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0306-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 51 | PS5-79-IG-0001 | 27 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0306 | 230400 | 240870 | 103807 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0197-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 51 | PS5-79-IG-0001 | 28 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0197 | 230810 | 244473 | 101182 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-71-TE-0361-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 84 | PS5-79-IG-0001 | 31 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-71-TE-0361 | 244467 | 270700 | 100000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-TE-0181-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 68 | PS5-79-IG-0002 | 1 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0181 | 237218 | 238542 | 101124 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0184-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 69 | PS5-79-IG-0002 | 2 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0184 | 240387 | 239000 | 101202 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0302-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 68 | PS5-79-IG-0002 | 3 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0302 | 241615 | 238750 | 101250 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0185-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 65 | PS5-79-IG-0002 | 4 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0185 | 240387 | 242400 | 101202 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0182-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 63 | PS5-79-IG-0002 | 5 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0182 | 237218 | 242850 | 101123 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0303-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 65 | PS5-79-IG-0002 | 6 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0303 | 241615 | 242140 | 101170 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0304-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 56 | PS5-79-IG-0002 | 7 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0304 | 241590 | 255255 | 101130 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0325-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0002 | 8 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0325 | 240743 | 253155 | 100906 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0311-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 72 | PS5-79-IG-0002 | 9 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0311 | 240750 | 252298 | 101265 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0312-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 71 | PS5-79-IG-0002 | 10 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0312 | 240450 | 251493 | 100572 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0173-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 62 | PS5-79-IG-0002 | 11 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0173 | 235536 | 238250 | 101935 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0183-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 58 | PS5-79-IG-0002 | 12 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0183 | 235900 | 238416 | 101356 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0355-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 68 | PS5-79-IG-0002 | 13 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0355 | 235800 | 248278 | 100958 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0354-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 68 | PS5-79-IG-0002 | 14 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0354 | 236254 | 249685 | 101808 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0201-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 70 | PS5-79-IG-0002 | 15 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0201 | 240750 | 252655 | 101201 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0193-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 37 | PS5-79-IG-0002 | 16 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0193 | 230900 | 256760 | 103808 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0322-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 38 | PS5-79-IG-0002 | 17 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0322 | 229750 | 257200 | 101810 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0192-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0002 | 18 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0192 | 234786 | 253801 | 101433 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0191-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 53 | PS5-79-IG-0002 | 19 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0191 | 235536 | 254891 | 102020 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0346-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0002 | 20 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0346 | 235900 | 254504 | 101433 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0172-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 58 | PS5-79-IG-0002 | 21 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0172 | 237218 | 255228 | 101124 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0179-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 56 | PS5-79-IG-0002 | 22 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0179 | 239808 | 255500 | 101202 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0326-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0002 | 23 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0326 | 243630 | 252799 | 100906 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0180-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 53 | PS5-79-IG-0002 | 24 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0180 | 239808 | 258900 | 101202 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0174-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 53 | PS5-79-IG-0002 | 25 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0174 | 237218 | 259172 | 101124 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0305-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0002 | 26 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0305 | 241628 | 258632 | 101165 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0199-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 15 | PS5-79-IG-0002 | 27 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0199 | 231080 | 268250 | 101208 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0187-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 13 | PS5-79-IG-0002 | 28 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0187 | 228590 | 271970 | 100932 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0190-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 12 | PS5-79-IG-0002 | 29 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0190 | 230590 | 272840 | 100933 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-71-TE-0363-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0002 | 31 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-71-TE-0363 | 236950 | 270400 | 100000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-TE-0023-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 104 | PS5-79-IG-0003 | 1 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0023 | 221392 | 290057 | 101203 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0278-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 107 | PS5-79-IG-0003 | 2 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0278 | 226125 | 289066 | 100966 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0307-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 104 | PS5-79-IG-0003 | 3 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0307 | 220400 | 290058 | 101534 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0198-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 103 | PS5-79-IG-0003 | 4 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0198 | 220150 | 289891 | 101053 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0046-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 103 | PS5-79-IG-0003 | 5 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0046 | 220677 | 289557 | 101204 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0195-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 102 | PS5-79-IG-0003 | 6 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0195 | 219400 | 290243 | 101188 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0252-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 95 | PS5-79-IG-0003 | 7 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0252 | 212892 | 289807 | 101201 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0253-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 95 | PS5-79-IG-0003 | 8 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0253 | 212177 | 289555 | 101202 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0200-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 90 | PS5-79-IG-0003 | 9 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0200 | 211643 | 289144 | 103742 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0194-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 90 | PS5-79-IG-0003 | 10 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0194 | 211246 | 289034 | 103742 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0246-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 90 | PS5-79-IG-0003 | 11 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0246 | 210672 | 289075 | 103717 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0189-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 91 | PS5-79-IG-0003 | 12 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0189 | 205176 | 283600 | 104682 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0210-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 66 | PS5-79-IG-0003 | 13 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0210 | 196946 | 264938 | 105415 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0186-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 91 | PS5-79-IG-0003 | 14 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0186 | 204875 | 283600 | 104682 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0279-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 99 | PS5-79-IG-0003 | 15 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0279 | 199010 | 286936 | 100766 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0260-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 62 | PS5-79-IG-0003 | 16 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0260 | 197100 | 272860 | 100932 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0211-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 64 | PS5-79-IG-0003 | 17 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0211 | 196947 | 273301 | 105573 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0196-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 77 | PS5-79-IG-0003 | 18 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0196 | 205676 | 278359 | 101382 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0244-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 78 | PS5-79-IG-0003 | 19 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0244 | 205975 | 278369 | 101407 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0238-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 94 | PS5-79-IG-0003 | 20 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0238 | 216899 | 271670 | 100957 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0348-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 132 | PS5-79-IG-0003 | 21 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0348 | 219647 | 254750 | 100833 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0352-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 143 | PS5-79-IG-0003 | 22 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0352 | 218391 | 247728 | 103510 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0242-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 158 | PS5-79-IG-0003 | 23 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0242 | 220155 | 228089 | 101150 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0109-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 145 | PS5-79-IG-0003 | 24 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0109 | 222085 | 240600 | 100705 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0113-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 146 | PS5-79-IG-0003 | 25 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0113 | 222085 | 237440 | 100805 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0106-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 147 | PS5-79-IG-0003 | 26 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0106 | 220275 | 238061 | 102551 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0351-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 161 | PS5-79-IG-0003 | 27 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0351 | 220627 | 228174 | 104727 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0243-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 142 | PS5-79-IG-0003 | 28 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0243 | 217200 | 247375 | 101150 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-60-TE-0365-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 85 | PS5-79-IG-0003 | 31 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0365 | 181572 | 278350 | 100000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-TE-0280-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 79 | PS5-79-IG-0004 | 1 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0280 | 215014 | 299886 | 100966 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0331-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 76 | PS5-79-IG-0004 | 2 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0331 | 215168 | 303801 | 101481 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0327-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0004 | 3 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0327 | 213515 | 304680 | 101934 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0266-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0004 | 4 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0266 | 212777 | 304931 | 100870 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0265-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0004 | 5 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0265 | 212966 | 305183 | 100872 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0212-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 16 | PS5-79-IG-0004 | 6 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0212 | 179511 | 288096 | 107550 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0049-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 76 | PS5-79-IG-0004 | 7 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0049 | 212114 | 299026 | 100734 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0329-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 67 | PS5-79-IG-0004 | 8 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0329 | 205508 | 308300 | 100855 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0285-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 65 | PS5-79-IG-0004 | 9 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0285 | 200500 | 300386 | 100766 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0220-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0004 | 10 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0220 | 199000 | 311000 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0217-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 66 | PS5-79-IG-0004 | 11 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0217 | 198698 | 314800 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0219-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0004 | 12 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0219 | 200810 | 309100 | 105155 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0237-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0004 | 13 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0237 | 166750 | 303101 | 101966 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0282-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 43 | PS5-79-IG-0004 | 14 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0282 | 184849 | 304826 | 100766 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0213-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 32 | PS5-79-IG-0004 | 15 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0213 | 177354 | 301049 | 110441 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0086-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 47 | PS5-79-IG-0004 | 16 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0086 | 166447 | 303869 | 102455 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0214-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 47 | PS5-79-IG-0004 | 17 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0214 | 177354 | 302401 | 109639 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0283-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 45 | PS5-79-IG-0004 | 18 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0283 | 185472 | 305326 | 100766 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0092-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 68 | PS5-79-IG-0004 | 19 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0092 | 166447 | 303569 | 102455 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0216-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 66 | PS5-79-IG-0004 | 20 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0216 | 164104 | 302200 | 101983 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0215-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 68 | PS5-79-IG-0004 | 21 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0215 | 160805 | 303570 | 101983 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0099-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 70 | PS5-79-IG-0004 | 22 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0099 | 160707 | 301999 | 100682 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0171-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0004 | 23 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0171 | 159908 | 304072 | 98765 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0264-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0004 | 24 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0264 | 212007 | 303534 | 99817 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0281-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 22 | PS5-79-IG-0004 | 25 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0281 | 182760 | 297737 | 100766 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0284-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 24 | PS5-79-IG-0004 | 26 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0284 | 183263 | 298408 | 100766 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-60-TE-0366-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 90 | PS5-79-IG-0004 | 28 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0366 | 181571 | 283767 | 100000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-TE-0332-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 89 | PS5-79-IG-0005 | 1 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0332 | 215168 | 312301 | 101481 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0330-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 86 | PS5-79-IG-0005 | 2 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0330 | 213515 | 313180 | 101934 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0269-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0005 | 3 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0269 | 212777 | 313431 | 100870 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0267-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0005 | 4 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0267 | 212007 | 312034 | 99817 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0268-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0005 | 5 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0268 | 212966 | 313683 | 100872 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0334-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 81 | PS5-79-IG-0005 | 6 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0334 | 215168 | 320801 | 101481 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0333-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 77 | PS5-79-IG-0005 | 7 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0333 | 213515 | 321680 | 101934 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0272-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 77 | PS5-79-IG-0005 | 8 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0272 | 212777 | 321931 | 100870 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0270-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 78 | PS5-79-IG-0005 | 9 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0270 | 212007 | 320534 | 99817 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0271-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 77 | PS5-79-IG-0005 | 10 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0271 | 212966 | 322183 | 100872 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0335-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 85 | PS5-79-IG-0005 | 11 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0335 | 215168 | 329301 | 101481 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0339-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 88 | PS5-79-IG-0005 | 12 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0339 | 213515 | 330180 | 101934 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0275-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 85 | PS5-79-IG-0005 | 13 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0275 | 212777 | 330431 | 100870 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0273-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 83 | PS5-79-IG-0005 | 14 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0273 | 212007 | 329034 | 99817 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0274-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 82 | PS5-79-IG-0005 | 15 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0274 | 212978 | 330683 | 100872 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0328-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 75 | PS5-79-IG-0005 | 16 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0328 | 205508 | 316800 | 100855 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0061-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 72 | PS5-79-IG-0005 | 17 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0061 | 205508 | 325300 | 100855 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0218-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 65 | PS5-79-IG-0005 | 18 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0218 | 198698 | 316800 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0229-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 81 | PS5-79-IG-0005 | 19 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0229 | 199000 | 345000 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0223-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 60 | PS5-79-IG-0005 | 20 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0223 | 200810 | 326100 | 105155 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0224-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 64 | PS5-79-IG-0005 | 21 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0224 | 199000 | 328000 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0221-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 71 | PS5-79-IG-0005 | 22 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0221 | 198698 | 331800 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0235-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 96 | PS5-79-IG-0005 | 23 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0235 | 197950 | 360000 | 104155 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0222-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 67 | PS5-79-IG-0005 | 24 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0222 | 198698 | 333800 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0350-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 70 | PS5-79-IG-0005 | 25 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0350 | 197550 | 334500 | 104156 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0228-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 76 | PS5-79-IG-0005 | 26 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0228 | 200810 | 343100 | 105155 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0236-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 90 | PS5-79-IG-0005 | 27 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0236 | 197109 | 356487 | 103665 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-60-TE-0367-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 85 | PS5-79-IG-0005 | 28 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0367 | 181572 | 289183 | 100000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-TE-0136-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 110 | PS5-79-IG-0009 | 1 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0136 | 174857 | 160698 | 100977 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0027-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 109 | PS5-79-IG-0009 | 2 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0027 | 180200 | 167000 | 101759 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0039-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0009 | 3 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0039 | 180700 | 175000 | 101759 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0037-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 75 | PS5-79-IG-0009 | 4 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0037 | 193145 | 175000 | 101760 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0025-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 97 | PS5-79-IG-0009 | 5 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0025 | 186200 | 167000 | 101759 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0343-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 109 | PS5-79-IG-0009 | 6 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0343 | 188000 | 151232 | 100756 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0118-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 88 | PS5-79-IG-0009 | 7 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0118 | 201490 | 167899 | 102792 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0137-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 88 | PS5-79-IG-0009 | 8 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0137 | 197700 | 163412 | 100520 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0024-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0009 | 9 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0024 | 195183 | 167000 | 101759 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0150-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 99 | PS5-79-IG-0009 | 10 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0150 | 172689 | 192702 | 101424 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0203-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 69 | PS5-79-IG-0009 | 11 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0203 | 197323 | 177900 | 103476 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0204-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 68 | PS5-79-IG-0009 | 12 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0204 | 198325 | 180000 | 103521 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0262-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0009 | 13 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0262 | 198500 | 184250 | 100932 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0102-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 75 | PS5-79-IG-0009 | 14 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0102 | 201400 | 183750 | 101508 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0081-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 84 | PS5-79-IG-0009 | 15 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0081 | 202600 | 174505 | 104208 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0036-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 85 | PS5-79-IG-0009 | 16 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0036 | 206200 | 175000 | 101759 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0066-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0009 | 17 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0066 | 186500 | 193840 | 102001 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0067-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 78 | PS5-79-IG-0009 | 18 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0067 | 181713 | 188775 | 102557 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0245-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 82 | PS5-79-IG-0009 | 19 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0245 | 177499 | 186398 | 100706 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0134-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 92 | PS5-79-IG-0009 | 20 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0134 | 174074 | 188775 | 100774 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0063-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 91 | PS5-79-IG-0009 | 21 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0063 | 174500 | 188775 | 101800 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0154-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 97 | PS5-79-IG-0009 | 22 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0154 | 177644 | 192677 | 103057 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0319-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0009 | 23 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0319 | 196925 | 174293 | 103412 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0290-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 100 | PS5-79-IG-0009 | 24 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0290 | 171117 | 194175 | 100325 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0152-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 99 | PS5-79-IG-0009 | 25 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0152 | 172433 | 193924 | 101329 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0002-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 83 | PS5-79-IG-0009 | 26 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0002 | 166450 | 195438 | 101170 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0005-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 96 | PS5-79-IG-0009 | 27 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0005 | 167902 | 193765 | 103275 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0146-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 83 | PS5-79-IG-0009 | 28 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0146 | 169805 | 195887 | 101115 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0041-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 85 | PS5-79-IG-0009 | 29 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0041 | 169755 | 196138 | 102052 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0135-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 102 | PS5-79-IG-0009 | 30 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0135 | 171113 | 189271 | 100855 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0239-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 103 | PS5-79-IG-0009 | 31 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0239 | 164054 | 191066 | 100815 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0247-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 61 | PS5-79-IG-0007 | 1 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0247 | 208952 | 209077 | 100703 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0084-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 63 | PS5-79-IG-0007 | 2 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0084 | 206380 | 202000 | 103808 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0090-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 58 | PS5-79-IG-0007 | 3 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0090 | 207189 | 204200 | 103858 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0085-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 101 | PS5-79-IG-0007 | 4 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0085 | 209345 | 190699 | 101459 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0082-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 84 | PS5-79-IG-0007 | 5 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0082 | 202600 | 184250 | 101458 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0101-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 67 | PS5-79-IG-0007 | 6 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0101 | 201400 | 191750 | 101509 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0156-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 72 | PS5-79-IG-0007 | 7 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0156 | 172433 | 205924 | 101329 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0107-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 61 | PS5-79-IG-0007 | 8 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0107 | 199600 | 197899 | 105458 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0020-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0007 | 9 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0020 | 204412 | 202048 | 100655 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0147-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0007 | 10 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0147 | 200200 | 202915 | 101509 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0043-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 62 | PS5-79-IG-0007 | 11 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0043 | 198200 | 196138 | 105257 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0344-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 61 | PS5-79-IG-0007 | 12 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0344 | 199150 | 200250 | 100957 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0019-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0007 | 13 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0019 | 201100 | 202114 | 100662 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0100-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 51 | PS5-79-IG-0007 | 14 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0100 | 201400 | 203901 | 101509 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0112-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0007 | 15 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0112 | 198423 | 199581 | 105256 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0068-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0007 | 16 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0068 | 187775 | 195297 | 104105 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0042-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0007 | 17 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0042 | 191179 | 196138 | 102051 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0121-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 65 | PS5-79-IG-0007 | 18 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0121 | 187775 | 195976 | 105458 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0072-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 71 | PS5-79-IG-0007 | 19 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0072 | 181713 | 200775 | 102557 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0116-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 65 | PS5-79-IG-0007 | 20 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0116 | 187955 | 198332 | 105858 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0145-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0007 | 21 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0145 | 174074 | 200775 | 100774 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0155-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 93 | PS5-79-IG-0007 | 22 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0155 | 172689 | 204702 | 101424 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0071-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 85 | PS5-79-IG-0007 | 23 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0071 | 174500 | 200775 | 101800 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0083-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 66 | PS5-79-IG-0007 | 24 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0083 | 202600 | 198400 | 101458 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0291-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 72 | PS5-79-IG-0007 | 25 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0291 | 171207 | 206325 | 100325 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0003-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0007 | 26 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0003 | 166449 | 207438 | 101170 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0143-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0007 | 27 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0143 | 169805 | 207889 | 101115 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0059-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 75 | PS5-79-IG-0007 | 28 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0059 | 169700 | 208140 | 102051 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0006-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 97 | PS5-79-IG-0007 | 29 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0006 | 167902 | 205765 | 103275 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0144-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 99 | PS5-79-IG-0007 | 30 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0144 | 170924 | 201271 | 100860 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0240-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 101 | PS5-79-IG-0007 | 31 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0240 | 164054 | 203066 | 100815 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0241-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0008 | 1 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0241 | 164054 | 215066 | 100815 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0208-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 58 | PS5-79-IG-0008 | 2 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0208 | 196925 | 204250 | 104025 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0292-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 72 | PS5-79-IG-0008 | 3 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0292 | 171157 | 218205 | 100325 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0058-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 76 | PS5-79-IG-0008 | 4 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0058 | 169700 | 220137 | 102051 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0140-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0008 | 5 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0140 | 169682 | 219889 | 101116 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0004-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0008 | 6 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0004 | 166499 | 219438 | 101170 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0007-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 92 | PS5-79-IG-0008 | 7 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0007 | 167902 | 217765 | 103275 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0161-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 71 | PS5-79-IG-0008 | 8 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0161 | 172433 | 217924 | 101329 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0139-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 68 | PS5-79-IG-0008 | 9 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0139 | 177600 | 222558 | 100592 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0162-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 72 | PS5-79-IG-0008 | 10 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0162 | 177644 | 216677 | 103057 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0074-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0008 | 11 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0074 | 174500 | 212775 | 101800 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0142-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0008 | 12 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0142 | 174074 | 212775 | 100774 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0160-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 72 | PS5-79-IG-0008 | 13 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0160 | 172689 | 216702 | 101424 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0077-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 67 | PS5-79-IG-0008 | 14 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0077 | 181713 | 212774 | 102557 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0075-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0008 | 15 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0075 | 186540 | 217839 | 102001 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0053-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 54 | PS5-79-IG-0008 | 16 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0053 | 191179 | 220137 | 102051 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0076-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 57 | PS5-79-IG-0008 | 17 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0076 | 187775 | 214671 | 104105 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0070-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 69 | PS5-79-IG-0008 | 18 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0070 | 188000 | 205839 | 102001 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0158-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 67 | PS5-79-IG-0008 | 19 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0158 | 184264 | 204676 | 103057 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0060-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 64 | PS5-79-IG-0008 | 20 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0060 | 191179 | 208140 | 102051 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0115-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 71 | PS5-79-IG-0008 | 21 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0115 | 187775 | 202287 | 105458 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0108-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 69 | PS5-79-IG-0008 | 22 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0108 | 191122 | 197899 | 105458 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0111-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 70 | PS5-79-IG-0008 | 23 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0111 | 187776 | 200139 | 105458 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0062-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0008 | 24 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0062 | 193609 | 208140 | 105256 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0141-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 89 | PS5-79-IG-0008 | 25 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0141 | 170924 | 213271 | 100865 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0207-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0008 | 26 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0207 | 196925 | 200922 | 103970 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0205-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 53 | PS5-79-IG-0008 | 27 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0205 | 197324 | 209377 | 104169 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0044-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0008 | 28 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0044 | 200200 | 208250 | 101509 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0045-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 53 | PS5-79-IG-0008 | 29 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0045 | 197920 | 220137 | 105256 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0261-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0008 | 30 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0261 | 198500 | 221250 | 100932 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0209-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 35 | PS5-79-IG-0008 | 31 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0209 | 196946 | 229260 | 104691 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0064-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 137 | PS5-79-IG-0006 | 1 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0064 | 236596 | 165701 | 100821 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0057-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 134 | PS5-79-IG-0006 | 2 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0057 | 234539 | 166030 | 102686 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0021-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 118 | PS5-79-IG-0006 | 3 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0021 | 228971 | 167000 | 101760 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0128-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 128 | PS5-79-IG-0006 | 4 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0128 | 235019 | 170968 | 106378 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0008-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 122 | PS5-79-IG-0006 | 5 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0008 | 233090 | 167120 | 102369 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0047-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 112 | PS5-79-IG-0006 | 6 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0047 | 229548 | 174159 | 100892 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0052-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 128 | PS5-79-IG-0006 | 7 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0052 | 229350 | 163500 | 101413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0056-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 130 | PS5-79-IG-0006 | 8 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0056 | 230166 | 164001 | 102150 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0055-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 130 | PS5-79-IG-0006 | 9 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0055 | 232257 | 164311 | 100750 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0028-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 111 | PS5-79-IG-0006 | 10 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0028 | 229198 | 175000 | 101759 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0294-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 124 | PS5-79-IG-0006 | 11 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0294 | 233965 | 166653 | 101323 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0293-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 125 | PS5-79-IG-0006 | 12 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0293 | 235030 | 166577 | 101403 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0129-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 123 | PS5-79-IG-0006 | 13 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0129 | 234540 | 171975 | 104899 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0073-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 118 | PS5-79-IG-0006 | 14 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0073 | 230570 | 167917 | 100816 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0010-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 117 | PS5-79-IG-0006 | 15 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0010 | 234070 | 174888 | 102451 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0124-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 126 | PS5-79-IG-0006 | 16 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0124 | 236600 | 170234 | 105727 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0295-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 119 | PS5-79-IG-0006 | 17 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0295 | 234537 | 174668 | 101310 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0030-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 111 | PS5-79-IG-0006 | 18 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0030 | 233800 | 178499 | 101484 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0127-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 117 | PS5-79-IG-0006 | 19 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0127 | 235019 | 171976 | 105894 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0051-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 114 | PS5-79-IG-0006 | 20 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0051 | 233542 | 175902 | 102880 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0032-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 112 | PS5-79-IG-0006 | 21 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0032 | 234577 | 178100 | 100849 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0033-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 111 | PS5-79-IG-0006 | 22 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0033 | 233281 | 178000 | 102321 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0126-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 126 | PS5-79-IG-0006 | 23 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0126 | 237100 | 170234 | 104900 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0125-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 128 | PS5-79-IG-0006 | 24 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0125 | 236599 | 171024 | 106165 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0011-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 138 | PS5-79-IG-0006 | 25 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0011 | 236102 | 165838 | 101175 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0301-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 118 | PS5-79-IG-0006 | 26 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0301 | 233937 | 174668 | 101310 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0001-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 127 | PS5-79-IG-0006 | 27 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0001 | 237724 | 167300 | 102907 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0009-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 120 | PS5-79-IG-0006 | 28 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0009 | 237218 | 174625 | 102907 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0014-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 121 | PS5-79-IG-0006 | 29 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0014 | 236001 | 174035 | 100955 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0034-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 110 | PS5-79-IG-0006 | 30 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0034 | 230300 | 178499 | 101484 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0353-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 115 | PS5-79-IG-0006 | 31 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0353 | 232858 | 175000 | 102338 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-71-TE-0362-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 97 | PS5-79-IG-0006 | 34 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-71-TE-0362 | 188770 | 231192 | 100000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-TE-0132-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 130 | PS5-79-IG-0010 | 1 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0132 | 224575 | 159480 | 103459 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0131-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 133 | PS5-79-IG-0010 | 2 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0131 | 237559 | 171008 | 103931 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0040-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 127 | PS5-79-IG-0010 | 3 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0040 | 236218 | 176342 | 100877 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0233-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 118 | PS5-79-IG-0010 | 4 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0233 | 223175 | 175342 | 100711 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0054-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 119 | PS5-79-IG-0010 | 5 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0054 | 218479 | 163500 | 103134 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0022-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 120 | PS5-79-IG-0010 | 6 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0022 | 219300 | 167000 | 101760 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0078-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 115 | PS5-79-IG-0010 | 7 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0078 | 215000 | 169500 | 101859 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0105-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 112 | PS5-79-IG-0010 | 8 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0105 | 219286 | 172501 | 101860 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0029-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 111 | PS5-79-IG-0010 | 9 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0029 | 220900 | 175000 | 101759 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0035-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 103 | PS5-79-IG-0010 | 10 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0035 | 219349 | 178499 | 103134 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0094-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 117 | PS5-79-IG-0010 | 11 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0094 | 225400 | 197501 | 101256 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0120-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 102 | PS5-79-IG-0010 | 12 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0120 | 208822 | 194001 | 100625 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0095-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 105 | PS5-79-IG-0010 | 13 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0095 | 218302 | 187701 | 101460 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0087-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 99 | PS5-79-IG-0010 | 14 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0087 | 212800 | 189046 | 103808 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0119-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 101 | PS5-79-IG-0010 | 15 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0119 | 208896 | 193701 | 100609 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0117-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 118 | PS5-79-IG-0010 | 16 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0117 | 224401 | 196123 | 100669 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0323-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 103 | PS5-79-IG-0010 | 17 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0323 | 213702 | 168590 | 100780 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0096-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0010 | 18 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0096 | 214800 | 196293 | 101459 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0079-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 98 | PS5-79-IG-0010 | 19 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0079 | 204850 | 169501 | 101860 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0345-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 96 | PS5-79-IG-0010 | 20 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0345 | 201448 | 168800 | 102208 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0104-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 93 | PS5-79-IG-0010 | 21 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0104 | 207720 | 172500 | 101859 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0230-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 83 | PS5-79-IG-0010 | 22 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0230 | 223174 | 200065 | 100427 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0093-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 80 | PS5-79-IG-0010 | 23 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0093 | 225400 | 203287 | 101460 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0088-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 81 | PS5-79-IG-0010 | 24 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0088 | 219900 | 195071 | 101409 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0089-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 81 | PS5-79-IG-0010 | 25 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0089 | 219900 | 198071 | 101409 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0091-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 71 | PS5-79-IG-0010 | 26 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0091 | 221699 | 204200 | 101459 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0097-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 67 | PS5-79-IG-0010 | 27 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0097 | 214800 | 203486 | 101459 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0321-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 100 | PS5-79-IG-0010 | 28 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0321 | 208715 | 169501 | 100806 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0227-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 71 | PS5-79-IG-0010 | 29 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0227 | 223175 | 213666 | 100511 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-60-TE-0364-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 157 | PS5-79-IG-0010 | 31 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0364 | 183353 | 231192 | 100000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-TE-0286-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 54 | PS5-79-IG-0011 | 1 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0286 | 197748 | 364073 | 100768 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0347-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0011 | 2 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0347 | 198249 | 364043 | 100683 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0289-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0011 | 3 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0289 | 198150 | 364073 | 100768 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0342-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 63 | PS5-79-IG-0011 | 4 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0342 | 213515 | 355680 | 101934 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0232-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 47 | PS5-79-IG-0011 | 5 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0232 | 198698 | 359300 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0231-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 42 | PS5-79-IG-0011 | 6 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0231 | 199000 | 357000 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0288-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 64 | PS5-79-IG-0011 | 7 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0288 | 212777 | 338931 | 100870 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0225-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 40 | PS5-79-IG-0011 | 8 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0225 | 198698 | 348800 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0324-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0011 | 9 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0324 | 205508 | 359300 | 100855 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0080-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 49 | PS5-79-IG-0011 | 10 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0080 | 205508 | 350800 | 100855 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0065-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0011 | 11 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0065 | 205508 | 342300 | 100855 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0287-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 61 | PS5-79-IG-0011 | 12 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0287 | 205508 | 333800 | 100855 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0277-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 64 | PS5-79-IG-0011 | 13 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0277 | 212966 | 339183 | 100872 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0276-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 64 | PS5-79-IG-0011 | 14 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0276 | 212007 | 337534 | 99817 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0226-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 37 | PS5-79-IG-0011 | 15 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0226 | 198698 | 350800 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0340-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 64 | PS5-79-IG-0011 | 16 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0340 | 213515 | 338680 | 101934 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0336-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 67 | PS5-79-IG-0011 | 17 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0336 | 215168 | 337801 | 101481 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0031-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 54 | PS5-79-IG-0011 | 18 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0031 | 212976 | 347683 | 100872 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0016-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0011 | 19 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0016 | 212007 | 346034 | 99817 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0038-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0011 | 20 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0038 | 212777 | 347431 | 100870 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0341-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0011 | 21 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0341 | 213515 | 347180 | 101934 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0337-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0011 | 22 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0337 | 215168 | 346301 | 101481 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0050-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 60 | PS5-79-IG-0011 | 23 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0050 | 212978 | 356183 | 100872 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0048-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 61 | PS5-79-IG-0011 | 24 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0048 | 212007 | 354534 | 99817 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0069-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 63 | PS5-79-IG-0011 | 25 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0069 | 212777 | 355931 | 100870 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0349-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0011 | 26 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0349 | 198100 | 364043 | 100683 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0338-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 62 | PS5-79-IG-0011 | 27 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0338 | 215168 | 354801 | 101481 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-60-TE-0368-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 67 | PS5-79-IG-0011 | 28 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0368 | 187682 | 327500 | 100150 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-60-TE-0369-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 58 | PS5-79-IG-0011 | 29 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0369 | 187682 | 327500 | 100150 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-60-TE-0370-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 63 | PS5-79-IG-0011 | 30 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0370 | 187682 | 327500 | 100150 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-TE-0251-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 40 | PS5-79-IG-0012 | 1 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0251 | 238124 | 145852 | 100694 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0297-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 41 | PS5-79-IG-0012 | 2 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0297 | 239500 | 147040 | 98105 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0296-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 40 | PS5-79-IG-0012 | 3 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0296 | 238950 | 147040 | 98105 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0012-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0012 | 4 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0012 | 193255 | 141600 | 102632 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0259-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 28 | PS5-79-IG-0012 | 5 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0259 | 221999 | 146301 | 101291 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0257-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0012 | 6 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0257 | 194796 | 146301 | 101820 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0258-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 62 | PS5-79-IG-0012 | 7 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0258 | 201705 | 137739 | 103147 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0098-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 63 | PS5-79-IG-0012 | 8 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0098 | 201783 | 140453 | 101661 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0300-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 64 | PS5-79-IG-0012 | 9 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0300 | 203210 | 137410 | 101000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0123-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 62 | PS5-79-IG-0012 | 10 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0123 | 201583 | 136797 | 101046 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0248-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 84 | PS5-79-IG-0012 | 11 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0248 | 189721 | 134450 | 102585 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0254-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 51 | PS5-79-IG-0012 | 12 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0254 | 197904 | 136994 | 103147 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0310-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 56 | PS5-79-IG-0012 | 13 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0310 | 197583 | 132505 | 100996 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0263-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 53 | PS5-79-IG-0012 | 14 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0263 | 196097 | 138065 | 102949 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0122-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 53 | PS5-79-IG-0012 | 15 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0122 | 197283 | 136797 | 101046 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0110-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 51 | PS5-79-IG-0012 | 16 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0110 | 197483 | 140453 | 101661 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0256-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 51 | PS5-79-IG-0012 | 17 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0256 | 195500 | 138926 | 103663 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0320-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 53 | PS5-79-IG-0012 | 18 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0320 | 196924 | 149401 | 102970 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0255-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0012 | 19 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0255 | 195500 | 137348 | 102544 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0017-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 54 | PS5-79-IG-0012 | 20 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0017 | 195005 | 144608 | 100459 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0250-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 56 | PS5-79-IG-0012 | 21 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0250 | 192234 | 145852 | 101629 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0249-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 58 | PS5-79-IG-0012 | 22 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0249 | 193751 | 144600 | 101577 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0318-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 58 | PS5-79-IG-0012 | 23 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0318 | 193236 | 144912 | 102055 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0309-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 79 | PS5-79-IG-0012 | 24 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0309 | 188178 | 133750 | 100454 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0018-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 80 | PS5-79-IG-0012 | 25 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0018 | 189525 | 133450 | 102280 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0130-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0012 | 26 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0130 | 188765 | 129942 | 95737 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0299-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0012 | 27 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0299 | 198900 | 137410 | 101000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0308-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 63 | PS5-79-IG-0012 | 28 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0308 | 197283 | 131351 | 100996 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0013-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 26 | PS5-79-IG-0012 | 29 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0013 | 232969 | 143608 | 100633 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0015-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 44 | PS5-79-IG-0012 | 30 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0015 | 241860 | 147400 | 96662 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0133-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 40 | PS5-79-IG-0012 | 31 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0133 | 242210 | 144975 | 102718 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0298-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 42 | PS5-79-IG-0012 | 32 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0298 | 241525 | 147040 | 98105 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0026-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 41 | PS5-79-IG-0012 | 33 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0026 | 240080 | 146600 | 100617 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0138-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 24 | PS5-79-IG-0012 | 34 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0138 | 225376 | 149272 | 100683 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-25-TE-0364-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 146 | PS5-79-IG-0012 | 37 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-25-TE-0364 | 237232 | 138099 | 100000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-BE-0175-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 104 | PS5-79-IG-0009 | 40 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND-M20-Gland | M20 | PS5-79-BE-0175 | 162500 | 192500 | 103000 | Marshalling Box | Field | SIND M25 Metal Gland Alarm | M25 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-IP-9101-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 2 | PS5-79-BE-0175 | 40 | 162500 | 192500 | 103000 | Marshalling Box | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9101 | 162500 | 192500 | 103000 | ETS-05 | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-IP-9102-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 2 | PS5-79-BE-0175 | 40 | 162500 | 192500 | 103000 | Marshalling Box | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9102 | 162500 | 192500 | 103000 | ETS-05 | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-BE-0176-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 97 | PS5-79-IG-0007 | 40 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND-M20-Gland | M20 | PS5-79-BE-0176 | 162300 | 204500 | 103000 | Marshalling Box | Field | SIND M25 Metal Gland Alarm | M25 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-IP-9103-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 2 | PS5-79-BE-0176 | 40 | 162300 | 204500 | 103000 | Marshalling Box | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9103 | 162300 | 204500 | 103000 | ETS-05 | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-IP-9104-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 2 | PS5-79-BE-0176 | 40 | 162300 | 204500 | 103000 | Marshalling Box | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9104 | 162300 | 204500 | 103000 | ETS-05 | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-BE-0177-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 86 | PS5-79-IG-0008 | 40 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND-M20-Gland | M20 | PS5-79-BE-0177 | 162300 | 216500 | 103000 | Marshalling Box | Field | SIND M25 Metal Gland Alarm | M25 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-IP-9105-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 2 | PS5-79-BE-0177 | 40 | 162300 | 216500 | 103000 | Marshalling Box | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9105 | 162300 | 216500 | 103000 | ETS-05 | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-IP-9106-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 2 | PS5-79-BE-0177 | 40 | 162300 | 216500 | 103000 | Marshalling Box | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9106 | 162300 | 216500 | 103000 | ETS-05 | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-TE-0175-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 124 | PS5-79-IG-0006 | 37 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0175 | 233965 | 166653 | 101323 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | 2nd Sensor on Pig Launcher | 01 | nVent
PS5-79-TE-0176-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 125 | PS5-79-IG-0006 | 38 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0176 | 235030 | 166577 | 101403 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | 2nd Sensor on Pig Launcher | 01 | nVent
PS5-79-TE-0178-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 118 | PS5-79-IG-0006 | 39 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0178 | 234537 | 174668 | 101310 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | 2nd Sensor on Pig Launcher | 01 | nVent
PS5-79-TE-0177-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 119 | PS5-79-IG-0006 | 40 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0177 | 233937 | 174668 | 101310 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | 2nd Sensor on Pig Launcher | 01 | nVent
| Page 17 | Mr Amruth Anarasi | MENTION CO-ORDINATE VALUES WITHOUT ANY DECIMALS (TYP.) | Comment accepted and incorporated | Mark Russell | 10/04/2025 | C
| Page 17 | Mr Amruth Anarasi | TYPICAL COMMENTS: 1.PE CABLES SHALL BE TAGED AS "PSX-79-IG-0001-CGXX". 2.FOR CONSISTENCY, ALL CO-ORDINATES SHOULD BE WITHOUT DECIMALS. 3.ALL SAMPLING CABINETS CABLE, JB & RTD TAGS SHALL BE AS PER SAMPLING TAG DETAILS. 4.IN REMARK COLUMN ADD WHICH CABLES BELONGS TO EXPORT PUMPS, SAMPLING CABINETS | Comment accepted and incorporated | Mark Russell | 10/04/2025 | C

## Electrical Cables
Cable No. | Voltage Grade | Type | System Voltage | Cores | Size (mm²) | Volt Drop (V) | Volt Drop (%) | Length (m) | Tag No. | CB No. | North | East | Elevation | Description | Location | Gland Type | Entry Thread | Tag No. | North | East | Elevation | Description | Location | Gland Type | Entry Thread | Cable Routing Drawing | Outer Diameter (mm) | Remarks | Rev | DPS
PS5-79-IG-0001-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,12 | 0,03 | 5 | PS5-79-IV-0001 | - | 244467 | 270700 | 100000 | 63 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0001 | 244467 | 270700 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0002-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,16 | 0,04 | 5 | PS5-79-IV-0002 | - | 236950 | 270400 | 100000 | 100 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0002 | 236950 | 270400 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0003-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,16 | 0,04 | 5 | PS5-79-IV-0003 | - | 181573 | 278351 | 100000 | 63 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0003 | 181573 | 278351 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0004-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,12 | 0,03 | 5 | PS5-79-IV-0004 | - | 181572 | 283768 | 100001 | 63 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0004 | 181572 | 283768 | 100001 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0005-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,08 | 0,02 | 5 | PS5-79-IV-0005 | - | 181573 | 289184 | 100001 | 100 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0005 | 181573 | 289184 | 100001 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0006-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,28 | 0,07 | 5 | PS5-79-IV-0006 | - | 188771 | 235993 | 100000 | 63 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0006 | 188771 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0007-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,24 | 0,06 | 5 | PS5-79-IV-0007 | - | 183354 | 235993 | 100000 | 100 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0007 | 183354 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0008-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,28 | 0,07 | 5 | PS5-79-IV-0008 | - | 177937 | 235993 | 100000 | 100 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0008 | 177937 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0009-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,16 | 0,04 | 5 | PS5-79-IV-0009 | - | 188771 | 231193 | 100000 | 100 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0009 | 188771 | 231193 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0010-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,28 | 0,07 | 5 | PS5-79-IV-0010 | - | 183354 | 231193 | 100000 | 100 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0010 | 183354 | 231193 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0011-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,12 | 0,03 | 5 | PS5-79-IV-0011 | - | 187682 | 327500 | 100150 | 100 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0011 | 187682 | 327500 | 100150 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0012-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 4C | 95 | 0,2 | 0,05 | 5 | PS5-79-IV-0012 | - | 237233 | 138100 | 100000 | 100 kVA Transformer | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0012 | 237233 | 138100 | 100000 | Heat Tracing Panel | Field | SIND M50-Metal-Gland | M50 | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
PS5-79-IG-0001-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0001 | - | 244467 | 270700 | 100000 | 63 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0001 | 244467 | 270700 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0002-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0002 | - | 236950 | 270400 | 100000 | 100 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0002 | 236950 | 270400 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0003-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0003 | - | 181573 | 278351 | 100000 | 63 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0003 | 181573 | 278351 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0004-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0004 | - | 181572 | 283768 | 100001 | 63 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0004 | 181572 | 283768 | 100001 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0005-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0005 | - | 181573 | 289184 | 100001 | 100 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0005 | 181573 | 289184 | 100001 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0006-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0006 | - | 188771 | 235993 | 100000 | 63 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0006 | 188771 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0007-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0007 | - | 183354 | 235993 | 100000 | 100 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0007 | 183354 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0008-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0008 | - | 177937 | 235993 | 100000 | 100 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0008 | 177937 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0009-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0009 | - | 188771 | 231193 | 100000 | 100 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0009 | 188771 | 231193 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0010-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0010 | - | 183354 | 231193 | 100000 | 100 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0010 | 183354 | 231193 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0011-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0011 | - | 187682 | 327500 | 100150 | 100 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0011 | 187682 | 327500 | 100150 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0012-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC | 1C | 95 | - | - | 5 | PS5-79-IV-0012 | - | 237233 | 138100 | 100000 | 100 kVA Transformer | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0012 | 237233 | 138100 | 100000 | Heat Tracing Panel | Field | SIND M25-Metal-Gland-PE | M25 | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
PS5-79-IG-0001-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0001 | - | 244467 | 270700 | 100000 | 63 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0001 | 244467 | 270700 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0002-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0002 | - | 236950 | 270400 | 100000 | 100 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0002 | 236950 | 270400 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0003-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0003 | - | 181573 | 278351 | 100000 | 63 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0003 | 181573 | 278351 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0004-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0004 | - | 181572 | 283768 | 100001 | 63 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0004 | 181572 | 283768 | 100001 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0005-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0005 | - | 181573 | 289184 | 100001 | 100 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0005 | 181573 | 289184 | 100001 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0006-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0006 | - | 188771 | 235993 | 100000 | 63 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0006 | 188771 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0007-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0007 | - | 183354 | 235993 | 100000 | 100 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0007 | 183354 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0008-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0008 | - | 177937 | 235993 | 100000 | 100 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0008 | 177937 | 235993 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0009-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0009 | - | 188771 | 231193 | 100000 | 100 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0009 | 188771 | 231193 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0010-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0010 | - | 183354 | 231193 | 100000 | 100 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0010 | 183354 | 231193 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0011-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0011 | - | 187682 | 327500 | 100150 | 100 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0011 | 187682 | 327500 | 100150 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-IG-0012-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 6 | PS5-79-IV-0012 | - | 237233 | 138100 | 100000 | 100 kVA Transformer | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0012 | 237233 | 138100 | 100000 | Heat Tracing Panel | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
PS5-79-BE-0316-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,645 | 1,15 | 88 | PS5-79-IG-0001 | 1 | 244467 | 270700 | 270700 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0316 | 243338 | 219996 | 101197 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0315-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,714 | 1,18 | 87 | PS5-79-IG-0001 | 2 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0315 | 243338 | 223504 | 101197 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0168-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,506 | 0,22 | 84 | PS5-79-IG-0001 | 3 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0168 | 241959 | 220525 | 102519 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0170-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,506 | 0,22 | 84 | PS5-79-IG-0001 | 4 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0170 | 241959 | 223025 | 102519 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0163-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,564 | 0,68 | 76 | PS5-79-IG-0001 | 5 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0163 | 231939 | 222100 | 107461 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0167-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,276 | 0,12 | 84 | PS5-79-IG-0001 | 6 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0167 | 240543 | 220525 | 101466 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-SP-0167-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,28 | 0,12 | 4 | PS5-79-BE-0167 | 6 | 240543 | 220525 | 101466 | Heat Tracing Junction Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0167 | 243286 | 220525 | 102148 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01
PS5-79-BE-0169-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,28 | 0,12 | 83 | PS5-79-IG-0001 | 7 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0169 | 240543 | 223025 | 101466 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-SP-0169-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,28 | 0,12 | 4 | PS5-79-BE-0169 | 7 | 240543 | 223025 | 101466 | Heat Tracing Junction Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0169 | 243286 | 223025 | 102148 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0159-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,28 | 0,99 | 82 | PS5-79-IG-0001 | 8 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0159 | 240568 | 223373 | 102718 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0164-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,19 | 1,82 | 82 | PS5-79-IG-0001 | 9 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0164 | 239353 | 220933 | 102111 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0151-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,02 | 0,88 | 75 | PS5-79-IG-0001 | 10 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0151 | 231939 | 223940 | 107461 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0356-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,48 | 0,21 | 87 | PS5-79-IG-0001 | 11 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0356 | 239409 | 227070 | 101525 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0206-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,52 | 1,53 | 71 | PS5-79-IG-0001 | 12 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0206 | 230410 | 222103 | 105090 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0148-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,23 | 0,97 | 80 | PS5-79-IG-0001 | 13 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0148 | 234264 | 218700 | 100757 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0314-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,33 | 0,58 | 79 | PS5-79-IG-0001 | 14 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0314 | 234664 | 223790 | 100810 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0149-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,17 | 0,51 | 79 | PS5-79-IG-0001 | 15 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0149 | 234664 | 223841 | 100864 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0234-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,45 | 0,63 | 85 | PS5-79-IG-0001 | 16 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0234 | 235900 | 228531 | 101214 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0114-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,44 | 0,19 | 83 | PS5-79-IG-0001 | 17 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0114 | 235643 | 227096 | 101122 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0165-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,41 | 0,18 | 73 | PS5-79-IG-0001 | 18 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0165 | 232390 | 222024 | 105269 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0166-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,30 | 1,00 | 83 | PS5-79-IG-0001 | 19 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0166 | 240568 | 220127 | 102718 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0157-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,41 | 0,18 | 72 | PS5-79-IG-0001 | 20 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0157 | 232390 | 224016 | 105269 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0153-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,16 | 1,81 | 81 | PS5-79-IG-0001 | 21 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0153 | 239353 | 222643 | 102111 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0313-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,02 | 0,88 | 81 | PS5-79-IG-0001 | 22 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0313 | 234664 | 218200 | 100810 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0188-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,88 | 2,99 | 71 | PS5-79-IG-0001 | 23 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0188 | 229077 | 221200 | 103567 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0202-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,58 | 1,99 | 62 | PS5-79-IG-0001 | 24 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0202 | 230815 | 233080 | 101207 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0103-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,35 | 1,02 | 52 | PS5-79-IG-0001 | 25 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0103 | 230928 | 240000 | 103807 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0317-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,66 | 2,46 | 50 | PS5-79-IG-0001 | 26 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0317 | 229998 | 240601 | 103757 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0306-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,13 | 1,36 | 51 | PS5-79-IG-0001 | 27 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0306 | 230663 | 240870 | 103807 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0197-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,06 | 2,20 | 52 | PS5-79-IG-0001 | 28 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0197 | 230924 | 242238 | 101694 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-71-BE-0361-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,31 | 0,57 | 85 | PS5-79-IG-0001 | 31 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-71-BE-0361 | 238800 | 226900 | 101600 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-BE-0181-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,66 | 0,72 | 69 | PS5-79-IG-0002 | 1 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0181 | 240997 | 238208 | 101917 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0184-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,71 | 3,35 | 69 | PS5-79-IG-0002 | 2 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0184 | 240723 | 238999 | 101200 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0302-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,10 | 0,48 | 69 | PS5-79-IG-0002 | 3 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0302 | 241490 | 240340 | 100830 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0185-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,68 | 0,73 | 65 | PS5-79-IG-0002 | 4 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0185 | 240723 | 242400 | 101200 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0182-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,54 | 0,67 | 63 | PS5-79-IG-0002 | 5 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0182 | 240980 | 243177 | 101917 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0303-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,06 | 0,46 | 65 | PS5-79-IG-0002 | 6 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0303 | 241500 | 243740 | 100830 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0304-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,92 | 0,40 | 57 | PS5-79-IG-0002 | 7 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0304 | 241500 | 256840 | 100830 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0325-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,37 | 0,16 | 74 | PS5-79-IG-0002 | 8 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0325 | 241877 | 253180 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0311-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,63 | 0,71 | 73 | PS5-79-IG-0002 | 9 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0311 | 240750 | 252298 | 101265 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0312-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,64 | 0,28 | 71 | PS5-79-IG-0002 | 10 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0312 | 240755 | 251693 | 101207 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0173-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,37 | 0,16 | 62 | PS5-79-IG-0002 | 11 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0173 | 235874 | 240560 | 101330 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0183-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,89 | 0,82 | 59 | PS5-79-IG-0002 | 12 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0183 | 234147 | 242200 | 101086 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0355-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,24 | 1,41 | 68 | PS5-79-IG-0002 | 13 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0355 | 235800 | 250475 | 100957 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0354-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,08 | 0,47 | 69 | PS5-79-IG-0002 | 14 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0354 | 235750 | 250580 | 101012 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0201-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,76 | 2,07 | 43 | PS5-79-IG-0002 | 15 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0201 | 230302 | 252108 | 102757 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0193-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,27 | 1,42 | 37 | PS5-79-IG-0002 | 16 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0193 | 228750 | 256760 | 103807 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0322-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,96 | 1,72 | 38 | PS5-79-IG-0002 | 17 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0322 | 228250 | 257200 | 101810 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0192-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,97 | 1,29 | 53 | PS5-79-IG-0002 | 18 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0192 | 235536 | 253763 | 101394 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0191-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,62 | 0,27 | 53 | PS5-79-IG-0002 | 19 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0191 | 235536 | 253839 | 101480 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0346-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,13 | 0,49 | 52 | PS5-79-IG-0002 | 20 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0346 | 235900 | 255166 | 101413 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0172-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,79 | 0,78 | 59 | PS5-79-IG-0002 | 21 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0172 | 240997 | 254708 | 101917 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0179-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,17 | 0,51 | 56 | PS5-79-IG-0002 | 22 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0179 | 240469 | 255500 | 101201 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0326-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,32 | 0,14 | 75 | PS5-79-IG-0002 | 23 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0326 | 243390 | 253155 | 101352 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0180-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,10 | 0,48 | 53 | PS5-79-IG-0002 | 24 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0180 | 240469 | 258900 | 101201 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0174-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,31 | 0,57 | 54 | PS5-79-IG-0002 | 25 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0174 | 240980 | 259677 | 101917 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0305-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,85 | 0,37 | 53 | PS5-79-IG-0002 | 26 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0305 | 241490 | 260240 | 100830 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0199-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,63 | 0,71 | 16 | PS5-79-IG-0002 | 27 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0199 | 231080 | 267750 | 101207 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0187-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,50 | 0,65 | 13 | PS5-79-IG-0002 | 28 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0187 | 230209 | 271970 | 100932 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0190-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,13 | 0,49 | 12 | PS5-79-IG-0002 | 29 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0190 | 231079 | 272840 | 100932 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-71-BE-0363-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,15 | 0,50 | 74 | PS5-79-IG-0002 | 31 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-71-BE-0363 | 242800 | 253200 | 101400 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-BE-0023-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,85 | 0,37 | 104 | PS5-79-IG-0003 | 1 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0023 | 220640 | 290532 | 101212 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0278-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 6,26 | 2,72 | 108 | PS5-79-IG-0003 | 2 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0278 | 226338 | 289066 | 101180 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0307-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,44 | 1,93 | 104 | PS5-79-IG-0003 | 3 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0307 | 220400 | 290532 | 101469 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0198-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,30 | 1,87 | 103 | PS5-79-IG-0003 | 4 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0198 | 220150 | 290532 | 100989 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0046-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,78 | 0,34 | 103 | PS5-79-IG-0003 | 5 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0046 | 220400 | 290532 | 101212 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0195-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,52 | 1,53 | 102 | PS5-79-IG-0003 | 6 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0195 | 219400 | 290480 | 101188 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0252-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,64 | 0,28 | 95 | PS5-79-IG-0003 | 7 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0252 | 212140 | 290532 | 101212 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0253-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,48 | 0,21 | 95 | PS5-79-IG-0003 | 8 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0253 | 211900 | 290532 | 101212 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0200-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,84 | 0,80 | 90 | PS5-79-IG-0003 | 9 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0200 | 211490 | 288175 | 103157 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0194-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,84 | 0,80 | 90 | PS5-79-IG-0003 | 10 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0194 | 211246 | 288425 | 103262 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0246-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,38 | 0,60 | 89 | PS5-79-IG-0003 | 11 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0246 | 210672 | 288763 | 103144 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0189-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 9,98 | 4,34 | 91 | PS5-79-IG-0003 | 12 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0189 | 204848 | 288289 | 105732 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0210-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,87 | 2,55 | 65 | PS5-79-IG-0003 | 13 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0210 | 196946 | 266438 | 105435 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0186-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 9,48 | 4,12 | 87 | PS5-79-IG-0003 | 14 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0186 | 204405 | 291103 | 105732 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0279-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,22 | 2,27 | 99 | PS5-79-IG-0003 | 15 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0279 | 199010 | 286722 | 100981 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0260-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,92 | 3,01 | 61 | PS5-79-IG-0003 | 16 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0260 | 197783 | 272860 | 100932 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0211-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,08 | 3,08 | 64 | PS5-79-IG-0003 | 17 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0211 | 196845 | 275099 | 105806 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0196-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,43 | 3,23 | 76 | PS5-79-IG-0003 | 18 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0196 | 205676 | 277859 | 101382 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0244-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,34 | 3,19 | 77 | PS5-79-IG-0003 | 19 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0244 | 205976 | 277870 | 101407 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0238-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,03 | 3,49 | 93 | PS5-79-IG-0003 | 20 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0238 | 217399 | 271620 | 100907 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0348-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,71 | 1,18 | 131 | PS5-79-IG-0003 | 21 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0348 | 219346 | 254053 | 102535 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0352-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,66 | 2,46 | 142 | PS5-79-IG-0003 | 22 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0352 | 218159 | 247962 | 108511 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0242-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,37 | 0,16 | 157 | PS5-79-IG-0003 | 23 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0242 | 220056 | 228161 | 101110 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0109-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,31 | 0,57 | 144 | PS5-79-IG-0003 | 24 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0109 | 222085 | 240958 | 100705 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0113-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,62 | 0,27 | 145 | PS5-79-IG-0003 | 25 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0113 | 222086 | 238208 | 101375 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0106-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,84 | 0,80 | 146 | PS5-79-IG-0003 | 26 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0106 | 219440 | 238342 | 102285 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0351-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,68 | 3,34 | 160 | PS5-79-IG-0003 | 27 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0351 | 220339 | 228361 | 110926 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0243-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,35 | 0,15 | 141 | PS5-79-IG-0003 | 28 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0243 | 217157 | 247498 | 101110 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-60-BE-0365-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,31 | 0,57 | 85 | PS5-79-IG-0003 | 31 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0365 | 215500 | 312500 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-BE-0280-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,86 | 3,85 | 79 | PS5-79-IG-0004 | 1 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0280 | 215228 | 299886 | 101181 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0331-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,52 | 0,66 | 75 | PS5-79-IG-0004 | 2 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0331 | 215614 | 303612 | 101575 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0327-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,62 | 0,27 | 73 | PS5-79-IG-0004 | 3 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0327 | 215360 | 304680 | 101934 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0266-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,24 | 0,54 | 73 | PS5-79-IG-0004 | 4 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0266 | 214054 | 304944 | 100997 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0265-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,76 | 0,33 | 72 | PS5-79-IG-0004 | 5 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0265 | 213097 | 303800 | 100793 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0212-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,68 | 0,73 | 16 | PS5-79-IG-0004 | 6 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0212 | 179511 | 288596 | 107559 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0049-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,99 | 0,43 | 76 | PS5-79-IG-0004 | 7 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0049 | 211500 | 298728 | 100859 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0329-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,14 | 0,93 | 67 | PS5-79-IG-0004 | 8 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0329 | 206506 | 308300 | 100862 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0285-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,09 | 1,78 | 65 | PS5-79-IG-0004 | 9 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0285 | 200713 | 300386 | 100981 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0220-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,61 | 0,70 | 58 | PS5-79-IG-0004 | 10 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0220 | 199000 | 309240 | 103413 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0217-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,77 | 0,77 | 65 | PS5-79-IG-0004 | 11 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0217 | 198698 | 316234 | 103413 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0219-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,79 | 0,78 | 54 | PS5-79-IG-0004 | 12 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0219 | 197750 | 306994 | 104165 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0237-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,81 | 0,35 | 52 | PS5-79-IG-0004 | 13 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0237 | 166750 | 305025 | 99503 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-SP-0237-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,81 | 0,35 | 4 | PS5-79-BE-0237 | 13 | 166750 | 305025 | 99503 | Heat Tracing Junction Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0237 | 165225 | 305000 | 99500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0282-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,58 | 1,12 | 43 | PS5-79-IG-0004 | 14 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0282 | 185063 | 304826 | 100981 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0213-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,76 | 0,35 | 34 | PS5-79-IG-0004 | 15 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0213 | 177353 | 299849 | 109584 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0086-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,51 | 0,22 | 48 | PS5-79-IG-0004 | 16 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0086 | 167025 | 303869 | 101940 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0214-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,44 | 1,93 | 48 | PS5-79-IG-0004 | 17 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0214 | 167400 | 304590 | 102299 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0283-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,71 | 1,18 | 44 | PS5-79-IG-0004 | 18 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0283 | 185685 | 305326 | 100981 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0092-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,76 | 0,33 | 68 | PS5-79-IG-0004 | 19 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0092 | 164079 | 303569 | 101944 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0216-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,02 | 0,88 | 67 | PS5-79-IG-0004 | 20 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0216 | 163800 | 304363 | 100526 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0215-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,96 | 0,85 | 68 | PS5-79-IG-0004 | 21 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0215 | 162600 | 304254 | 100526 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0099-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,12 | 2,66 | 71 | PS5-79-IG-0004 | 22 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0099 | 162045 | 301748 | 101355 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0171-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,98 | 0,86 | 74 | PS5-79-IG-0004 | 23 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0171 | 156950 | 304072 | 101055 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0264-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,24 | 0,54 | 73 | PS5-79-IG-0004 | 24 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0264 | 213090 | 303800 | 101027 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0281-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,67 | 0,29 | 22 | PS5-79-IG-0004 | 25 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0281 | 182760 | 297505 | 100999 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0284-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,71 | 0,31 | 24 | PS5-79-IG-0004 | 26 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0284 | 183263 | 298176 | 100999 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-60-BE-0366-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,38 | 0,60 | 90 | PS5-79-IG-0004 | 28 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0366 | 215500 | 321000 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-BE-0332-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,82 | 0,79 | 90 | PS5-79-IG-0005 | 1 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0332 | 215614 | 312112 | 101575 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0330-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,74 | 0,32 | 87 | PS5-79-IG-0005 | 2 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0330 | 215360 | 313180 | 101934 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0269-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,50 | 0,65 | 87 | PS5-79-IG-0005 | 3 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0269 | 214054 | 313444 | 100997 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0267-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,50 | 0,65 | 88 | PS5-79-IG-0005 | 4 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0267 | 213090 | 312300 | 101027 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0268-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,92 | 0,40 | 87 | PS5-79-IG-0005 | 5 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0268 | 213097 | 312300 | 100793 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0334-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,63 | 0,71 | 81 | PS5-79-IG-0005 | 6 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0334 | 215614 | 320612 | 101575 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0333-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,64 | 0,28 | 78 | PS5-79-IG-0005 | 7 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0333 | 215360 | 321680 | 101934 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0272-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,33 | 0,58 | 78 | PS5-79-IG-0005 | 8 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0272 | 214054 | 321944 | 100997 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0270-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,33 | 0,58 | 78 | PS5-79-IG-0005 | 9 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0270 | 213090 | 320800 | 101027 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0271-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,83 | 0,36 | 77 | PS5-79-IG-0005 | 10 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0271 | 213097 | 320800 | 100793 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0335-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,70 | 0,74 | 85 | PS5-79-IG-0005 | 11 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0335 | 215614 | 329112 | 101575 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0339-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,74 | 0,32 | 88 | PS5-79-IG-0005 | 12 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0339 | 215350 | 330180 | 101934 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0275-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,45 | 0,63 | 85 | PS5-79-IG-0005 | 13 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0275 | 214054 | 330444 | 100997 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0273-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,40 | 0,61 | 83 | PS5-79-IG-0005 | 14 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0273 | 213090 | 329300 | 101027 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0274-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,87 | 0,38 | 83 | PS5-79-IG-0005 | 15 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0274 | 213097 | 329300 | 100793 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0328-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,59 | 1,56 | 76 | PS5-79-IG-0005 | 16 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0328 | 206562 | 316800 | 100862 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0061-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,34 | 1,45 | 73 | PS5-79-IG-0005 | 17 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0061 | 206562 | 325300 | 100862 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0218-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,28 | 0,97 | 65 | PS5-79-IG-0005 | 18 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0218 | 197950 | 315225 | 104093 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0229-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,25 | 0,98 | 81 | PS5-79-IG-0005 | 19 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0229 | 199000 | 343304 | 103413 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0223-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,02 | 0,88 | 61 | PS5-79-IG-0005 | 20 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0223 | 197750 | 323994 | 104165 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0224-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,79 | 0,78 | 64 | PS5-79-IG-0005 | 21 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0224 | 199000 | 326304 | 103413 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0221-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,96 | 0,85 | 72 | PS5-79-IG-0005 | 22 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0221 | 198698 | 333234 | 103413 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0235-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,91 | 2,57 | 69 | PS5-79-IG-0005 | 23 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0235 | 197950 | 332136 | 104155 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0222-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,35 | 1,02 | 68 | PS5-79-IG-0005 | 24 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0222 | 197950 | 332225 | 104094 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0350-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,12 | 2,66 | 71 | PS5-79-IG-0005 | 25 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0350 | 197550 | 335000 | 104155 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0228-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,58 | 1,12 | 77 | PS5-79-IG-0005 | 26 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0228 | 197750 | 340995 | 104165 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0236-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,03 | 2,62 | 60 | PS5-79-IG-0005 | 27 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0236 | 197750 | 323405 | 104155 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-60-BE-0367-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,33 | 0,58 | 86 | PS5-79-IG-0005 | 28 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0367 | 500000 | 329500 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-BE-0136-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 5,43 | 2,36 | 111 | PS5-79-IG-0009 | 1 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0136 | 174539 | 160699 | 101299 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0027-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 4,81 | 2,09 | 109 | PS5-79-IG-0009 | 2 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0027 | 183200 | 167000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0039-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,28 | 2,73 | 87 | PS5-79-IG-0009 | 3 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0039 | 183065 | 175000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0037-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,96 | 3,46 | 82 | PS5-79-IG-0009 | 4 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0037 | 188029 | 175000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0025-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 5,29 | 2,30 | 91 | PS5-79-IG-0009 | 5 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0025 | 191636 | 166696 | 101455 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0343-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,91 | 2,57 | 109 | PS5-79-IG-0009 | 6 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0343 | 188000 | 151456 | 100981 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0118-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 6,26 | 2,72 | 96 | PS5-79-IG-0009 | 7 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0118 | 201450 | 160299 | 100932 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0137-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,34 | 3,19 | 89 | PS5-79-IG-0009 | 8 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0137 | 197700 | 163721 | 100831 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0024-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 5,70 | 2,48 | 87 | PS5-79-IG-0009 | 9 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0024 | 196183 | 167000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0150-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,46 | 0,20 | 99 | PS5-79-IG-0009 | 10 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0150 | 172449 | 193420 | 100933 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0203-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,21 | 3,57 | 72 | PS5-79-IG-0009 | 11 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0203 | 197324 | 179771 | 103496 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0204-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,73 | 3,36 | 70 | PS5-79-IG-0009 | 12 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0204 | 197324 | 179771 | 103496 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0262-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,91 | 3,44 | 74 | PS5-79-IG-0009 | 13 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0262 | 198500 | 180769 | 100932 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0102-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,14 | 3,54 | 75 | PS5-79-IG-0009 | 14 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0102 | 201400 | 180806 | 102118 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0081-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,58 | 3,73 | 85 | PS5-79-IG-0009 | 15 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0081 | 202600 | 176506 | 104208 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0036-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 5,57 | 2,42 | 85 | PS5-79-IG-0009 | 16 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0036 | 204700 | 175000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0066-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,18 | 2,25 | 73 | PS5-79-IG-0009 | 17 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0066 | 183217 | 193840 | 101950 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0067-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,30 | 3,61 | 82 | PS5-79-IG-0009 | 18 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0067 | 181159 | 188775 | 102557 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0245-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,79 | 2,95 | 86 | PS5-79-IG-0009 | 19 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0245 | 177292 | 186398 | 100709 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0134-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,31 | 0,57 | 92 | PS5-79-IG-0009 | 20 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0134 | 174474 | 188800 | 101105 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0063-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,72 | 3,79 | 91 | PS5-79-IG-0009 | 21 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0063 | 173422 | 188775 | 102557 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0154-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,97 | 1,29 | 98 | PS5-79-IG-0009 | 22 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0154 | 172689 | 192677 | 101185 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0319-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,18 | 2,25 | 77 | PS5-79-IG-0009 | 23 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0319 | 196925 | 175793 | 103450 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0290-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,16 | 2,68 | 101 | PS5-79-IG-0009 | 24 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0290 | 171233 | 194182 | 100325 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0152-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,44 | 0,19 | 100 | PS5-79-IG-0009 | 25 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0152 | 172176 | 193950 | 100853 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0002-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,40 | 0,61 | 83 | PS5-79-IG-0009 | 26 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0002 | 171084 | 195053 | 101124 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0005-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,53 | 0,23 | 102 | PS5-79-IG-0009 | 27 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0005 | 167902 | 193341 | 101931 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0146-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,70 | 0,74 | 84 | PS5-79-IG-0009 | 28 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0146 | 168255 | 196163 | 101848 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0041-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,30 | 3,61 | 86 | PS5-79-IG-0009 | 29 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0041 | 166404 | 196138 | 101856 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0135-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,63 | 1,58 | 102 | PS5-79-IG-0009 | 30 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0135 | 165955 | 191157 | 101225 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0239-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,12 | 0,05 | 104 | PS5-79-IG-0009 | 31 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0239 | 164054 | 191175 | 100815 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-IP-9901-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 9,82 | 4,27 | 107 | PS5-79-IG-0009 | 40 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9901 | 162500 | 192500 | 103000 | Marshalling Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-IP-9101-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 9,82 | 4,27 | 2 | PS5-79-IP-9901 | 40 | 188770 | 235992 | 100000 | Marshalling Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9101 | 162500 | 192500 | 103000 | ETS-05 | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-IP-9102-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 9,82 | 4,27 | 2 | PS5-79-IP-9901 | 40 | 188770 | 235992 | 100000 | Marshalling Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9102 | 162500 | 192500 | 103000 | ETS-05 | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-BE-0247-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,45 | 1,50 | 62 | PS5-79-IG-0007 | 1 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0247 | 208675 | 209077 | 100981 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0084-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,51 | 2,83 | 63 | PS5-79-IG-0007 | 2 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0084 | 207145 | 202000 | 103808 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0090-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,74 | 2,93 | 59 | PS5-79-IG-0007 | 3 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0090 | 205689 | 204200 | 103858 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0085-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 6,28 | 2,73 | 102 | PS5-79-IG-0007 | 4 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0085 | 209345 | 195451 | 101459 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0082-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,54 | 3,28 | 85 | PS5-79-IG-0007 | 5 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0082 | 202600 | 185283 | 101458 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0101-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,34 | 3,19 | 67 | PS5-79-IG-0007 | 6 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0101 | 201400 | 192750 | 101508 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0156-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,32 | 0,14 | 73 | PS5-79-IG-0007 | 7 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0156 | 172176 | 205950 | 100853 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0107-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,99 | 1,30 | 61 | PS5-79-IG-0007 | 8 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0107 | 202295 | 197899 | 101586 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0020-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,87 | 0,38 | 60 | PS5-79-IG-0007 | 9 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0020 | 202600 | 200539 | 101111 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0147-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,61 | 1,57 | 62 | PS5-79-IG-0007 | 10 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0147 | 200200 | 196749 | 101306 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0043-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,49 | 1,95 | 61 | PS5-79-IG-0007 | 11 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0043 | 200200 | 196748 | 100899 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0344-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,30 | 2,74 | 60 | PS5-79-IG-0007 | 12 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0344 | 199150 | 197250 | 100957 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0019-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,54 | 0,67 | 56 | PS5-79-IG-0007 | 13 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0019 | 200200 | 202140 | 101204 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0100-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,64 | 2,45 | 52 | PS5-79-IG-0007 | 14 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0100 | 201095 | 205400 | 102118 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0112-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,62 | 2,88 | 59 | PS5-79-IG-0007 | 15 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0112 | 196423 | 199581 | 105256 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0068-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,17 | 1,38 | 74 | PS5-79-IG-0007 | 16 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0068 | 187776 | 194297 | 104013 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0042-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,10 | 3,52 | 73 | PS5-79-IG-0007 | 17 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0042 | 188219 | 196139 | 102051 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0121-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,11 | 3,09 | 65 | PS5-79-IG-0007 | 18 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0121 | 187776 | 198775 | 105458 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0072-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,05 | 3,50 | 71 | PS5-79-IG-0007 | 19 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0072 | 181159 | 200776 | 102557 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0116-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,37 | 0,16 | 65 | PS5-79-IG-0007 | 20 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0116 | 186955 | 198357 | 103990 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0145-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,38 | 0,60 | 87 | PS5-79-IG-0007 | 21 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0145 | 174474 | 200800 | 101105 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0155-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,44 | 0,19 | 93 | PS5-79-IG-0007 | 22 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0155 | 172449 | 205420 | 100933 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0071-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,26 | 3,59 | 86 | PS5-79-IG-0007 | 23 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0071 | 173422 | 200775 | 102557 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0083-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,23 | 1,84 | 66 | PS5-79-IG-0007 | 24 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0083 | 202600 | 196129 | 101458 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0291-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,51 | 1,96 | 74 | PS5-79-IG-0007 | 25 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0291 | 171200 | 206167 | 100325 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0003-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,22 | 0,53 | 73 | PS5-79-IG-0007 | 26 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0003 | 171084 | 207053 | 101124 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0143-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,50 | 0,65 | 74 | PS5-79-IG-0007 | 27 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0143 | 168255 | 208165 | 101848 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0059-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,36 | 3,20 | 76 | PS5-79-IG-0007 | 28 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0059 | 166234 | 208140 | 101856 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0006-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,51 | 0,22 | 96 | PS5-79-IG-0007 | 29 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0006 | 167902 | 205341 | 101931 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0144-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,42 | 1,05 | 99 | PS5-79-IG-0007 | 30 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0144 | 165955 | 203157 | 101225 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0240-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,12 | 0,05 | 101 | PS5-79-IG-0007 | 31 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0240 | 164054 | 203175 | 100815 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-IP-9902-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 9,18 | 3,99 | 100 | PS5-79-IG-0007 | 40 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9902 | 162300 | 204500 | 103000 | Marshalling Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-IP-9103-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 9,18 | 3,99 | 2 | PS5-79-IP-9902 | 40 | 162300 | 204500 | 103000 | Marshalling Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9103 | 162300 | 204500 | 103000 | ETS-05 | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-IP-9104-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 9,18 | 3,99 | 2 | PS5-79-IP-9902 | 40 | 162300 | 204500 | 103000 | Marshalling Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9104 | 162300 | 204500 | 103000 | ETS-05 | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-BE-0241-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,09 | 0,04 | 87 | PS5-79-IG-0008 | 1 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0241 | 164054 | 215175 | 100815 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0208-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,34 | 2,32 | 60 | PS5-79-IG-0008 | 2 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0208 | 196823 | 202422 | 103897 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0292-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,44 | 1,93 | 73 | PS5-79-IG-0008 | 3 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0292 | 171157 | 218205 | 100325 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0058-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,45 | 3,24 | 77 | PS5-79-IG-0008 | 4 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0058 | 166404 | 220137 | 101856 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0140-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,52 | 0,66 | 75 | PS5-79-IG-0008 | 5 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0140 | 168255 | 220162 | 101848 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0004-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,22 | 0,53 | 73 | PS5-79-IG-0008 | 6 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0004 | 171084 | 219053 | 101124 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0007-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,48 | 0,21 | 92 | PS5-79-IG-0008 | 7 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0007 | 167902 | 217341 | 101931 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0161-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,30 | 0,13 | 72 | PS5-79-IG-0008 | 8 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0161 | 172176 | 217950 | 100853 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0139-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,82 | 3,40 | 69 | PS5-79-IG-0008 | 9 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0139 | 177600 | 222875 | 100911 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0162-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,29 | 1,43 | 73 | PS5-79-IG-0008 | 10 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0162 | 172689 | 216677 | 101185 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0074-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,18 | 3,12 | 75 | PS5-79-IG-0008 | 11 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0074 | 173422 | 212775 | 102557 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0142-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,20 | 0,52 | 76 | PS5-79-IG-0008 | 12 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0142 | 174474 | 212800 | 101105 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0160-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,35 | 0,15 | 73 | PS5-79-IG-0008 | 13 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0160 | 172449 | 217420 | 100933 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0077-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,71 | 3,35 | 68 | PS5-79-IG-0008 | 14 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0077 | 181161 | 212775 | 102557 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0075-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,44 | 1,93 | 61 | PS5-79-IG-0008 | 15 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0075 | 183067 | 217840 | 101950 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0053-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,10 | 2,65 | 55 | PS5-79-IG-0008 | 16 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0053 | 188219 | 220137 | 102051 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0076-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,34 | 2,32 | 57 | PS5-79-IG-0008 | 17 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0076 | 187776 | 217027 | 104105 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0070-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,61 | 2,44 | 69 | PS5-79-IG-0008 | 18 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0070 | 183217 | 205840 | 101950 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0158-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,59 | 0,69 | 67 | PS5-79-IG-0008 | 19 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0158 | 186955 | 204702 | 103862 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0060-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,99 | 3,04 | 63 | PS5-79-IG-0008 | 20 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0060 | 188220 | 208140 | 102051 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0115-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,98 | 2,60 | 70 | PS5-79-IG-0008 | 21 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0115 | 187470 | 201639 | 105153 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0108-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,35 | 3,63 | 69 | PS5-79-IG-0008 | 22 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0108 | 187775 | 201639 | 105458 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0111-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,45 | 0,63 | 70 | PS5-79-IG-0008 | 23 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0111 | 187776 | 201639 | 105458 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0062-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,92 | 2,14 | 60 | PS5-79-IG-0008 | 24 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0062 | 192099 | 208343 | 104443 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0141-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,16 | 0,94 | 89 | PS5-79-IG-0008 | 25 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0141 | 165955 | 215157 | 101225 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0207-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,18 | 2,25 | 61 | PS5-79-IG-0008 | 26 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0207 | 196925 | 202422 | 103999 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0205-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,10 | 2,65 | 54 | PS5-79-IG-0008 | 27 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0205 | 197324 | 208877 | 104158 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0044-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,06 | 2,20 | 59 | PS5-79-IG-0008 | 28 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0044 | 200200 | 204201 | 101509 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0045-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,80 | 2,52 | 51 | PS5-79-IG-0008 | 29 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0045 | 200200 | 219527 | 101305 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0261-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,89 | 2,56 | 45 | PS5-79-IG-0008 | 30 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0261 | 198500 | 220750 | 100932 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0209-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,73 | 1,62 | 37 | PS5-79-IG-0008 | 31 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0209 | 196947 | 228659 | 104680 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-IP-9903-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,26 | 3,59 | 90 | PS5-79-IG-0008 | 40 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9903 | 162300 | 216500 | 103000 | Marshalling Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-IP-9105-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,26 | 3,59 | 2 | PS5-79-IP-9903 | 40 | 162300 | 216500 | 103000 | Marshalling Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9105 | 162300 | 216500 | 103000 | ETS-05 | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-IP-9106-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,26 | 3,59 | 2 | PS5-79-IP-9903 | 40 | 162300 | 216500 | 103000 | Marshalling Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9106 | 162300 | 216500 | 103000 | ETS-05 | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
PS5-79-BE-0064-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,18 | 3,12 | 127 | PS5-79-IG-0006 | 1 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0064 | 228214 | 165701 | 100715 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0057-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,67 | 1,16 | 129 | PS5-79-IG-0006 | 2 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0057 | 228213 | 165700 | 100689 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0021-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,94 | 3,45 | 119 | PS5-79-IG-0006 | 3 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0021 | 228571 | 167000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0128-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,47 | 1,51 | 128 | PS5-79-IG-0006 | 4 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0128 | 235019 | 171416 | 106386 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0008-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,99 | 0,43 | 123 | PS5-79-IG-0006 | 5 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0008 | 233210 | 167025 | 102000 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-SP-0008-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,99 | 0,43 | 4 | PS5-79-BE-0008 | 5 | 233210 | 167025 | 102000 | Heat Tracing Junction Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0008 | 236800 | 167050 | 101871 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0047-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,04 | 0,45 | 113 | PS5-79-IG-0006 | 6 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0047 | 228548 | 175025 | 101454 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0052-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 8,05 | 3,50 | 127 | PS5-79-IG-0006 | 7 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0052 | 229050 | 163348 | 101261 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0056-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,83 | 0,36 | 129 | PS5-79-IG-0006 | 8 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0056 | 231065 | 163375 | 101264 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0055-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,62 | 0,27 | 130 | PS5-79-IG-0006 | 9 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0055 | 232257 | 163475 | 101061 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0028-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,68 | 3,34 | 111 | PS5-79-IG-0006 | 10 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0028 | 228549 | 175000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0294-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 8,76 | 3,81 | 124 | PS5-79-IG-0006 | 11 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0294 | 234065 | 166653 | 101323 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0293-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 8,56 | 3,72 | 125 | PS5-79-IG-0006 | 12 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0293 | 234273 | 166647 | 101323 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0129-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,99 | 0,43 | 124 | PS5-79-IG-0006 | 13 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0129 | 234844 | 169860 | 104312 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0073-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,15 | 0,50 | 117 | PS5-79-IG-0006 | 14 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0073 | 228570 | 167025 | 101454 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0010-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,27 | 0,55 | 117 | PS5-79-IG-0006 | 15 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0010 | 233958 | 175025 | 102052 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-SP-0010-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,27 | 0,55 | 4 | PS5-79-BE-0010 | 15 | 233958 | 175025 | 102052 | Heat Tracing Junction Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0010 | 235900 | 175050 | 102185 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0124-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,11 | 2,22 | 126 | PS5-79-IG-0006 | 16 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0124 | 238800 | 168373 | 103338 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0295-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 8,12 | 3,53 | 119 | PS5-79-IG-0006 | 17 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0295 | 234437 | 174668 | 101310 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0030-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,31 | 3,18 | 111 | PS5-79-IG-0006 | 18 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0030 | 231955 | 178347 | 101332 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0127-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,12 | 2,66 | 118 | PS5-79-IG-0006 | 19 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0127 | 235418 | 174600 | 103736 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0051-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,25 | 0,98 | 113 | PS5-79-IG-0006 | 20 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0051 | 229877 | 176342 | 100778 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0032-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,64 | 0,28 | 113 | PS5-79-IG-0006 | 21 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0032 | 234577 | 178525 | 101132 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0033-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,76 | 0,33 | 112 | PS5-79-IG-0006 | 22 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0033 | 234421 | 178625 | 101332 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0126-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,87 | 0,38 | 126 | PS5-79-IG-0006 | 23 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0126 | 236689 | 170208 | 104335 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0125-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,06 | 1,33 | 128 | PS5-79-IG-0006 | 24 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0125 | 236600 | 170673 | 106169 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0011-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,70 | 0,74 | 137 | PS5-79-IG-0006 | 25 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0011 | 238298 | 165338 | 101175 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0301-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 8,03 | 3,49 | 118 | PS5-79-IG-0006 | 26 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0301 | 234237 | 174668 | 101310 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0001-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,56 | 0,68 | 127 | PS5-79-IG-0006 | 27 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0001 | 238100 | 168588 | 100857 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0009-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,68 | 0,74 | 121 | PS5-79-IG-0006 | 28 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0009 | 238100 | 173364 | 100857 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0014-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,68 | 0,73 | 122 | PS5-79-IG-0006 | 29 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0014 | 238553 | 174035 | 100955 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0034-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,83 | 3,84 | 110 | PS5-79-IG-0006 | 30 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0034 | 231955 | 178500 | 101484 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0353-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,12 | 0,05 | 116 | PS5-79-IG-0006 | 31 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0353 | 232858 | 175000 | 102038 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-71-BE-0362-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,47 | 0,64 | 96 | PS5-79-IG-0006 | 34 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-71-BE-0362 | 222100 | 238700 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-BE-0132-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,51 | 3,70 | 129 | PS5-79-IG-0010 | 1 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0132 | 224576 | 160480 | 103459 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0131-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,77 | 3,38 | 123 | PS5-79-IG-0010 | 2 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0131 | 224576 | 170627 | 103663 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0040-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,08 | 2,21 | 115 | PS5-79-IG-0010 | 3 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0040 | 226578 | 176343 | 100762 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0233-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 6,58 | 2,83 | 117 | PS5-79-IG-0010 | 4 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0233 | 226574 | 176343 | 100762 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0054-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,54 | 3,28 | 119 | PS5-79-IG-0010 | 5 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0054 | 219480 | 163500 | 103134 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0022-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,75 | 3,37 | 120 | PS5-79-IG-0010 | 6 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0022 | 216500 | 167000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0078-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 6,39 | 2,78 | 115 | PS5-79-IG-0010 | 7 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0078 | 219286 | 169500 | 101859 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0105-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,38 | 3,21 | 112 | PS5-79-IG-0010 | 8 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0105 | 218361 | 172500 | 101859 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0029-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,68 | 3,34 | 112 | PS5-79-IG-0010 | 9 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0029 | 216500 | 175000 | 101759 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0035-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 5,66 | 2,46 | 103 | PS5-79-IG-0010 | 10 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0035 | 220950 | 178500 | 103134 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0094-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 6,10 | 2,65 | 117 | PS5-79-IG-0010 | 11 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0094 | 225400 | 194027 | 101256 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0120-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,22 | 2,27 | 102 | PS5-79-IG-0010 | 12 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0120 | 209307 | 194000 | 100805 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0095-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 7,27 | 3,16 | 105 | PS5-79-IG-0010 | 13 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0095 | 219302 | 187701 | 101459 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
PS5-79-BE-0087-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,71 | 3,35 | 99 | PS5-79-IG-0010 | 14 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0087 | 214800 | 189046 | 103800 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0119-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,47 | 0,64 | 101 | PS5-79-IG-0010 | 15 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0119 | 209319 | 193700 | 100812 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0117-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,24 | 1,41 | 118 | PS5-79-IG-0010 | 16 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0117 | 224091 | 195374 | 100690 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0323-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,75 | 0,76 | 103 | PS5-79-IG-0010 | 17 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0323 | 211053 | 168590 | 100805 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0096-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 8,30 | 3,61 | 73 | PS5-79-IG-0010 | 18 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0096 | 214800 | 198461 | 101459 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0079-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 5,98 | 2,60 | 98 | PS5-79-IG-0010 | 19 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0079 | 207218 | 169500 | 101859 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0345-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,83 | 2,10 | 96 | PS5-79-IG-0010 | 20 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0345 | 205850 | 169551 | 101550 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0104-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 10 | 6,05 | 2,63 | 93 | PS5-79-IG-0010 | 21 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0104 | 205714 | 172500 | 101859 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
PS5-79-BE-0230-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,66 | 3,33 | 83 | PS5-79-IG-0010 | 22 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0230 | 224091 | 199276 | 100642 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0093-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,07 | 2,64 | 80 | PS5-79-IG-0010 | 23 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0093 | 225400 | 202887 | 101459 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0088-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,79 | 2,95 | 81 | PS5-79-IG-0010 | 24 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0088 | 219900 | 196571 | 101409 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0089-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,76 | 2,07 | 81 | PS5-79-IG-0010 | 25 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0089 | 219660 | 196571 | 101200 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0091-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,98 | 2,60 | 71 | PS5-79-IG-0010 | 26 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0091 | 217966 | 204200 | 101460 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0097-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 7,48 | 3,25 | 66 | PS5-79-IG-0010 | 27 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0097 | 214495 | 205400 | 102069 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0321-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,17 | 0,51 | 101 | PS5-79-IG-0010 | 28 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0321 | 209350 | 169769 | 101312 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0227-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,43 | 1,49 | 70 | PS5-79-IG-0010 | 29 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0227 | 223175 | 213949 | 100794 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-60-BE-0364-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,39 | 1,04 | 156 | PS5-79-IG-0010 | 31 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0364 | 215500 | 304000 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-BE-0286-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,46 | 2,81 | 55 | PS5-79-IG-0011 | 1 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0286 | 197748 | 364287 | 100982 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0347-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,98 | 1,73 | 55 | PS5-79-IG-0011 | 2 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0347 | 198049 | 364286 | 100982 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0289-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,14 | 1,80 | 56 | PS5-79-IG-0011 | 3 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0289 | 198150 | 364287 | 100982 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0342-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,53 | 0,23 | 64 | PS5-79-IG-0011 | 4 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0342 | 215350 | 355680 | 101934 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0232-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,73 | 0,75 | 48 | PS5-79-IG-0011 | 5 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0232 | 197950 | 358238 | 104094 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0231-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,52 | 0,66 | 43 | PS5-79-IG-0011 | 6 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0231 | 197750 | 354702 | 104165 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0288-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,10 | 0,48 | 65 | PS5-79-IG-0011 | 7 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0288 | 214054 | 338944 | 100997 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0225-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,08 | 0,47 | 40 | PS5-79-IG-0011 | 8 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0225 | 198698 | 350234 | 103413 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0324-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,13 | 0,49 | 60 | PS5-79-IG-0011 | 9 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0324 | 206562 | 359300 | 100862 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0080-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,94 | 0,41 | 51 | PS5-79-IG-0011 | 10 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0080 | 206562 | 350800 | 100862 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0065-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,99 | 0,43 | 53 | PS5-79-IG-0011 | 11 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0065 | 206562 | 342300 | 100862 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0287-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,94 | 1,28 | 62 | PS5-79-IG-0011 | 12 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0287 | 206562 | 333800 | 100862 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0277-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,69 | 0,30 | 64 | PS5-79-IG-0011 | 13 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0277 | 213097 | 337800 | 100793 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0276-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,10 | 0,48 | 65 | PS5-79-IG-0011 | 14 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0276 | 213090 | 337800 | 101027 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0226-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,27 | 0,55 | 37 | PS5-79-IG-0011 | 15 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0226 | 197950 | 349225 | 104094 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0340-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,48 | 0,21 | 65 | PS5-79-IG-0011 | 16 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0340 | 215350 | 338680 | 101934 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0336-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,38 | 0,60 | 70 | PS5-79-IG-0011 | 17 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0336 | 215614 | 337612 | 101575 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0031-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,58 | 0,25 | 55 | PS5-79-IG-0011 | 18 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0031 | 213097 | 346300 | 100793 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0016-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,94 | 0,41 | 56 | PS5-79-IG-0011 | 19 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0016 | 213090 | 346300 | 101027 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0038-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,97 | 0,42 | 56 | PS5-79-IG-0011 | 20 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0038 | 214054 | 347444 | 100997 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0341-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,46 | 0,21 | 57 | PS5-79-IG-0011 | 21 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0341 | 215350 | 347180 | 101934 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0337-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,20 | 0,52 | 60 | PS5-79-IG-0011 | 22 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0337 | 215614 | 346112 | 101575 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0050-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,64 | 0,28 | 61 | PS5-79-IG-0011 | 23 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0050 | 213097 | 354800 | 100793 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0048-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,06 | 0,46 | 62 | PS5-79-IG-0011 | 24 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0048 | 213090 | 354800 | 101027 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0069-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,08 | 0,47 | 63 | PS5-79-IG-0011 | 25 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0069 | 214054 | 355944 | 100997 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0349-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,05 | 1,76 | 56 | PS5-79-IG-0011 | 26 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0349 | 198249 | 364286 | 100982 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0338-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,27 | 0,56 | 64 | PS5-79-IG-0011 | 27 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0338 | 215614 | 354612 | 101575 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-60-BE-0368-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,06 | 0,46 | 69 | PS5-79-IG-0011 | 28 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0368 | 215500 | 338000 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-60-BE-0369-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,90 | 0,39 | 59 | PS5-79-IG-0011 | 29 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0369 | 215500 | 346500 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-60-BE-0370-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,97 | 0,43 | 64 | PS5-79-IG-0011 | 30 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0370 | 215500 | 355000 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-BE-0251-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,19 | 1,82 | 40 | PS5-79-IG-0012 | 1 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0251 | 239386 | 146336 | 100676 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0297-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,86 | 1,68 | 41 | PS5-79-IG-0012 | 2 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0297 | 239300 | 147040 | 98105 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0296-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,73 | 1,62 | 40 | PS5-79-IG-0012 | 3 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0296 | 239150 | 147040 | 98105 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0012-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,66 | 1,59 | 32 | PS5-79-IG-0012 | 4 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0012 | 216500 | 143608 | 100632 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0259-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 3,43 | 1,49 | 38 | PS5-79-IG-0012 | 5 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0259 | 238710 | 146783 | 100934 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0257-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,62 | 2,01 | 42 | PS5-79-IG-0012 | 6 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0257 | 208499 | 146301 | 101560 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0258-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,24 | 0,54 | 63 | PS5-79-IG-0012 | 7 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0258 | 203205 | 137535 | 102669 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0098-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,56 | 0,68 | 65 | PS5-79-IG-0012 | 8 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0098 | 201820 | 137480 | 101261 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0300-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,16 | 0,94 | 65 | PS5-79-IG-0012 | 9 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0300 | 203110 | 137410 | 101000 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0123-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,63 | 0,71 | 63 | PS5-79-IG-0012 | 10 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0123 | 201583 | 136497 | 101046 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0248-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,39 | 1,91 | 85 | PS5-79-IG-0012 | 11 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0248 | 189221 | 134450 | 102585 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0254-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,58 | 0,25 | 53 | PS5-79-IG-0012 | 12 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0254 | 198905 | 137199 | 102669 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0310-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,39 | 0,17 | 57 | PS5-79-IG-0012 | 13 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0310 | 197283 | 132705 | 100996 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0263-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,18 | 2,25 | 54 | PS5-79-IG-0012 | 14 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0263 | 196097 | 134965 | 102949 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0122-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,36 | 0,59 | 53 | PS5-79-IG-0012 | 15 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0122 | 197283 | 136497 | 101046 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0110-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,17 | 0,51 | 52 | PS5-79-IG-0012 | 16 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0110 | 197444 | 137480 | 101261 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0256-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,37 | 0,16 | 51 | PS5-79-IG-0012 | 17 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0256 | 195500 | 139465 | 102551 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0320-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,65 | 2,02 | 53 | PS5-79-IG-0012 | 18 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0320 | 196924 | 147901 | 102900 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0255-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,70 | 0,74 | 55 | PS5-79-IG-0012 | 19 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0255 | 195500 | 146339 | 101874 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0017-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,60 | 0,26 | 56 | PS5-79-IG-0012 | 20 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0017 | 195005 | 143600 | 100594 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0250-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 6,23 | 2,71 | 57 | PS5-79-IG-0012 | 21 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0250 | 194925 | 145853 | 101575 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0249-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,92 | 1,27 | 58 | PS5-79-IG-0012 | 22 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0249 | 193752 | 145650 | 101577 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0318-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,55 | 0,24 | 59 | PS5-79-IG-0012 | 23 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0318 | 193233 | 145878 | 101482 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0309-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,29 | 0,56 | 80 | PS5-79-IG-0012 | 24 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0309 | 188000 | 133775 | 99912 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0018-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,08 | 0,47 | 81 | PS5-79-IG-0012 | 25 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0018 | 188000 | 133475 | 99973 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-SP-0018-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,08 | 0,47 | 4 | PS5-79-BE-0018 | 25 | 188000 | 133475 | 99973 | Heat Tracing Junction Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0018 | 188073 | 132498 | 99903 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0130-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,86 | 0,81 | 88 | PS5-79-IG-0012 | 26 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0130 | 188089 | 130543 | 95737 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0299-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 1,75 | 0,76 | 53 | PS5-79-IG-0012 | 27 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0299 | 198800 | 137410 | 101000 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0308-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 5,75 | 2,50 | 85 | PS5-79-IG-0012 | 28 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0308 | 188754 | 130838 | 100908 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0013-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,25 | 0,98 | 42 | PS5-79-IG-0012 | 29 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0013 | 241860 | 146810 | 101037 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0015-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,67 | 0,29 | 44 | PS5-79-IG-0012 | 30 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0015 | 241860 | 148012 | 96662 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0133-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,81 | 0,35 | 40 | PS5-79-IG-0012 | 31 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0133 | 241210 | 147725 | 99988 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-SP-0133-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,81 | 0,35 | 4 | PS5-79-BE-0133 | 31 | 241210 | 147725 | 99988 | Heat Tracing Junction Box | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0133 | 238238 | 147751 | 99916 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0298-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 4,35 | 1,89 | 43 | PS5-79-IG-0012 | 32 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0298 | 241325 | 147040 | 98105 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
PS5-79-BE-0026-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 0,39 | 0,17 | 42 | PS5-79-IG-0012 | 33 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0026 | 240420 | 144825 | 101007 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-79-BE-0138-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,23 | 0,97 | 24 | PS5-79-IG-0012 | 34 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0138 | 225604 | 149272 | 100912 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
PS5-25-BE-0364-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | 2C+E | 6 | 2,28 | 0,99 | 148 | PS5-79-IG-0012 | 37 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | GL38-M25-METAL | M25 | PS5-25-BE-0364 | 168700 | 210600 | 101500 | Heat Tracing Junction Box | Field | GL38-M25-METAL | M25 | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
PS5-79-TE-0316-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 88 | PS5-79-IG-0001 | 1 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0316 | 238823 | 219996 | 101198 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0315-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0001 | 2 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0315 | 238823 | 223504 | 101198 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0168-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 83 | PS5-79-IG-0001 | 3 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0168 | 241959 | 220752 | 102733 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0170-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 83 | PS5-79-IG-0001 | 4 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0170 | 241959 | 222748 | 102733 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0163-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 76 | PS5-79-IG-0001 | 5 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0163 | 231300 | 222100 | 107460 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0167-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 83 | PS5-79-IG-0001 | 6 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0167 | 240472 | 220525 | 101251 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0169-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 83 | PS5-79-IG-0001 | 7 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0169 | 240472 | 223025 | 101251 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0159-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 82 | PS5-79-IG-0001 | 8 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0159 | 239053 | 223000 | 101408 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0164-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0001 | 9 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0164 | 232390 | 222113 | 107198 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0151-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 75 | PS5-79-IG-0001 | 10 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0151 | 231300 | 223940 | 107460 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0356-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 86 | PS5-79-IG-0001 | 11 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0356 | 239891 | 227070 | 100963 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0206-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 70 | PS5-79-IG-0001 | 12 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0206 | 229610 | 220823 | 105048 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0148-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 79 | PS5-79-IG-0001 | 13 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0148 | 234264 | 219817 | 100758 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0314-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 79 | PS5-79-IG-0001 | 14 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0314 | 234664 | 224790 | 100810 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0149-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 78 | PS5-79-IG-0001 | 15 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0149 | 234914 | 223790 | 101199 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0234-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 84 | PS5-79-IG-0001 | 16 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0234 | 235422 | 230795 | 102252 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0114-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 82 | PS5-79-IG-0001 | 17 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0114 | 235893 | 227070 | 100825 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0165-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0001 | 18 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0165 | 232390 | 221800 | 105270 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0166-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 82 | PS5-79-IG-0001 | 19 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0166 | 239053 | 220500 | 101408 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0157-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 72 | PS5-79-IG-0001 | 20 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0157 | 232390 | 224260 | 105270 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0153-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 71 | PS5-79-IG-0001 | 21 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0153 | 232390 | 223953 | 107198 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0313-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 80 | PS5-79-IG-0001 | 22 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0313 | 234664 | 218529 | 100810 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0188-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 70 | PS5-79-IG-0001 | 23 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0188 | 230850 | 221200 | 103568 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0202-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 61 | PS5-79-IG-0001 | 24 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0202 | 235900 | 228743 | 101262 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0103-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 51 | PS5-79-IG-0001 | 25 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0103 | 230400 | 240000 | 103807 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0317-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 49 | PS5-79-IG-0001 | 26 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0317 | 230150 | 243250 | 101207 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0306-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 51 | PS5-79-IG-0001 | 27 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0306 | 230400 | 240870 | 103807 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0197-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 51 | PS5-79-IG-0001 | 28 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0197 | 230810 | 244473 | 101182 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-71-TE-0361-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 84 | PS5-79-IG-0001 | 31 | 244467 | 270700 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-71-TE-0361 | 244467 | 270700 | 100000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-TE-0181-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 68 | PS5-79-IG-0002 | 1 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0181 | 237218 | 238542 | 101124 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0184-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 69 | PS5-79-IG-0002 | 2 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0184 | 240387 | 239000 | 101202 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0302-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 68 | PS5-79-IG-0002 | 3 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0302 | 241615 | 238750 | 101250 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0185-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 65 | PS5-79-IG-0002 | 4 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0185 | 240387 | 242400 | 101202 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0182-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 63 | PS5-79-IG-0002 | 5 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0182 | 237218 | 242850 | 101123 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0303-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 65 | PS5-79-IG-0002 | 6 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0303 | 241615 | 242140 | 101170 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0304-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 56 | PS5-79-IG-0002 | 7 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0304 | 241590 | 255255 | 101130 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0325-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0002 | 8 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0325 | 240743 | 253155 | 100906 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0311-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 72 | PS5-79-IG-0002 | 9 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0311 | 240750 | 252298 | 101265 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0312-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 71 | PS5-79-IG-0002 | 10 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0312 | 240450 | 251493 | 100572 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0173-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 62 | PS5-79-IG-0002 | 11 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0173 | 235536 | 238250 | 101935 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0183-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 58 | PS5-79-IG-0002 | 12 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0183 | 235900 | 238416 | 101356 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0355-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 68 | PS5-79-IG-0002 | 13 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0355 | 235800 | 248278 | 100958 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0354-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 68 | PS5-79-IG-0002 | 14 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0354 | 236254 | 249685 | 101808 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0201-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 70 | PS5-79-IG-0002 | 15 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0201 | 240750 | 252655 | 101201 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0193-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 37 | PS5-79-IG-0002 | 16 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0193 | 230900 | 256760 | 103808 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0322-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 38 | PS5-79-IG-0002 | 17 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0322 | 229750 | 257200 | 101810 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0192-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0002 | 18 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0192 | 234786 | 253801 | 101433 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0191-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 53 | PS5-79-IG-0002 | 19 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0191 | 235536 | 254891 | 102020 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0346-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0002 | 20 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0346 | 235900 | 254504 | 101433 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0172-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 58 | PS5-79-IG-0002 | 21 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0172 | 237218 | 255228 | 101124 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0179-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 56 | PS5-79-IG-0002 | 22 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0179 | 239808 | 255500 | 101202 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0326-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0002 | 23 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0326 | 243630 | 252799 | 100906 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0180-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 53 | PS5-79-IG-0002 | 24 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0180 | 239808 | 258900 | 101202 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0174-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 53 | PS5-79-IG-0002 | 25 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0174 | 237218 | 259172 | 101124 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0305-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0002 | 26 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0305 | 241628 | 258632 | 101165 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0199-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 15 | PS5-79-IG-0002 | 27 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0199 | 231080 | 268250 | 101208 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0187-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 13 | PS5-79-IG-0002 | 28 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0187 | 228590 | 271970 | 100932 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0190-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 12 | PS5-79-IG-0002 | 29 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0190 | 230590 | 272840 | 100933 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-71-TE-0363-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0002 | 31 | 236950 | 270400 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-71-TE-0363 | 236950 | 270400 | 100000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-TE-0023-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 104 | PS5-79-IG-0003 | 1 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0023 | 221392 | 290057 | 101203 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0278-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 107 | PS5-79-IG-0003 | 2 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0278 | 226125 | 289066 | 100966 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0307-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 104 | PS5-79-IG-0003 | 3 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0307 | 220400 | 290058 | 101534 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0198-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 103 | PS5-79-IG-0003 | 4 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0198 | 220150 | 289891 | 101053 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0046-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 103 | PS5-79-IG-0003 | 5 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0046 | 220677 | 289557 | 101204 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0195-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 102 | PS5-79-IG-0003 | 6 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0195 | 219400 | 290243 | 101188 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0252-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 95 | PS5-79-IG-0003 | 7 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0252 | 212892 | 289807 | 101201 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0253-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 95 | PS5-79-IG-0003 | 8 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0253 | 212177 | 289555 | 101202 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0200-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 90 | PS5-79-IG-0003 | 9 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0200 | 211643 | 289144 | 103742 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0194-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 90 | PS5-79-IG-0003 | 10 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0194 | 211246 | 289034 | 103742 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0246-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 90 | PS5-79-IG-0003 | 11 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0246 | 210672 | 289075 | 103717 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0189-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 91 | PS5-79-IG-0003 | 12 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0189 | 205176 | 283600 | 104682 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0210-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 66 | PS5-79-IG-0003 | 13 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0210 | 196946 | 264938 | 105415 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0186-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 91 | PS5-79-IG-0003 | 14 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0186 | 204875 | 283600 | 104682 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0279-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 99 | PS5-79-IG-0003 | 15 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0279 | 199010 | 286936 | 100766 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0260-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 62 | PS5-79-IG-0003 | 16 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0260 | 197100 | 272860 | 100932 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0211-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 64 | PS5-79-IG-0003 | 17 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0211 | 196947 | 273301 | 105573 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0196-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 77 | PS5-79-IG-0003 | 18 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0196 | 205676 | 278359 | 101382 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0244-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 78 | PS5-79-IG-0003 | 19 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0244 | 205975 | 278369 | 101407 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0238-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 94 | PS5-79-IG-0003 | 20 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0238 | 216899 | 271670 | 100957 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0348-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 132 | PS5-79-IG-0003 | 21 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0348 | 219647 | 254750 | 100833 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0352-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 143 | PS5-79-IG-0003 | 22 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0352 | 218391 | 247728 | 103510 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0242-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 158 | PS5-79-IG-0003 | 23 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0242 | 220155 | 228089 | 101150 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0109-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 145 | PS5-79-IG-0003 | 24 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0109 | 222085 | 240600 | 100705 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0113-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 146 | PS5-79-IG-0003 | 25 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0113 | 222085 | 237440 | 100805 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0106-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 147 | PS5-79-IG-0003 | 26 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0106 | 220275 | 238061 | 102551 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0351-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 161 | PS5-79-IG-0003 | 27 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0351 | 220627 | 228174 | 104727 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0243-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 142 | PS5-79-IG-0003 | 28 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0243 | 217200 | 247375 | 101150 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-60-TE-0365-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 85 | PS5-79-IG-0003 | 31 | 181572 | 278350 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0365 | 181572 | 278350 | 100000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-TE-0280-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 79 | PS5-79-IG-0004 | 1 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0280 | 215014 | 299886 | 100966 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0331-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 76 | PS5-79-IG-0004 | 2 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0331 | 215168 | 303801 | 101481 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0327-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0004 | 3 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0327 | 213515 | 304680 | 101934 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0266-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0004 | 4 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0266 | 212777 | 304931 | 100870 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0265-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0004 | 5 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0265 | 212966 | 305183 | 100872 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0212-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 16 | PS5-79-IG-0004 | 6 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0212 | 179511 | 288096 | 107550 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0049-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 76 | PS5-79-IG-0004 | 7 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0049 | 212114 | 299026 | 100734 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0329-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 67 | PS5-79-IG-0004 | 8 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0329 | 205508 | 308300 | 100855 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0285-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 65 | PS5-79-IG-0004 | 9 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0285 | 200500 | 300386 | 100766 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0220-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0004 | 10 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0220 | 199000 | 311000 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0217-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 66 | PS5-79-IG-0004 | 11 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0217 | 198698 | 314800 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0219-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0004 | 12 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0219 | 200810 | 309100 | 105155 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0237-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0004 | 13 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0237 | 166750 | 303101 | 101966 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0282-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 43 | PS5-79-IG-0004 | 14 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0282 | 184849 | 304826 | 100766 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0213-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 32 | PS5-79-IG-0004 | 15 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0213 | 177354 | 301049 | 110441 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0086-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 47 | PS5-79-IG-0004 | 16 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0086 | 166447 | 303869 | 102455 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0214-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 47 | PS5-79-IG-0004 | 17 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0214 | 177354 | 302401 | 109639 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0283-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 45 | PS5-79-IG-0004 | 18 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0283 | 185472 | 305326 | 100766 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0092-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 68 | PS5-79-IG-0004 | 19 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0092 | 166447 | 303569 | 102455 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0216-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 66 | PS5-79-IG-0004 | 20 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0216 | 164104 | 302200 | 101983 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0215-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 68 | PS5-79-IG-0004 | 21 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0215 | 160805 | 303570 | 101983 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0099-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 70 | PS5-79-IG-0004 | 22 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0099 | 160707 | 301999 | 100682 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0171-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0004 | 23 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0171 | 159908 | 304072 | 98765 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0264-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0004 | 24 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0264 | 212007 | 303534 | 99817 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0281-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 22 | PS5-79-IG-0004 | 25 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0281 | 182760 | 297737 | 100766 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0284-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 24 | PS5-79-IG-0004 | 26 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0284 | 183263 | 298408 | 100766 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-60-TE-0366-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 90 | PS5-79-IG-0004 | 28 | 181571 | 283767 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0366 | 181571 | 283767 | 100000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-TE-0332-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 89 | PS5-79-IG-0005 | 1 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0332 | 215168 | 312301 | 101481 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0330-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 86 | PS5-79-IG-0005 | 2 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0330 | 213515 | 313180 | 101934 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0269-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0005 | 3 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0269 | 212777 | 313431 | 100870 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0267-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0005 | 4 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0267 | 212007 | 312034 | 99817 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0268-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0005 | 5 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0268 | 212966 | 313683 | 100872 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0334-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 81 | PS5-79-IG-0005 | 6 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0334 | 215168 | 320801 | 101481 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0333-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 77 | PS5-79-IG-0005 | 7 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0333 | 213515 | 321680 | 101934 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0272-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 77 | PS5-79-IG-0005 | 8 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0272 | 212777 | 321931 | 100870 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0270-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 78 | PS5-79-IG-0005 | 9 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0270 | 212007 | 320534 | 99817 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0271-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 77 | PS5-79-IG-0005 | 10 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0271 | 212966 | 322183 | 100872 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0335-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 85 | PS5-79-IG-0005 | 11 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0335 | 215168 | 329301 | 101481 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0339-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 88 | PS5-79-IG-0005 | 12 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0339 | 213515 | 330180 | 101934 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0275-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 85 | PS5-79-IG-0005 | 13 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0275 | 212777 | 330431 | 100870 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0273-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 83 | PS5-79-IG-0005 | 14 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0273 | 212007 | 329034 | 99817 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0274-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 82 | PS5-79-IG-0005 | 15 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0274 | 212978 | 330683 | 100872 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0328-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 75 | PS5-79-IG-0005 | 16 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0328 | 205508 | 316800 | 100855 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0061-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 72 | PS5-79-IG-0005 | 17 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0061 | 205508 | 325300 | 100855 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0218-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 65 | PS5-79-IG-0005 | 18 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0218 | 198698 | 316800 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0229-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 81 | PS5-79-IG-0005 | 19 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0229 | 199000 | 345000 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0223-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 60 | PS5-79-IG-0005 | 20 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0223 | 200810 | 326100 | 105155 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0224-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 64 | PS5-79-IG-0005 | 21 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0224 | 199000 | 328000 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0221-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 71 | PS5-79-IG-0005 | 22 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0221 | 198698 | 331800 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0235-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 96 | PS5-79-IG-0005 | 23 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0235 | 197950 | 360000 | 104155 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0222-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 67 | PS5-79-IG-0005 | 24 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0222 | 198698 | 333800 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0350-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 70 | PS5-79-IG-0005 | 25 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0350 | 197550 | 334500 | 104156 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0228-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 76 | PS5-79-IG-0005 | 26 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0228 | 200810 | 343100 | 105155 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0236-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 90 | PS5-79-IG-0005 | 27 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0236 | 197109 | 356487 | 103665 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-60-TE-0367-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 85 | PS5-79-IG-0005 | 28 | 181572 | 289183 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0367 | 181572 | 289183 | 100000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-TE-0136-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 110 | PS5-79-IG-0009 | 1 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0136 | 174857 | 160698 | 100977 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0027-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 109 | PS5-79-IG-0009 | 2 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0027 | 180200 | 167000 | 101759 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0039-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0009 | 3 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0039 | 180700 | 175000 | 101759 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0037-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 75 | PS5-79-IG-0009 | 4 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0037 | 193145 | 175000 | 101760 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0025-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 97 | PS5-79-IG-0009 | 5 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0025 | 186200 | 167000 | 101759 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0343-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 109 | PS5-79-IG-0009 | 6 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0343 | 188000 | 151232 | 100756 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0118-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 88 | PS5-79-IG-0009 | 7 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0118 | 201490 | 167899 | 102792 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0137-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 88 | PS5-79-IG-0009 | 8 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0137 | 197700 | 163412 | 100520 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0024-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0009 | 9 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0024 | 195183 | 167000 | 101759 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0150-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 99 | PS5-79-IG-0009 | 10 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0150 | 172689 | 192702 | 101424 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0203-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 69 | PS5-79-IG-0009 | 11 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0203 | 197323 | 177900 | 103476 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0204-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 68 | PS5-79-IG-0009 | 12 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0204 | 198325 | 180000 | 103521 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0262-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0009 | 13 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0262 | 198500 | 184250 | 100932 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0102-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 75 | PS5-79-IG-0009 | 14 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0102 | 201400 | 183750 | 101508 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0081-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 84 | PS5-79-IG-0009 | 15 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0081 | 202600 | 174505 | 104208 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0036-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 85 | PS5-79-IG-0009 | 16 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0036 | 206200 | 175000 | 101759 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0066-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0009 | 17 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0066 | 186500 | 193840 | 102001 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0067-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 78 | PS5-79-IG-0009 | 18 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0067 | 181713 | 188775 | 102557 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0245-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 82 | PS5-79-IG-0009 | 19 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0245 | 177499 | 186398 | 100706 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0134-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 92 | PS5-79-IG-0009 | 20 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0134 | 174074 | 188775 | 100774 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0063-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 91 | PS5-79-IG-0009 | 21 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0063 | 174500 | 188775 | 101800 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0154-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 97 | PS5-79-IG-0009 | 22 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0154 | 177644 | 192677 | 103057 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0319-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0009 | 23 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0319 | 196925 | 174293 | 103412 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0290-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 100 | PS5-79-IG-0009 | 24 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0290 | 171117 | 194175 | 100325 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0152-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 99 | PS5-79-IG-0009 | 25 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0152 | 172433 | 193924 | 101329 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0002-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 83 | PS5-79-IG-0009 | 26 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0002 | 166450 | 195438 | 101170 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0005-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 96 | PS5-79-IG-0009 | 27 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0005 | 167902 | 193765 | 103275 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0146-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 83 | PS5-79-IG-0009 | 28 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0146 | 169805 | 195887 | 101115 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0041-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 85 | PS5-79-IG-0009 | 29 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0041 | 169755 | 196138 | 102052 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0135-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 102 | PS5-79-IG-0009 | 30 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0135 | 171113 | 189271 | 100855 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0239-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 103 | PS5-79-IG-0009 | 31 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0239 | 164054 | 191066 | 100815 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0247-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 61 | PS5-79-IG-0007 | 1 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0247 | 208952 | 209077 | 100703 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0084-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 63 | PS5-79-IG-0007 | 2 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0084 | 206380 | 202000 | 103808 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0090-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 58 | PS5-79-IG-0007 | 3 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0090 | 207189 | 204200 | 103858 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0085-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 101 | PS5-79-IG-0007 | 4 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0085 | 209345 | 190699 | 101459 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0082-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 84 | PS5-79-IG-0007 | 5 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0082 | 202600 | 184250 | 101458 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0101-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 67 | PS5-79-IG-0007 | 6 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0101 | 201400 | 191750 | 101509 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0156-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 72 | PS5-79-IG-0007 | 7 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0156 | 172433 | 205924 | 101329 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0107-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 61 | PS5-79-IG-0007 | 8 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0107 | 199600 | 197899 | 105458 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0020-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0007 | 9 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0020 | 204412 | 202048 | 100655 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0147-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0007 | 10 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0147 | 200200 | 202915 | 101509 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0043-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 62 | PS5-79-IG-0007 | 11 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0043 | 198200 | 196138 | 105257 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0344-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 61 | PS5-79-IG-0007 | 12 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0344 | 199150 | 200250 | 100957 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0019-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0007 | 13 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0019 | 201100 | 202114 | 100662 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0100-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 51 | PS5-79-IG-0007 | 14 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0100 | 201400 | 203901 | 101509 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0112-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0007 | 15 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0112 | 198423 | 199581 | 105256 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0068-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0007 | 16 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0068 | 187775 | 195297 | 104105 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0042-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0007 | 17 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0042 | 191179 | 196138 | 102051 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0121-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 65 | PS5-79-IG-0007 | 18 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0121 | 187775 | 195976 | 105458 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0072-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 71 | PS5-79-IG-0007 | 19 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0072 | 181713 | 200775 | 102557 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0116-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 65 | PS5-79-IG-0007 | 20 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0116 | 187955 | 198332 | 105858 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0145-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0007 | 21 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0145 | 174074 | 200775 | 100774 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0155-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 93 | PS5-79-IG-0007 | 22 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0155 | 172689 | 204702 | 101424 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0071-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 85 | PS5-79-IG-0007 | 23 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0071 | 174500 | 200775 | 101800 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0083-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 66 | PS5-79-IG-0007 | 24 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0083 | 202600 | 198400 | 101458 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0291-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 72 | PS5-79-IG-0007 | 25 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0291 | 171207 | 206325 | 100325 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0003-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0007 | 26 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0003 | 166449 | 207438 | 101170 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0143-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0007 | 27 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0143 | 169805 | 207889 | 101115 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0059-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 75 | PS5-79-IG-0007 | 28 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0059 | 169700 | 208140 | 102051 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0006-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 97 | PS5-79-IG-0007 | 29 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0006 | 167902 | 205765 | 103275 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0144-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 99 | PS5-79-IG-0007 | 30 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0144 | 170924 | 201271 | 100860 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0240-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 101 | PS5-79-IG-0007 | 31 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0240 | 164054 | 203066 | 100815 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0241-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0008 | 1 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0241 | 164054 | 215066 | 100815 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0208-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 58 | PS5-79-IG-0008 | 2 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0208 | 196925 | 204250 | 104025 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0292-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 72 | PS5-79-IG-0008 | 3 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0292 | 171157 | 218205 | 100325 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0058-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 76 | PS5-79-IG-0008 | 4 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0058 | 169700 | 220137 | 102051 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0140-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0008 | 5 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0140 | 169682 | 219889 | 101116 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0004-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0008 | 6 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0004 | 166499 | 219438 | 101170 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0007-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 92 | PS5-79-IG-0008 | 7 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0007 | 167902 | 217765 | 103275 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0161-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 71 | PS5-79-IG-0008 | 8 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0161 | 172433 | 217924 | 101329 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0139-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 68 | PS5-79-IG-0008 | 9 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0139 | 177600 | 222558 | 100592 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0162-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 72 | PS5-79-IG-0008 | 10 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0162 | 177644 | 216677 | 103057 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0074-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0008 | 11 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0074 | 174500 | 212775 | 101800 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0142-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 74 | PS5-79-IG-0008 | 12 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0142 | 174074 | 212775 | 100774 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0160-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 72 | PS5-79-IG-0008 | 13 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0160 | 172689 | 216702 | 101424 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0077-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 67 | PS5-79-IG-0008 | 14 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0077 | 181713 | 212774 | 102557 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0075-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0008 | 15 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0075 | 186540 | 217839 | 102001 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0053-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 54 | PS5-79-IG-0008 | 16 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0053 | 191179 | 220137 | 102051 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0076-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 57 | PS5-79-IG-0008 | 17 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0076 | 187775 | 214671 | 104105 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0070-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 69 | PS5-79-IG-0008 | 18 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0070 | 188000 | 205839 | 102001 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0158-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 67 | PS5-79-IG-0008 | 19 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0158 | 184264 | 204676 | 103057 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0060-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 64 | PS5-79-IG-0008 | 20 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0060 | 191179 | 208140 | 102051 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0115-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 71 | PS5-79-IG-0008 | 21 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0115 | 187775 | 202287 | 105458 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0108-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 69 | PS5-79-IG-0008 | 22 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0108 | 191122 | 197899 | 105458 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0111-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 70 | PS5-79-IG-0008 | 23 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0111 | 187776 | 200139 | 105458 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0062-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0008 | 24 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0062 | 193609 | 208140 | 105256 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0141-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 89 | PS5-79-IG-0008 | 25 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0141 | 170924 | 213271 | 100865 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0207-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0008 | 26 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0207 | 196925 | 200922 | 103970 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0205-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 53 | PS5-79-IG-0008 | 27 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0205 | 197324 | 209377 | 104169 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0044-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0008 | 28 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0044 | 200200 | 208250 | 101509 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0045-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 53 | PS5-79-IG-0008 | 29 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0045 | 197920 | 220137 | 105256 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0261-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0008 | 30 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0261 | 198500 | 221250 | 100932 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0209-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 35 | PS5-79-IG-0008 | 31 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0209 | 196946 | 229260 | 104691 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0064-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 137 | PS5-79-IG-0006 | 1 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0064 | 236596 | 165701 | 100821 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0057-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 134 | PS5-79-IG-0006 | 2 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0057 | 234539 | 166030 | 102686 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0021-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 118 | PS5-79-IG-0006 | 3 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0021 | 228971 | 167000 | 101760 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0128-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 128 | PS5-79-IG-0006 | 4 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0128 | 235019 | 170968 | 106378 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0008-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 122 | PS5-79-IG-0006 | 5 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0008 | 233090 | 167120 | 102369 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0047-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 112 | PS5-79-IG-0006 | 6 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0047 | 229548 | 174159 | 100892 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0052-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 128 | PS5-79-IG-0006 | 7 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0052 | 229350 | 163500 | 101413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0056-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 130 | PS5-79-IG-0006 | 8 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0056 | 230166 | 164001 | 102150 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0055-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 130 | PS5-79-IG-0006 | 9 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0055 | 232257 | 164311 | 100750 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0028-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 111 | PS5-79-IG-0006 | 10 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0028 | 229198 | 175000 | 101759 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0294-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 124 | PS5-79-IG-0006 | 11 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0294 | 233965 | 166653 | 101323 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0293-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 125 | PS5-79-IG-0006 | 12 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0293 | 235030 | 166577 | 101403 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0129-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 123 | PS5-79-IG-0006 | 13 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0129 | 234540 | 171975 | 104899 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0073-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 118 | PS5-79-IG-0006 | 14 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0073 | 230570 | 167917 | 100816 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0010-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 117 | PS5-79-IG-0006 | 15 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0010 | 234070 | 174888 | 102451 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0124-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 126 | PS5-79-IG-0006 | 16 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0124 | 236600 | 170234 | 105727 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0295-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 119 | PS5-79-IG-0006 | 17 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0295 | 234537 | 174668 | 101310 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0030-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 111 | PS5-79-IG-0006 | 18 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0030 | 233800 | 178499 | 101484 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0127-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 117 | PS5-79-IG-0006 | 19 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0127 | 235019 | 171976 | 105894 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0051-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 114 | PS5-79-IG-0006 | 20 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0051 | 233542 | 175902 | 102880 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0032-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 112 | PS5-79-IG-0006 | 21 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0032 | 234577 | 178100 | 100849 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0033-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 111 | PS5-79-IG-0006 | 22 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0033 | 233281 | 178000 | 102321 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0126-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 126 | PS5-79-IG-0006 | 23 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0126 | 237100 | 170234 | 104900 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0125-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 128 | PS5-79-IG-0006 | 24 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0125 | 236599 | 171024 | 106165 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0011-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 138 | PS5-79-IG-0006 | 25 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0011 | 236102 | 165838 | 101175 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0301-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 118 | PS5-79-IG-0006 | 26 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0301 | 233937 | 174668 | 101310 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0001-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 127 | PS5-79-IG-0006 | 27 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0001 | 237724 | 167300 | 102907 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0009-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 120 | PS5-79-IG-0006 | 28 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0009 | 237218 | 174625 | 102907 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0014-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 121 | PS5-79-IG-0006 | 29 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0014 | 236001 | 174035 | 100955 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0034-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 110 | PS5-79-IG-0006 | 30 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0034 | 230300 | 178499 | 101484 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0353-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 115 | PS5-79-IG-0006 | 31 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0353 | 232858 | 175000 | 102338 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-71-TE-0362-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 97 | PS5-79-IG-0006 | 34 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-71-TE-0362 | 188770 | 231192 | 100000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-TE-0132-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 130 | PS5-79-IG-0010 | 1 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0132 | 224575 | 159480 | 103459 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0131-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 133 | PS5-79-IG-0010 | 2 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0131 | 237559 | 171008 | 103931 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0040-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 127 | PS5-79-IG-0010 | 3 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0040 | 236218 | 176342 | 100877 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0233-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 118 | PS5-79-IG-0010 | 4 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0233 | 223175 | 175342 | 100711 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0054-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 119 | PS5-79-IG-0010 | 5 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0054 | 218479 | 163500 | 103134 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0022-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 120 | PS5-79-IG-0010 | 6 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0022 | 219300 | 167000 | 101760 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0078-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 115 | PS5-79-IG-0010 | 7 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0078 | 215000 | 169500 | 101859 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0105-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 112 | PS5-79-IG-0010 | 8 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0105 | 219286 | 172501 | 101860 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0029-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 111 | PS5-79-IG-0010 | 9 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0029 | 220900 | 175000 | 101759 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0035-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 103 | PS5-79-IG-0010 | 10 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0035 | 219349 | 178499 | 103134 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0094-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 117 | PS5-79-IG-0010 | 11 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0094 | 225400 | 197501 | 101256 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0120-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 102 | PS5-79-IG-0010 | 12 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0120 | 208822 | 194001 | 100625 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0095-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 105 | PS5-79-IG-0010 | 13 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0095 | 218302 | 187701 | 101460 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0087-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 99 | PS5-79-IG-0010 | 14 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0087 | 212800 | 189046 | 103808 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0119-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 101 | PS5-79-IG-0010 | 15 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0119 | 208896 | 193701 | 100609 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0117-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 118 | PS5-79-IG-0010 | 16 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0117 | 224401 | 196123 | 100669 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0323-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 103 | PS5-79-IG-0010 | 17 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0323 | 213702 | 168590 | 100780 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0096-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 73 | PS5-79-IG-0010 | 18 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0096 | 214800 | 196293 | 101459 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0079-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 98 | PS5-79-IG-0010 | 19 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0079 | 204850 | 169501 | 101860 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0345-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 96 | PS5-79-IG-0010 | 20 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0345 | 201448 | 168800 | 102208 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0104-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 93 | PS5-79-IG-0010 | 21 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0104 | 207720 | 172500 | 101859 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0230-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 83 | PS5-79-IG-0010 | 22 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0230 | 223174 | 200065 | 100427 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0093-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 80 | PS5-79-IG-0010 | 23 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0093 | 225400 | 203287 | 101460 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0088-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 81 | PS5-79-IG-0010 | 24 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0088 | 219900 | 195071 | 101409 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0089-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 81 | PS5-79-IG-0010 | 25 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0089 | 219900 | 198071 | 101409 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0091-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 71 | PS5-79-IG-0010 | 26 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0091 | 221699 | 204200 | 101459 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0097-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 67 | PS5-79-IG-0010 | 27 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0097 | 214800 | 203486 | 101459 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0321-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 100 | PS5-79-IG-0010 | 28 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0321 | 208715 | 169501 | 100806 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0227-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 71 | PS5-79-IG-0010 | 29 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0227 | 223175 | 213666 | 100511 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-60-TE-0364-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 157 | PS5-79-IG-0010 | 31 | 183353 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0364 | 183353 | 231192 | 100000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-TE-0286-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 54 | PS5-79-IG-0011 | 1 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0286 | 197748 | 364073 | 100768 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0347-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0011 | 2 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0347 | 198249 | 364043 | 100683 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0289-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0011 | 3 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0289 | 198150 | 364073 | 100768 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0342-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 63 | PS5-79-IG-0011 | 4 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0342 | 213515 | 355680 | 101934 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0232-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 47 | PS5-79-IG-0011 | 5 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0232 | 198698 | 359300 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0231-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 42 | PS5-79-IG-0011 | 6 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0231 | 199000 | 357000 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0288-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 64 | PS5-79-IG-0011 | 7 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0288 | 212777 | 338931 | 100870 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0225-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 40 | PS5-79-IG-0011 | 8 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0225 | 198698 | 348800 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0324-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0011 | 9 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0324 | 205508 | 359300 | 100855 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0080-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 49 | PS5-79-IG-0011 | 10 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0080 | 205508 | 350800 | 100855 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0065-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0011 | 11 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0065 | 205508 | 342300 | 100855 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0287-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 61 | PS5-79-IG-0011 | 12 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0287 | 205508 | 333800 | 100855 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0277-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 64 | PS5-79-IG-0011 | 13 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0277 | 212966 | 339183 | 100872 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0276-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 64 | PS5-79-IG-0011 | 14 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0276 | 212007 | 337534 | 99817 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0226-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 37 | PS5-79-IG-0011 | 15 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0226 | 198698 | 350800 | 103413 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0340-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 64 | PS5-79-IG-0011 | 16 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0340 | 213515 | 338680 | 101934 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0336-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 67 | PS5-79-IG-0011 | 17 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0336 | 215168 | 337801 | 101481 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0031-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 54 | PS5-79-IG-0011 | 18 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0031 | 212976 | 347683 | 100872 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0016-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0011 | 19 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0016 | 212007 | 346034 | 99817 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0038-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0011 | 20 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0038 | 212777 | 347431 | 100870 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0341-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0011 | 21 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0341 | 213515 | 347180 | 101934 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0337-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 59 | PS5-79-IG-0011 | 22 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0337 | 215168 | 346301 | 101481 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0050-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 60 | PS5-79-IG-0011 | 23 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0050 | 212978 | 356183 | 100872 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0048-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 61 | PS5-79-IG-0011 | 24 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0048 | 212007 | 354534 | 99817 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0069-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 63 | PS5-79-IG-0011 | 25 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0069 | 212777 | 355931 | 100870 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0349-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0011 | 26 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0349 | 198100 | 364043 | 100683 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0338-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 62 | PS5-79-IG-0011 | 27 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0338 | 215168 | 354801 | 101481 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-60-TE-0368-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 67 | PS5-79-IG-0011 | 28 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0368 | 187682 | 327500 | 100150 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-60-TE-0369-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 58 | PS5-79-IG-0011 | 29 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0369 | 187682 | 327500 | 100150 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-60-TE-0370-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 63 | PS5-79-IG-0011 | 30 | 187682 | 327500 | 100150 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0370 | 187682 | 327500 | 100150 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-TE-0251-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 40 | PS5-79-IG-0012 | 1 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0251 | 238124 | 145852 | 100694 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0297-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 41 | PS5-79-IG-0012 | 2 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0297 | 239500 | 147040 | 98105 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0296-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 40 | PS5-79-IG-0012 | 3 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0296 | 238950 | 147040 | 98105 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0012-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0012 | 4 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0012 | 193255 | 141600 | 102632 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0259-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 28 | PS5-79-IG-0012 | 5 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0259 | 221999 | 146301 | 101291 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0257-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 55 | PS5-79-IG-0012 | 6 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0257 | 194796 | 146301 | 101820 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0258-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 62 | PS5-79-IG-0012 | 7 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0258 | 201705 | 137739 | 103147 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0098-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 63 | PS5-79-IG-0012 | 8 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0098 | 201783 | 140453 | 101661 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0300-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 64 | PS5-79-IG-0012 | 9 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0300 | 203210 | 137410 | 101000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0123-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 62 | PS5-79-IG-0012 | 10 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0123 | 201583 | 136797 | 101046 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0248-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 84 | PS5-79-IG-0012 | 11 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0248 | 189721 | 134450 | 102585 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0254-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 51 | PS5-79-IG-0012 | 12 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0254 | 197904 | 136994 | 103147 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0310-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 56 | PS5-79-IG-0012 | 13 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0310 | 197583 | 132505 | 100996 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0263-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 53 | PS5-79-IG-0012 | 14 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0263 | 196097 | 138065 | 102949 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0122-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 53 | PS5-79-IG-0012 | 15 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0122 | 197283 | 136797 | 101046 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0110-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 51 | PS5-79-IG-0012 | 16 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0110 | 197483 | 140453 | 101661 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0256-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 51 | PS5-79-IG-0012 | 17 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0256 | 195500 | 138926 | 103663 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0320-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 53 | PS5-79-IG-0012 | 18 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0320 | 196924 | 149401 | 102970 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0255-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0012 | 19 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0255 | 195500 | 137348 | 102544 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0017-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 54 | PS5-79-IG-0012 | 20 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0017 | 195005 | 144608 | 100459 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0250-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 56 | PS5-79-IG-0012 | 21 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0250 | 192234 | 145852 | 101629 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0249-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 58 | PS5-79-IG-0012 | 22 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0249 | 193751 | 144600 | 101577 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0318-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 58 | PS5-79-IG-0012 | 23 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0318 | 193236 | 144912 | 102055 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0309-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 79 | PS5-79-IG-0012 | 24 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0309 | 188178 | 133750 | 100454 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0018-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 80 | PS5-79-IG-0012 | 25 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0018 | 189525 | 133450 | 102280 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0130-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 87 | PS5-79-IG-0012 | 26 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0130 | 188765 | 129942 | 95737 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0299-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 52 | PS5-79-IG-0012 | 27 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0299 | 198900 | 137410 | 101000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0308-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 63 | PS5-79-IG-0012 | 28 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0308 | 197283 | 131351 | 100996 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0013-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 26 | PS5-79-IG-0012 | 29 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0013 | 232969 | 143608 | 100633 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0015-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 44 | PS5-79-IG-0012 | 30 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0015 | 241860 | 147400 | 96662 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0133-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 40 | PS5-79-IG-0012 | 31 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0133 | 242210 | 144975 | 102718 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0298-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 42 | PS5-79-IG-0012 | 32 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0298 | 241525 | 147040 | 98105 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
PS5-79-TE-0026-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 41 | PS5-79-IG-0012 | 33 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0026 | 240080 | 146600 | 100617 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-79-TE-0138-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 24 | PS5-79-IG-0012 | 34 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0138 | 225376 | 149272 | 100683 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
PS5-25-TE-0364-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 146 | PS5-79-IG-0012 | 37 | 237232 | 138099 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-25-TE-0364 | 237232 | 138099 | 100000 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
PS5-79-BE-0175-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 104 | PS5-79-IG-0009 | 40 | 188770 | 231192 | 100000 | Heat Tracing Panel | Outdoor | SIND-M20-Gland | M20 | PS5-79-BE-0175 | 162500 | 192500 | 103000 | Marshalling Box | Field | SIND M25 Metal Gland Alarm | M25 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-IP-9101-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 2 | PS5-79-BE-0175 | 40 | 162500 | 192500 | 103000 | Marshalling Box | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9101 | 162500 | 192500 | 103000 | ETS-05 | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-IP-9102-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 2 | PS5-79-BE-0175 | 40 | 162500 | 192500 | 103000 | Marshalling Box | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9102 | 162500 | 192500 | 103000 | ETS-05 | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-BE-0176-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 97 | PS5-79-IG-0007 | 40 | 183353 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND-M20-Gland | M20 | PS5-79-BE-0176 | 162300 | 204500 | 103000 | Marshalling Box | Field | SIND M25 Metal Gland Alarm | M25 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-IP-9103-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 2 | PS5-79-BE-0176 | 40 | 162300 | 204500 | 103000 | Marshalling Box | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9103 | 162300 | 204500 | 103000 | ETS-05 | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-IP-9104-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 2 | PS5-79-BE-0176 | 40 | 162300 | 204500 | 103000 | Marshalling Box | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9104 | 162300 | 204500 | 103000 | ETS-05 | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-BE-0177-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 86 | PS5-79-IG-0008 | 40 | 177936 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND-M20-Gland | M20 | PS5-79-BE-0177 | 162300 | 216500 | 103000 | Marshalling Box | Field | SIND M25 Metal Gland Alarm | M25 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-IP-9105-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 2 | PS5-79-BE-0177 | 40 | 162300 | 216500 | 103000 | Marshalling Box | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9105 | 162300 | 216500 | 103000 | ETS-05 | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-IP-9106-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 2 | PS5-79-BE-0177 | 40 | 162300 | 216500 | 103000 | Marshalling Box | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9106 | 162300 | 216500 | 103000 | ETS-05 | Field | SIND M20 Gland | M20 | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
PS5-79-TE-0175-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 124 | PS5-79-IG-0006 | 37 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0175 | 233965 | 166653 | 101323 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | 2nd Sensor on Pig Launcher | 01 | nVent
PS5-79-TE-0176-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 125 | PS5-79-IG-0006 | 38 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0176 | 235030 | 166577 | 101403 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | 2nd Sensor on Pig Launcher | 01 | nVent
PS5-79-TE-0178-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 118 | PS5-79-IG-0006 | 39 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0178 | 234537 | 174668 | 101310 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | 2nd Sensor on Pig Launcher | 01 | nVent
PS5-79-TE-0177-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | 3C | 1,5 | - | - | 119 | PS5-79-IG-0006 | 40 | 188770 | 235992 | 100000 | Heat Tracing Panel | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0177 | 233937 | 174668 | 101310 | PT100 Junction Box | Field | SIND M20 Gland | M25 | TZ-MID-68-NVS1-150360 | 14 | 2nd Sensor on Pig Launcher | 01 | nVent
| Page 17 | Mr Amruth Anarasi | MENTION CO-ORDINATE VALUES WITHOUT ANY DECIMALS (TYP.) | Comment accepted and incorporated | Mark Russell | 10/04/2025 | C
| Page 17 | Mr Amruth Anarasi | TYPICAL COMMENTS: 1.PE CABLES SHALL BE TAGED AS "PSX-79-IG-0001-CGXX". 2.FOR CONSISTENCY, ALL CO-ORDINATES SHOULD BE WITHOUT DECIMALS. 3.ALL SAMPLING CABINETS CABLE, JB & RTD TAGS SHALL BE AS PER SAMPLING TAG DETAILS. 4.IN REMARK COLUMN ADD WHICH CABLES BELONGS TO EXPORT PUMPS, SAMPLING CABINETS | Comment accepted and incorporated | Mark Russell | 10/04/2025 | C

## Instrument Cables
Cable No. | Voltage Grade | Type | System Voltage | Cores | Size (mm²) | Volt Drop (V) | Volt Drop (%) | Length (m) | Tag No. | CB No. | North | East | Elevation | Description | Location | Gland Type | Entry Thread | Tag No. | North | East | Elevation | Description | Location | Gland Type | Entry Thread | Cable Routing Drawing | Outer Diameter (mm) | Remarks | Rev | DPS

## Telecom Cables
Cable No. | Voltage Grade | Type | System Voltage | Cores | Size (mm²) | Volt Drop (V) | Volt Drop (%) | Length (m) | Tag No. | CB No. | North | East | Elevation | Description | Location | Gland Type | Entry Thread | Tag No. | North | East | Elevation | Description | Location | Gland Type | Entry Thread | Cable Routing Drawing | Outer Diameter (mm) | Remarks | Rev | DPS

## EHT Cables
Cable No. | Voltage Grade | Type | System Voltage | Cores | Size (mm²) | Volt Drop (V) | Volt Drop (%) | Length (m) | Tag No. | CB No. | North | East | Elevation | Description | Location | Gland Type | Entry Thread | Tag No. | North | East | Elevation | Description | Location | Gland Type | Entry Thread | Cable Routing Drawing | Outer Diameter (mm) | Remarks | Rev | DPS