## Electrical Cable Schedule
PROJECT NO. : 415000-00095
Cable Details | [9 empty] | From Equipment | [6 empty] | To Equipment
Sr. No. | Cable Tag. | Voltage Grade | Type | System Voltage | Drum No | Cores | Size (mm²) | Actual length laying done (m) | planned Length (m) | Tag No. | Cub. Ref | Description | G&T completed | Location | Gland Type | Entry Thread | Tag No. | Cub. Ref | Description | G&T Completed | Location | Gland Type | Entry Thread | Cable routing plan | Cable Routing Drawing | Outer Diameter (mm) | Remarks | Rev | DPS | Cable pulling date | Cable laying RFI Num | Drum tested RFI | Coiled length
1 | PS5-01-BE-0001 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 85 |  | PS5-05-IG-0004 | N/A | Outdoor Emergency Lighting DB - Field - (South Side) |  | Near Export pump area | Ind - IP 55 | M20 | PS5-01-BE-0001 | N/A | Power Supply JB ( Deluge skid MOV's ) |  | Near Deluge skid | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151117 | 18.1 | A=2 B=2 C=0 | 06 | EPS | 2026-05-10 00:00:00 | CPP-RFI-68-331-05-0260
2 | PS5-01-FCV- 0003A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 290 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-01-FCV- 0003A | N/A | Flow Control Valve |  | FIRE WATER PUMP AREA | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151115,151111, 151108,151109 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
3 | PS5-01-FCV- 0003B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 300 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-01-FCV- 0003B | N/A | Flow Control Valve |  | FIRE WATER PUMP AREA | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151115,151111, 151108,151109 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
4 | PS5-01-FCV- 0004A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 305 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-01-FCV- 0004A | N/A | Flow Control Valve |  | FIRE WATER PUMP AREA | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151115,151111, 151108,151109 | 18.1 | A=0 B=4 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
5 | PS5-01-FCV- 0004B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 310 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-01-FCV- 0004B | N/A | Flow Control Valve |  | FIRE WATER PUMP AREA | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151115,151111, 151108,151109 | 18.1 | A=0 B=4 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
6 | PS5-01-FIT- 0003A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 110 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-01-FIT- 0003A | N/A | Electromagnetic Flow Ind Transmitter |  | FIRE WATER PUMP AREA | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151109 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-04-16 00:00:00 | CPP-RFI-68-33/1-05-0219
7 | PS5-01-FIT- 0003B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 120 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-01-FIT- 0003B | N/A | Electromagnetic Flow Ind Transmitter |  | FIRE WATER PUMP AREA | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151109 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 2026-04-16 00:00:00 | CPP-RFI-68-33/1-05-0219
8 | PS5-01-FIT- 0004A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 120 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-01-FIT- 0004A | N/A | Electromagnetic Flow Ind Transmitter |  | FIRE WATER PUMP AREA | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151109 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 2026-04-16 00:00:00 | CPP-RFI-68-33/1-05-0219
9 | PS5-01-FIT- 0004B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 125 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-01-FIT- 0004B | N/A | Electromagnetic Flow Ind Transmitter |  | FIRE WATER PUMP AREA | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151109 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 2026-04-16 00:00:00 | CPP-RFI-68-33/1-05-0219
10 | PS5-01-IE- 0001A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 16 | 300 |  | PS5-61-IK-0001 | C0229 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-01-IE-0001A | N/A | Foam Package Pump Control Panel A |  | Foam Package | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117 | 26.4 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0278
11 | PS5-01-IE- 0001B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 16 | 300 |  | PS5-61-IK-0001 | C0225 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-01-IE-0001B | N/A | Foam Package Pump Control Panel B |  | Foam Package | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117 | 26.4 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0278
12 | PS5-01-IE- 0002A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 35 | 140 |  | PS5-61-IK-0001 | C0317 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-01-IE-0002A | N/A | Jockey Pump Control Panel A |  | Field_Fire Water Pump Area | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112,151109 | 29.3 | A=0 B=1 C=0 | 05 | EPS | 2026-04-16 00:00:00 | CPP-RFI-68-33/1-05-0219
13 | PS5-01-IE- 0002B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 35 | 145 |  | PS5-61-IK-0001 | C0311 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-01-IE-0002B | N/A | Jockey Pump Control Panel B |  | Field_Fire Water Pump Area | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112,151109 | 29.3 | A=0 B=1 C=0 | 05 | EPS | 2026-04-16 00:00:00 | CPP-RFI-68-33/1-05-0219
14 | PS5-01-IE- 0009A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 6 | 135 |  | PS5-61-IK-0001 | C0216 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-01-IE-0009A | N/A | Fire Water pump LCP A |  | Field_Fire Water Pump Area | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112,151109 | 22.9 | A=0 B=1 C=0 | 05 | EPS | 2026-04-16 00:00:00 | CPP-RFI-68-33/1-05-0219
15 | PS5-01-IE- 0009B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 6 | 140 |  | PS5-61-IK-0001 | B0331 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-01-IE-0009B | N/A | Fire Water pump LCP B |  | Field_Fire Water Pump Area | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112,151109 | 22.9 | A=0 B=1 C=0 | 05 | EPS | 2026-04-16 00:00:00 | CPP-RFI-68-33/1-05-0219
16 | PS5-01-IG-0001 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 95 | 130 |  | PS5-61-IK-0003 | C0211 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 | PS5-01-IG-0001 | N/A | Water Mist system Distribution board |  | Generator Electrical Building | Ind - IP 55 | M50 / M63 |  | TZ-MID-68-WPR2- 151167, 151118 | 49.5 | LV Power - Water mist system MDB (Refer Note 13) | 05 | EPS
17 | PS5-01-LA-0001 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 0 |  | PS5-06-IG- 0001A | N/A | AC UPS Distribution Board (A) Dual supply loads - 230VAC, 50Hz, 320A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-01-LA-0001 | N/A | HIPPS (OPPS) CABINET |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 18.5 | UPS A_OPPS cabinet ( Refer Note 06) | 06 | EITS
18 | PS5-01-LA-0001 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 0 |  | PS5-06-IG- 0001B | N/A | AC UPS Distribution Board (B) Dual supply loads - 230VAC, 50Hz, 320A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-01-LA-0001 | N/A | HIPPS (OPPS) CABINET |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 18.5 | UPS B_OPPS cabinet ( Refer Note 06) | 06 | EITS
19 | PS5-01-LA-0001 -CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 0 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-01-LA-0001 | N/A | HIPPS (OPPS) CABINET |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | Auxillary supply to OPPS cabinet ( Refer Note 06) | 06 | EITS
20 | PS5-01-LB-0004 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-01-LB-0004 | N/A | Gaseous package system skid - control panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A_Gaseous System Skid | 06 | EPS
21 | PS5-01-LB-0004 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-01-LB-0004 | N/A | Gaseous package system skid - control panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B_Gaseous System Skid | 06 | EPS
22 | PS5-01-LB-0004 -CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 55 |  | PS5-61-IG-0016 | N/A | Generator Electrical Building Normal L&SP Distribution Board PS-5 |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-01-LB-0004 | N/A | Gaseous package system skid - control panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.5 | A=0 B=2 C=0 | 06 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
23 | PS5-01-MOV- 8701-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 80 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-01-MOV- 8701 | N/A | Motor Operated Valve |  | FOAM PACKAGE | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117 | 18.1 | MOV DB outgoing to MOV (Refer Note 13) | 06 | EPS
24 | PS5-02-SWSI- 0001-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 240 |  | PS5-05-IG-0006 | N/A | Outdoor Emergency Lighting DB - Field - (North Side) |  | Near EDG package | Ind - IP 55 | M20 | PS5-02-SWSI- 0001 | N/A | Illuminated Windsock |  | Near Workshop | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151111,151108,151107, 151105 | 17.2 | A=1 B=2 C=0 | 07 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
25 | PS5-02-SWSI- 0003-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 90 |  | PS5-05-IG-0006 | N/A | Outdoor Emergency Lighting DB - Field - (North Side) |  | Near EDG package | Ind - IP 55 | M20 | PS5-02-SWSI- 0003 | N/A | Illuminated Windsock |  | On Piperack Near E- House | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151111,151115 | 17.2 | Windsock Emergency Power Supply | 07 | EPS
26 | PS5-03-GDLHP- 0137-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 240 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-03-GDLHP- 0137 | N/A | Liquid Hydrocarbon Detector |  | CFO Storage Tank Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151115 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0278
27 | PS5-03-GDLHP- 0142-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 200 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-03-GDLHP- 0142 | N/A | Liquid Hydrocarbon Detector |  | CFO Storage Tank Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151115 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0278
28 | PS5-03-GDLHP- 0143-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 320 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-03-GDLHP- 0143 | N/A | Liquid Hydrocarbon Detector |  | Export Pump Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151115, 151117, 151114 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0278
29 | PS5-03-GDLHP- 0144-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 290 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-03-GDLHP- 0144 | N/A | Liquid Hydrocarbon Detector |  | Export Pump Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151115, 151117, 151114 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0278
30 | PS5-03-GDLHP- 0146-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 340 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-03-GDLHP- 0146 | N/A | Liquid Hydrocarbon Detector |  | LAUNCHER/RECEIVE R Area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151115, 151117, 151114, 151113 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0278
31 | PS5-03-GDLHP- 0147-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 310 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-03-GDLHP- 0147 | N/A | Liquid Hydrocarbon Detector |  | Export Pump Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151115, 151117, 151114 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0278
32 | PS5-03-GDLHP- 0149-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 300 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-03-GDLHP- 0149 | N/A | Liquid Hydrocarbon Detector |  | Export Pump Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151115, 151117, 151114 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0278
33 | PS5-03-GDLHP- 0150-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 310 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-03-GDLHP- 0150 | N/A | Liquid Hydrocarbon Detector |  | Export Pump Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151115, 151117, 151114 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0278
34 | PS5-03-GDLHP- 0401-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 280 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-03-GDLHP- 0401 | N/A | Liquid Hydrocarbon Detector |  | Diesel Fuel Storage Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151108, 151107 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0278
35 | PS5-03-SEA- 0002-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 15 |  | PS5-06-IG-0006 | N/A | AC UPS DB - Guard House |  | Guard House | Ind - IP 55 | M20 | PS5-03-SEA- 0002 | N/A | LFAP - Guard House |  | Guard House | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151106 | 17.2 | LFAP - Guard House Building (Non-Redundant UPS supply) | 06 | EPS
36 | PS5-03-SEA- 0003-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 15 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-03-SEA- 0003 | N/A | LFAP Panel - Power Generator building |  | Generator electrical building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | LFAP UPS SUPPLY | 06 | EPS
37 | PS5-05-BE-0001 -CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 240 | 18 |  | PS5-05-DG-8100 | N/A | Emergency Diesel Engine Generator - Field |  | EDG Package | Ind - IP 55 | M25 | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151111 | 24 | A=1 B=2 C=0 | 05 | Contract or | 2026-05-03 00:00:00 | CPP-RFI-68-331-05-0243
38 | PS5-05-BE-0001 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 18 |  | PS5-05-DG-8100 | N/A | Emergency Diesel Engine Generator - Field |  | EDG Package | Ind - IP 55 | M50 | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-12 00:00:00 | CPP-RFI-68-331-05-0264
39 | PS5-05-BE-0001 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 18 |  | PS5-05-DG-8100 | N/A | Emergency Diesel Engine Generator - Field |  | EDG Package | Ind - IP 55 | M50 | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-12 00:00:00 | CPP-RFI-68-331-05-0264
40 | PS5-05-BE-0001 -CL03 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 18 |  | PS5-05-DG-8100 | N/A | Emergency Diesel Engine Generator - Field |  | EDG Package | Ind - IP 55 | M50 | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-12 00:00:00 | CPP-RFI-68-331-05-0264
41 | PS5-05-BE-0001 -CL04 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 18 |  | PS5-05-DG-8100 | N/A | Emergency Diesel Engine Generator - Field |  | EDG Package | Ind - IP 55 | M50 | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-12 00:00:00 | CPP-RFI-68-331-05-0264
42 | PS5-05-BE-0001 -CL05 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 18 |  | PS5-05-DG-8100 | N/A | Emergency Diesel Engine Generator - Field |  | EDG Package | Ind - IP 55 | M50 | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-12 00:00:00 | CPP-RFI-68-331-05-0264
43 | PS5-05-BE-0001 -CL06 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 18 |  | PS5-05-DG-8100 | N/A | Emergency Diesel Engine Generator - Field |  | EDG Package | Ind - IP 55 | M50 | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-12 00:00:00 | CPP-RFI-68-331-05-0264
44 | PS5-05-BE-0001 -CL07 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 18 |  | PS5-05-DG-8100 | N/A | Emergency Diesel Engine Generator - Field |  | EDG Package | Ind - IP 55 | M50 | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-12 00:00:00 | CPP-RFI-68-331-05-0264
45 | PS5-05-BE-0001 -CL08 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 18 |  | PS5-05-DG-8100 | N/A | Emergency Diesel Engine Generator - Field |  | EDG Package | Ind - IP 55 | M50 | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-12 00:00:00 | CPP-RFI-68-331-05-0264
46 | PS5-05-BE-0001 -CL09 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 18 |  | PS5-05-DG-8100 | N/A | Emergency Diesel Engine Generator - Field |  | EDG Package | Ind - IP 55 | M50 | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-12 00:00:00 | CPP-RFI-68-331-05-0264
47 | PS5-05-BE-0001 -CL10 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 18 |  | PS5-05-DG-8100 | N/A | Emergency Diesel Engine Generator - Field |  | EDG Package | Ind - IP 55 | M50 | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-12 00:00:00 | CPP-RFI-68-331-05-0264
48 | PS5-05-BE-0001 -CL11 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 18 |  | PS5-05-DG-8100 | N/A | Emergency Diesel Engine Generator - Field |  | EDG Package | Ind - IP 55 | M50 | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-12 00:00:00 | CPP-RFI-68-331-05-0264
49 | PS5-05-IE-8100- CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 35 |  | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
50 | PS5-05-IE-8100- CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 35 |  | PS5-61-IK-0003 | AB01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
51 | PS5-05-IE-8100- CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 35 |  | PS5-61-IK-0003 | AB01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
52 | PS5-05-IE-8100- CD04 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 35 |  | PS5-61-IK-0003 | BC | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
53 | PS5-05-IE-8100- CD05 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 35 |  | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
54 | PS5-05-IE-8100- CD06 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 35 |  | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
55 | PS5-05-IE-8100- CD07 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | - |  | 7C | 2.5 | 35 |  | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
56 | PS5-05-IE-8100- CD08 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 5C | 2.5 | 35 |  | PS5-61-IK-0003 | AB01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 19.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-30 00:00:00 | CPP-RFI-68-331-05-0391
57 | PS5-05-IE-8100- CD09 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 145 |  | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M32 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112, 151116 | 29.7 | A=1 B=2 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-07-0248
58 | PS5-05-IE-8100- CD10 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 12C | 2.5 | 35 |  | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 25.3 | A=0 B=2 C=0 | 05 | EPS | 2026-06-30 00:00:00 | CPP-RFI-68-331-05-0391
59 | PS5-05-IE-8100- CD11 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 35 |  | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
60 | PS5-05-IE-8100- CD12 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 12C | 2.5 | 35 |  | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 25.3 | A=0 B=2 C=0 | 05 | EPS | 2026-06-30 00:00:00 | CPP-RFI-68-331-05-0391
61 | PS5-05-IE-8100- CD13 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 5C | 2.5 | 35 |  | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 19.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-30 00:00:00 | CPP-RFI-68-331-05-0391
62 | PS5-05-IE-8100- CD14 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 35 |  | PS5-61-IK-0003 | AB01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-30 00:00:00 | CPP-RFI-68-331-05-0391
63 | PS5-05-IE-8100- CD15 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 12C | 2.5 | 35 |  | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 25.3 | A=0 B=2 C=0 | 05 | EPS | 2026-06-30 00:00:00 | CPP-RFI-68-331-05-0391
64 | PS5-05-IE-8100- CD16 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 5C | 2.5 | 35 |  | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 19.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-30 00:00:00 | CPP-RFI-68-331-05-0391
65 | PS5-05-IE-8100- CD17 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 35 |  | PS5-61-IK-0003 | BC | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-30 00:00:00 | CPP-RFI-68-331-05-0391
66 | PS5-05-IE-8100- CD18 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 35 |  | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
67 | PS5-05-IE-8100- CD19 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 35 |  | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
68 | PS5-05-IE-8100- CD20 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 35 |  | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
69 | PS5-05-IE-8100- CD21 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 35 |  | PS5-61-IK-0003 | AB01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-30 00:00:00 | CPP-RFI-68-331-05-0391
70 | PS5-05-IE-8100- CD22 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 5C | 2.5 | 145 |  | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116 | 19.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0278
71 | PS5-05-IE-8100- | 0.6/1KV | CU/PVC/LSZH/G | 48V DC |  | 12C | 2.5 | 0 |  | PS5-61-IK-0003 | AB01 | 0.4kV Switchboard |  | Generator Electrical | Ind - IP | M25 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151167 | 25.3 | EDG Ready to Start, EDG Running Status, UCP Selector Automatic Position | 05 | EPS
72 | PS5-05-IE-8100- CD24 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 5C | 2.5 | 145 |  | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116 | 19.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0278
73 | PS5-05-IE-8100- CD25 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 15 |  | PS5-60-IE-0004 | N/A | Master Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
74 | PS5-05-IE-8100- CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 30 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 18.5 | UPS A - 230V | 05 | EPS
75 | PS5-05-IE-8100- CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 30 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-05-IE-8100 | N/A | Unit Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 18.5 | UPS B -230V | 05 | EPS
76 | PS5-05-IG-0004 -CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 3C | 2.5 | 270 |  | PS5-61-IE-0003 | N/A | ECS 3 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-05-IG-0004 | N/A | Outdoor Emergency Lighting DB - Field - (South Side) |  | Near Export pump area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151115, 151117 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 30-May-2026 | CPP-RFI-68-33/1-07-0307
77 | PS5-05-IG-0004 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 50 | 270 |  | PS5-61-IK-0001 | C0327 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 | PS5-05-IG-0004 | N/A | Outdoor Emergency Lighting DB - Field - (South Side) |  | Near Export pump area | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112, 151111, 151115, 151117 | 39 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
78 | PS5-05-IG-0006 -CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 3C | 2.5 | 130 |  | PS5-61-IE-0003 | N/A | ECS 3 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-05-IG-0006 | N/A | Outdoor Emergency Lighting DB - Field - (North Side) |  | Near EDG package | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151111 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 30-May-2026 | CPP-RFI-68-33/1-07-0307
79 | PS5-05-IG-0006 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 25 | 130 |  | PS5-61-IK-0001 | C0331 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-05-IG-0006 | N/A | Outdoor Emergency Lighting DB - Field - (North Side) |  | Near EDG package | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112, 151111 | 31.7 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
80 | PS5-05-IG-0009 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 25 | 200 |  | PS5-61-IK-0003 | C0207 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-05-IG-0009 | N/A | EDG - Power Distribution Panel |  | EDG Skid | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167, 151116, 151112, 151111 | 31.7 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
81 | PS5-05-IG-0009 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 16 | 245 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IG-0009 | N/A | EDG - Power Distribution Panel |  | EDG Skid | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167, 151116, 151112, 151111 | 24.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
82 | PS5-05-IG-0025 -CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 3C | 2.5 | 200 |  | PS5-61-IE-0003 | N/A | ECS 3 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-05-IG-0025 | N/A | Indoor Emergency L&SP DB - Generator Building |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116 | 17.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0261
83 | PS5-05-IG-0025 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 10 | 100 |  | PS5-61-IK-0003 | C0227 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IG-0025 | N/A | Indoor Emergency L&SP DB - Generator Building |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 25.6 | A=1 B=2 C=0 | 05 | EPS | 2026-06-04 00:00:00 | CPP-RFI-68-33/1-05-0309
84 | PS5-05-IG-0026 -CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 3C | 2.5 | 155 |  | PS5-61-IE-0003 | N/A | ECS 3 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-05-IG-0026 | N/A | Indoor Emergency L&SP DB - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116 | 17.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0261
85 | PS5-05-IG-0026 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 6 | 35 |  | PS5-61-IK-0003 | C0231 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-05-IG-0026 | N/A | Indoor Emergency L&SP DB - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 22.9 | A=1 B=2 C=0 | 05 | EPS | 2026-06-04 00:00:00 | CPP-RFI-68-33/1-05-0309
86 | PS5-06-GB- 0003-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 70 | 35 |  | PS5-06-GU- 0003A | A1 | AC UPS A - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-06-GB-0003 | N/A | SMC Battery cubicle |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17 | UPS A to Battery SMC Battery cubicle_PE Cable | 06 | Contract or
87 | PS5-06-GB- 0003-CL01 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 230V DC |  | 1C | 150 | 35 |  | PS5-06-GU- 0003A | A1 | AC UPS A - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-06-GB-0003 | N/A | SMC Battery cubicle |  | Generator Electrical Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167 | 28.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
88 | PS5-06-GB- 0003-CL02 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 230V DC |  | 1C | 150 | 35 |  | PS5-06-GU- 0003A | A1 | AC UPS A - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-06-GB-0003 | N/A | SMC Battery cubicle |  | Generator Electrical Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167 | 28.2 | A=0 B=2 C=0 | 06 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
89 | PS5-06-GB- 0003-CL03 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 230V DC |  | 1C | 150 | 35 |  | PS5-06-GU- 0003A | A1 | AC UPS A - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-06-GB-0003 | N/A | SMC Battery cubicle |  | Generator Electrical Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167 | 28.2 | A=0 B=2 C=0 | 06 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
90 | PS5-06-GB- 0003-CL04 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 230V DC |  | 1C | 150 | 35 |  | PS5-06-GU- 0003A | A1 | AC UPS A - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-06-GB-0003 | N/A | SMC Battery cubicle |  | Generator Electrical Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167 | 28.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
91 | PS5-06-GB- 0003-CL05 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 230V DC |  | 1C | 150 | 35 |  | PS5-06-GU- 0003A | A1 | AC UPS A - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-06-GB-0003 | N/A | SMC Battery cubicle |  | Generator Electrical Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167 | 28.2 | A=0 B=2 C=0 | 06 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
92 | PS5-06-GB- 0003-CL06 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 230V DC |  | 1C | 150 | 35 |  | PS5-06-GU- 0003A | A1 | AC UPS A - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-06-GB-0003 | N/A | SMC Battery cubicle |  | Generator Electrical Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167 | 28.2 | A=0 B=2 C=0 | 06 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
93 | PS5-06-GU- 0003A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 5C | 2.5 | 190 |  | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-06-GU- 0003A | A3 | AC UPS A - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151118 | 19.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0278
94 | PS5-06-GU- 0003A-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 35 |  | PS5-06-GB-0003 | B1 | SMC Battery cubicle |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-06-GU- 0003A | A1 | AC UPS A - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151118 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
95 | PS5-06-GU- 0003A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 150 | 75 |  | PS5-61-IK-0003 | B0231 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 | PS5-06-GU- 0003A | A2 | AC UPS A - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151167 | 50.9 | A=0 B=2 C=0 | 05 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
96 | PS5-06-GU- 0003B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 5C | 2.5 | 190 |  | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-06-GU- 0003B | A8 | AC UPS B - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151118 | 19.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-12 00:00:00 | CPP-RFI-68-331-07-0286
97 | PS5-06-GU- 0003B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 150 | 75 |  | PS5-61-IK-0003 | C0201 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 | PS5-06-GU- 0003B | A7 | AC UPS B - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151167 | 50.9 | A=0 B=2 C=0 | 05 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
98 | PS5-06-GU- 0003C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 240 | 75 |  | PS5-61-IK-0003 | C0219 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M75 | PS5-06-GU- 0003C | A4 | AC UPS Bypass - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M75 |  | TZ-MID-68-WPR2- 151167 | 75.1 | A=0 B=2 C=0 | 05 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
99 | PS5-06-GU- 0005-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 15 |  | PS5-05-IG-0007 | N/A | Indoor Emergency L&SP DB - Guard House |  | Guard House | Ind - IP 55 | M20 | PS5-06-GU-0005 | N/A | AC UPS - Guard House |  | Indoor Guard house | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151185 | 17.2 | LV Power_UPS | 07 | EPS
100 | PS5-06-IG- 0004A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 5C | 2.5 | 165 |  | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151118 | 19.6 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
101 | PS5-06-IG- 0004A-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 95 | 40 |  | PS5-06-GU- 0003A | A4 | AC UPS A - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 18 | PE Cable_UPS DB A | 06 | Contract or
102 | PS5-06-IG- 0004A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 230V AC |  | 1C | 150 | 40 |  | PS5-06-GU- 0003A | A4 | AC UPS A - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167 | 28.2 | A=0 B=2 C=0 | 06 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
103 | PS5-06-IG- 0004A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 230V AC |  | 1C | 150 | 40 |  | PS5-06-GU- 0003A | A4 | AC UPS A - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167 | 28.2 | A=0 B=2 C=0 | 06 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
104 | PS5-06-IG- 0004A-CL03 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 230V AC |  | 1C | 150 | 40 |  | PS5-06-GU- 0003A | A4 | AC UPS A - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167 | 28.2 | A=0 B=2 C=0 | 06 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
105 | PS5-06-IG- 0004A-CL04 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 230V AC |  | 1C | 150 | 40 |  | PS5-06-GU- 0003A | A4 | AC UPS A - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167 | 28.2 | A=0 B=2 C=0 | 06 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
106 | PS5-06-IG- 0004B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 5C | 2.5 | 165 |  | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151118 | 19.6 | A=1 B=2 C=0 | 06 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-07-0247
107 | PS5-06-IG- 0004B-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 95 | 40 |  | PS5-06-GU- 0003B | A4 | AC UPS B - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 18 | PE Cable_UPS DB B | 06 | Contract or
108 | PS5-06-IG- 0004B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 230V AC |  | 1C | 150 | 40 |  | PS5-06-GU- 0003B | A4 | AC UPS B - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167 | 28.2 | A=0 B=2 C=0 | 06 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
109 | PS5-06-IG- 0004B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 230V AC |  | 1C | 150 | 40 |  | PS5-06-GU- 0003B | A4 | AC UPS B - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167 | 28.2 | A=0 B=2 C=0 | 06 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
110 | PS5-06-IG- 0004B-CL03 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 230V AC |  | 1C | 150 | 40 |  | PS5-06-GU- 0003B | A4 | AC UPS B - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167 | 28.2 | A=0 B=2 C=0 | 06 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
111 | PS5-06-IG- 0004B-CL04 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 230V AC |  | 1C | 150 | 40 |  | PS5-06-GU- 0003B | A4 | AC UPS B - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167 | 28.2 | A=0 B=2 C=0 | 06 | EPS | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0298
112 | PS5-08-01FB- 0901-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 125 |  | PS5-08-13CB- 1001 | N/A | TELECOM SII SP3 SAF Cabinet |  | EITS Building |  |  | PS5-08-01FB- 0901 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112, 151116 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
113 | PS5-08-01FB- 0902-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 60 |  | PS5-08-01FB- 0901 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 0902 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=2 B=2 C=0 | 06 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
114 | PS5-08-01FB- 0903-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 70 |  | PS5-08-01FB- 0902 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 0903 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
115 | PS5-08-01FB- 0904-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 60 |  | PS5-08-01FB- 0903 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 0904 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=2 B=2 C=0 | 06 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
116 | PS5-08-01FB- 0905-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 15 |  | PS5-08-01FB- 0904 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 0905 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
117 | PS5-08-01FB- 0906-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 70 |  | PS5-08-01FB- 0905 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 0906 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
118 | PS5-08-01FB- 0907-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 60 |  | PS5-08-01FB- 0906 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 0907 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
119 | PS5-08-01FB- 0908-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 15 |  | PS5-08-01FB- 0907 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 0908 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
120 | PS5-08-01FB- 0909-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 70 |  | PS5-08-01FB- 0908 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 0909 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
121 | PS5-08-01FB- 0910-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 60 |  | PS5-08-01FB- 0909 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 0910 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
122 | PS5-08-01FB- 0911-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 15 |  | PS5-08-01FB- 0910 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 0911 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
123 | PS5-08-01FB- 0912-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 70 |  | PS5-08-01FB- 0911 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 0912 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
124 | PS5-08-01FB- 0913-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 90 |  | PS5-08-01FB- 0912 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 0913 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=1 B=2 C=0 | 06 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0210
125 | PS5-08-01FB- 0913-CS02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 130 |  | PS5-08-01FB- 0913 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-13CB- 1001 | N/A | TELECOM SII SP3 SAF Cabinet |  | EITS Building |  |  |  | TZ-MID-68-WPR2- 151116, 151112 | 17.2 | A=2 B=2 C=0 | 06 | EPS | 2026-05-10 00:00:00 | CPP-RFI-68-331-05-0260
126 | PS5-08-01FB- 1001-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 150 |  | PS5-08-13CB- 1001 | N/A | TELECOM SII SP3 SAF Cabinet |  | EITS Building |  |  | PS5-08-01FB- 1001 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112, 151116 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
127 | PS5-08-01FB- 1002-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 50 |  | PS5-08-01FB- 1001 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 1002 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
128 | PS5-08-01FB- 1003-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-08-01FB- 1002 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 1003 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
129 | PS5-08-01FB- 1004-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 20 |  | PS5-08-01FB- 1003 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 1004 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
130 | PS5-08-01FB- 1005-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 95 |  | PS5-08-01FB- 1004 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 1005 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
131 | PS5-08-01FB- 1006-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 80 |  | PS5-08-01FB- 1005 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 1006 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
132 | PS5-08-01FB- 1007-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 20 |  | PS5-08-01FB- 1006 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 1007 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=2 B=2 C=0 | 06 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
133 | PS5-08-01FB- 1008-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 95 |  | PS5-08-01FB- 1007 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 1008 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
134 | PS5-08-01FB- 1009-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 95 |  | PS5-08-01FB- 1008 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 1009 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
135 | PS5-08-01FB- 1010-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 20 |  | PS5-08-01FB- 1009 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 1010 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=2 B=2 C=0 | 06 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
136 | PS5-08-01FB- 1011-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 95 |  | PS5-08-01FB- 1010 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 1011 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
137 | PS5-08-01FB- 1012-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 95 |  | PS5-08-01FB- 1011 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 1012 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
138 | PS5-08-01FB- 1013-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 20 |  | PS5-08-01FB- 1012 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-01FB- 1013 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
139 | PS5-08-01FB- 1013-CS02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 170 |  | PS5-08-01FB- 1013 | N/A | PAGA Flashing Beacon |  | Power generator building area | Ex'd - IP 66 | M20 | PS5-08-13CB- 1001 | N/A | TELECOM SII SP3 SAF Cabinet |  | EITS Building |  |  |  | TZ-MID-68-WPR2- 151116, 151112 | 17.2 | A=2 B=2 C=0 | 06 | EPS | 2026-05-10 00:00:00 | CPP-RFI-68-331-05-0260
140 | PS5-08-01FB- 1101-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 170 |  | PS5-08-13CB- 1001 | N/A | TELECOM SII SP3 SAF Cabinet |  | EITS Building |  |  | PS5-08-01FB- 1101 | N/A | PAGA Flashing Beacon (Safe Area) |  | Field | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112, 151116 | 17.2 | A=1 B=2 C=0 | 06 | EPS | 2026-05-10 00:00:00 | CPP-RFI-68-331-05-0260
141 | PS5-08-01FB- 1102-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 150 |  | PS5-08-01FB- 1101 | N/A | PAGA Flashing Beacon (Safe Area) |  | Field | Ex'd - IP 66 | M20 | PS5-08-01FB- 1102 | N/A | PAGA Flashing Beacon (Safe Area) |  | Field | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=2 B=1 C=0 | 06 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
142 | PS5-08-01FB- 1103-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 80 |  | PS5-08-01FB- 1102 | N/A | PAGA Flashing Beacon (Safe Area) |  | Field | Ex'd - IP 66 | M20 | PS5-08-01FB- 1103 | N/A | PAGA Flashing Beacon (Safe Area) |  | Field | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=2 B=1 C=0 | 06 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
143 | PS5-08-01FB- 1104-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 150 |  | PS5-08-01FB- 1103 | N/A | PAGA Flashing Beacon (Safe Area) |  | Field | Ex'd - IP 66 | M20 | PS5-08-01FB- 1104 | N/A | PAGA Flashing Beacon (Safe Area) |  | Field | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116, 151112 | 17.2 | A=1 B=1 C=0 | 06 | EPS
144 | PS5-08-01FB- 1105-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 175 |  | PS5-08-01FB- 1104 | N/A | PAGA Flashing Beacon (Safe Area) |  | Field | Ex'd - IP 66 | M20 | PS5-08-01FB- 1105 | N/A | PAGA Flashing Beacon (Safe Area) |  | Field | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151116, 151118 | 17.2 | A=2 B=2 C=0 | 06 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
145 | PS5-08-01FB- 1106-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 80 |  | PS5-08-01FB- 1105 | N/A | PAGA Flashing Beacon (Safe Area) |  | Field | Ex'd - IP 66 | M20 | PS5-08-01FB- 1106 | N/A | PAGA Flashing Beacon (Safe Area) |  | Field | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151118 | 17.2 | A=1 B=1 C=0 | 06 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
146 | PS5-08-01FB- 1106-CS02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 230 |  | PS5-08-01FB- 1106 | N/A | PAGA Flashing Beacon (Safe Area) |  | Field | Ex'd - IP 66 | M20 | PS5-08-13CB- 1001 | N/A | TELECOM SII SP3 SAF Cabinet |  | EITS Building |  |  |  | TZ-MID-68-WPR2- 151116, 151112 | 17.2 | A=2 B=2 C=0 | 06 | EPS | 2026-05-12 00:00:00 | CPP-RFI-68-331-05-0264
147 | PS5-08-03FB- 0001-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 200 |  | PS5-08-11CB- 1001 | N/A | TELECOM SIE Cabinet |  | EITS Building |  |  | PS5-08-03FB- 0001 | N/A | TELEPHONE WITH BEACON/SOUNDER |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151108 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
148 | PS5-08-03FB- 0002-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 240 |  | PS5-08-11CB- 1001 | N/A | TELECOM SIE Cabinet |  | EITS Building |  |  | PS5-08-03FB- 0002 | N/A | TELEPHONE WITH BEACON/SOUNDER |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151108, 151105 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
149 | PS5-08-03FB- 0003-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 100 |  | PS5-08-11CB- 1201 | N/A | TELECOM SIE Cabinet |  | Office Building |  |  | PS5-08-03FB- 0003 | N/A | TELEPHONE WITH BEACON/SOUNDER |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151106 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
150 | PS5-08-03FB- 0004-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 170 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-03FB- 0004 | N/A | TELEPHONE WITH BEACON/SOUNDER |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116, 151118, 151122 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
151 | PS5-08-03FB- 0101-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 70 |  | PS5-08-11CB- 1001 | N/A | TELECOM SIE Cabinet |  | EITS Building |  |  | PS5-08-03FB- 0101 | N/A | TELEPHONE WITH BEACON/SOUNDER |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
152 | PS5-08-03FB- 0102-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 100 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-03FB- 0102 | N/A | TELEPHONE WITH BEACON /SOUNDER |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116, 151118 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
153 | PS5-08-03FB- 0103-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 285 |  | PS5-08-11CB- 1001 | N/A | TELECOM SIE Cabinet |  | EITS Building |  |  | PS5-08-03FB- 0103 | N/A | TELEPHONE WITH BEACON/SOUNDER |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151108, 151107, 151110 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
154 | PS5-08-03FB- 1903-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 55 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-03FB- 1903 | N/A | TELEPHONE WITH BEACON/SOUNDER |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=2 B=2 C=0 | 06 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
155 | PS5-08-03FB- 1904-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 115 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-03FB- 1904 | N/A | TELEPHONE WITH BEACON/SOUNDER |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
156 | PS5-08-11CB- 1501-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 30 |  | PS5-06-IG-0006 | N/A | AC UPS DB - Guard House |  | Guard House | Ind - IP 55 | M20 | PS5-08-11CB- 1501 | N/A | TELECOM SIE Cabinet |  | Guard House Building |  |  |  | TZ-MID-68-WPR2- 151112 | 17.2 | Telecom LV UPS Cable | 06 | EPS
157 | PS5-08-11CB- 1901-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  |  | TZ-MID-68-WPR2- 151167 | 17.2 | Telecom LV UPS Cable | 06 | EPS
158 | PS5-08-11CB- 1901-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  |  | TZ-MID-68-WPR2- 151167 | 17.2 | Telecom LV UPS Cable | 06 | EPS
159 | PS5-08-11CB- 1901-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-61-IG-0016 | N/A | Generator Electrical Building Normal L&SP Distribution Board PS-5 |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Normal Auxiliary Supply | 06 | EPS
160 | PS5-08-12BT- 0001-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 370 |  | PS5-08-11CB- 1201 | N/A | TELECOM SIE Cabinet |  | Office Building |  |  | PS5-08-12BT- 0001 | N/A | WAP JUNCTION BOX-1 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151106, 151108, 151107, 151105 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
161 | PS5-08-12BT- 0104-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 280 |  | PS5-08-11CB- 1001 | N/A | TELECOM SIE Cabinet |  | EITS Building |  |  | PS5-08-12BT- 0104 | N/A | WAP JUNCTION BOX-4 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151108, 151107 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
162 | PS5-08-12BT- 0105-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 255 |  | PS5-08-11CB- 1001 | N/A | TELECOM SIE Cabinet |  | EITS Building |  |  | PS5-08-12BT- 0105 | N/A | WAP JUNCTION BOX-5 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151108 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
163 | PS5-08-12BT- 0106-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 60 |  | PS5-08-11CB- 1001 | N/A | TELECOM SIE Cabinet |  | EITS Building |  |  | PS5-08-12BT- 0106 | N/A | WAP JUNCTION BOX-6 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
164 | PS5-08-12BT- 0107-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 340 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-12BT- 0107 | N/A | WAP JUNCTION BOX-7 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116, 151118, 151117, 151115, 151114, 151113 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
165 | PS5-08-12BT- 0108-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 230 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-12BT- 0108 | N/A | WAP JUNCTION BOX-8 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116, 151118, 151117, 151115 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
166 | PS5-08-12BT- 0109-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 230 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-12BT- 0109 | N/A | WAP JUNCTION BOX-9 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116, 151118, 151117, 151115 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
167 | PS5-08-12BT- 1903-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 85 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-12BT- 1903 | N/A | WAP JUNCTION BOX-11 |  | Power generator building area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
168 | PS5-08-12BT- 1904-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 110 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-12BT- 1904 | N/A | WAP JUNCTION BOX-13 |  | Power generator building area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
169 | PS5-08-15CP- 0001-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 430 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-15CP- 0001 | N/A | Control Panel-1 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116, 151118, 151117, 151114, 151119 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
170 | PS5-08-15CP- 0002-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 370 |  | PS5-08-15CB- 1001 | N/A | TELECOM SII SP3 SEC Cabinet |  | EITS Building |  |  | PS5-08-15CP- 0002 | N/A | Control Panel-2 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151119,151107, 151108, 151111, 151112 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
171 | PS5-08-15CP- 0003-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 280 |  | PS5-08-11CB- 1201 | N/A | TELECOM SIE Cabinet |  | Office Building |  |  | PS5-08-15CP- 0003 | N/A | Control Panel-3 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151106,151105 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
172 | PS5-08-15CP- 0004-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 170 |  | PS5-08-11CB- 1201 | N/A | TELECOM SIE Cabinet |  | Office Building |  |  | PS5-08-15CP- 0004 | N/A | Control Panel-4 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151106 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
173 | PS5-08-15CP- 0005-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 150 |  | PS5-08-15CB- 1001 | N/A | TELECOM SII SP3 SEC Cabinet |  | EITS Building |  |  | PS5-08-15CP- 0005 | N/A | Control Panel-5 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151109, 151112 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
174 | PS5-08-15CP- 0006-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 150 |  | PS5-08-15CB- 1001 | N/A | TELECOM SII SP3 SEC Cabinet |  | EITS Building |  |  | PS5-08-15CP- 0006 | N/A | Control Panel-6 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
175 | PS5-08-15CP- 0007-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 205 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-15CP- 0007 | N/A | Control Panel-7 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116, 151118, 151122 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
176 | PS5-08-15CP- 0008-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 305 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-15CP- 0008 | N/A | Control Panel-8 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116, 151118, 151122, 151121 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
177 | PS5-08-52BT- 0131-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 110 |  | PS5-08-15CB- 1001 | N/A | TELECOM SII SP3 SEC Cabinet |  | EITS Building |  |  | PS5-08-52BT- 0131 | N/A | JUNCTION BOX PTZ CAMERA-5 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151111 | 17.2 | A=1 B=2 C=0 | 08 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0276
178 | PS5-08-52BT- 0132-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 310 |  | PS5-08-15CB- 1001 | N/A | TELECOM SII SP3 SEC Cabinet |  | EITS Building |  |  | PS5-08-52BT- 0132 | N/A | JUNCTION BOX PTZ CAMERA-6 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151108, 151110 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
179 | PS5-08-52BT- 0133-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 140 |  | PS5-08-15CB- 1001 | N/A | TELECOM SII SP3 SEC Cabinet |  | EITS Building |  |  | PS5-08-52BT- 0133 | N/A | JUNCTION BOX PTZ CAMERA-7 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151115 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
180 | PS5-08-52BT- 0134-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 60 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-52BT- 0134 | N/A | JUNCTION BOX PTZ CAMERA-8 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=1 B=2 C=0 | 06 | EPS | 2026-04-30 00:00:00 | CPP-RFI-68-331-05-0238
181 | PS5-08-52BT- 0135-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 100 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-52BT- 0135 | N/A | JUNCTION BOX PTZ CAMERA-9 |  | Power generator building area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=1 B=1 C=0 | 06 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-331-05-0226
182 | PS5-08-52BT- 0136-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 85 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-52BT- 0136 | N/A | JUNCTION BOX PTZ CAMERA-10 |  | Power generator building area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=1 B=2 C=0 | 06 | EPS | 30-April-20206 | CPP-RFI-68-331-05-0239
183 | PS5-08-52BT- 0137-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 75 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-52BT- 0137 | N/A | JUNCTION BOX PTZ CAMERA-11 |  | Power generator building area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=1 B=2 C=0 | 06 | EPS |  | CPP-RFI-68-33/1-07-0321
184 | PS5-08-52BT- 0138-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 245 |  | PS5-08-15CB- 1001 | N/A | TELECOM SII SP3 SEC Cabinet |  | EITS Building |  |  | PS5-08-52BT- 0138 | N/A | JUNCTION BOX PTZ CAMERA-12 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151120, 151122 | 17.2 | A=1 B=2 C=0 | 06 | EPS | 2026-05-10 00:00:00 | CPP-RFI-68-331-05-0260
185 | PS5-08-52BT- 0139-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 420 |  | PS5-08-15CB- 1001 | N/A | TELECOM SII SP3 SEC Cabinet |  | EITS Building |  |  | PS5-08-52BT- 0139 | N/A | JUNCTION BOX PTZ CAMERA-13 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151120, 151122, 151121 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-06-02 00:00:00 | CPP-RFI-68-33/1-07-0308
186 | PS5-08-52BT- 0140-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 50 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-52BT- 0140 | N/A | JUNCTION BOX PTZ CAMERA-14 |  | Power generator building area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=1 B=1 C=0 | 06 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-331-05-0226
187 | PS5-08-52BT- 0931-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 65 |  | PS5-08-11CB- 1201 | N/A | TELECOM SIE Cabinet |  | Office Building |  |  | PS5-08-52BT- 0931 | N/A | JUNCTION BOX PTZ CAMERA-2 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151106 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
188 | PS5-08-52CM- 0031-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-15CP- 0002 | N/A | Control Panel-2 |  | Field | Ind - IP 55 | M20 | PS5-08-52CM- 0031 | N/A | CCTV CAMERA |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151119 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
189 | PS5-08-52CM- 0032-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-15CP- 0006 | N/A | Control Panel-6 |  | Field | Ind - IP 55 | M20 | PS5-08-52CM- 0032 | N/A | CCTV CAMERA |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151120 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
190 | PS5-08-52CM- 0033-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-15CP- 0008 | N/A | Control Panel-8 |  | Field | Ind - IP 55 | M20 | PS5-08-52CM- 0033 | N/A | CCTV CAMERA |  | field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151121 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
191 | PS5-08-52CM- 0131-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0131 | N/A | JUNCTION BOX PTZ CAMERA-5 |  | Field | Ind - IP 55 | M20 | PS5-08-52CM- 0131 | N/A | CCTV CAMERA |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151111 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
192 | PS5-08-52CM- 0132-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0132 | N/A | JUNCTION BOX PTZ CAMERA-6 |  | Field | Ind - IP 55 | M20 | PS5-08-52CM- 0132 | N/A | CCTV CAMERA |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151110 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
193 | PS5-08-52CM- 0133-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0133 | N/A | JUNCTION BOX PTZ CAMERA-7 |  | Field | Ind - IP 55 | M20 | PS5-08-52CM- 0133 | N/A | CCTV CAMERA |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151115 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
194 | PS5-08-52CM- 0134-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0134 | N/A | JUNCTION BOX PTZ CAMERA-8 |  | Field | Ind - IP 55 | M20 | PS5-08-52CM- 0134 | N/A | CCTV CAMERA |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
195 | PS5-08-52CM- 0135-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0135 | N/A | JUNCTION BOX PTZ CAMERA-9 |  | Power generator building area | Ind - IP 55 | M20 | PS5-08-52CM- 0135 | N/A | CCTV CAMERA |  | Power generator building area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
196 | PS5-08-52CM- 0136-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0136 | N/A | JUNCTION BOX PTZ CAMERA-10 |  | Power generator building area | Ind - IP 55 | M20 | PS5-08-52CM- 0136 | N/A | CCTV CAMERA |  | Power generator building area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
197 | PS5-08-52CM- 0137-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0137 | N/A | JUNCTION BOX PTZ CAMERA-11 |  | Power generator building area | Ind - IP 55 | M20 | PS5-08-52CM- 0137 | N/A | CCTV CAMERA |  | Power generator building area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
198 | PS5-08-52CM- 0138-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0138 | N/A | JUNCTION BOX PTZ CAMERA-12 |  | Field | Ind - IP 55 | M20 | PS5-08-52CM- 0138 | N/A | CCTV CAMERA |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151122 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
199 | PS5-08-52CM- 0139-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0139 | N/A | JUNCTION BOX PTZ CAMERA-13 |  | Field | Ind - IP 55 | M20 | PS5-08-52CM- 0139 | N/A | CCTV CAMERA |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151121 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
200 | PS5-08-52CM- 0140-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0140 | N/A | JUNCTION BOX PTZ CAMERA-14 |  | Power generator building area | Ind - IP 55 | M20 | PS5-08-52CM- 0140 | N/A | CCTV CAMERA |  | Power generator building area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
201 | PS5-08-52CM- 0931-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0931 | N/A | JUNCTION BOX PTZ CAMERA-2 |  | Field | Ind - IP 55 | M20 | PS5-08-52CM- 0931 | N/A | CCTV CAMERA |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151106 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
202 | PS5-08-52TK- 0031-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-15CP- 0002 | N/A | Control Panel-2 |  | Field | Ind - IP 55 | M20 | PS5-08-52TK- 0031 | N/A | CCTV CAMERA Water Tank |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151119 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
203 | PS5-08-52TK- 0032-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-15CP- 0006 | N/A | Control Panel-6 |  | Field | Ind - IP 55 | M20 | PS5-08-52TK- 0032 | N/A | CCTV CAMERA Water Tank |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151120 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
204 | PS5-08-52TK- 0033-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-15CP- 0008 | N/A | Control Panel-8 |  | Field | Ind - IP 55 | M20 | PS5-08-52TK- 0033 | N/A | CCTV CAMERA Water Tank |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151121 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
205 | PS5-08-52TK- 0131-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0131 | N/A | JUNCTION BOX PTZ CAMERA-5 |  | Field | Ind - IP 55 | M20 | PS5-08-52TK- 0131 | N/A | CCTV CAMERA Water Tank |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151111 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
206 | PS5-08-52TK- 0132-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0132 | N/A | JUNCTION BOX PTZ CAMERA-6 |  | Field | Ind - IP 55 | M20 | PS5-08-52TK- 0132 | N/A | CCTV CAMERA Water Tank |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151110 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
207 | PS5-08-52TK- 0133-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0133 | N/A | JUNCTION BOX PTZ CAMERA-7 |  | Field | Ind - IP 55 | M20 | PS5-08-52TK- 0133 | N/A | CCTV CAMERA Water Tank |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151115 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
208 | PS5-08-52TK- 0134-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0134 | N/A | JUNCTION BOX PTZ CAMERA-8 |  | Field | Ind - IP 55 | M20 | PS5-08-52TK- 0134 | N/A | CCTV CAMERA Water Tank |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
209 | PS5-08-52TK- 0135-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0135 | N/A | JUNCTION BOX PTZ CAMERA-9 |  | Power generator building area | Ind - IP 55 | M20 | PS5-08-52TK- 0135 | N/A | CCTV CAMERA Water Tank |  | Power generator building area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
210 | PS5-08-52TK- 0136-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0136 | N/A | JUNCTION BOX PTZ CAMERA-10 |  | Power generator building area | Ind - IP 55 | M20 | PS5-08-52TK- 0136 | N/A | CCTV CAMERA Water Tank |  | Power generator building area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
211 | PS5-08-52TK- 0137-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0137 | N/A | JUNCTION BOX PTZ CAMERA-11 |  | Power generator building area | Ind - IP 55 | M20 | PS5-08-52TK- 0137 | N/A | CCTV CAMERA Water Tank |  | Power generator building area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
212 | PS5-08-52TK- 0138-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0138 | N/A | JUNCTION BOX PTZ CAMERA-12 |  | Field | Ind - IP 55 | M20 | PS5-08-52TK- 0138 | N/A | CCTV CAMERA Water Tank |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151122 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
213 | PS5-08-52TK- 0139-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0139 | N/A | JUNCTION BOX PTZ CAMERA-13 |  | Field | Ind - IP 55 | M20 | PS5-08-52TK- 0139 | N/A | CCTV CAMERA Water Tank |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151121 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
214 | PS5-08-52TK- 0140-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0140 | N/A | JUNCTION BOX PTZ CAMERA-14 |  | Power generator building area | Ind - IP 55 | M20 | PS5-08-52TK- 0140 | N/A | CCTV CAMERA Water Tank |  | Power generator building area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
215 | PS5-08-52TK- 0931-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 8 |  | PS5-08-52BT- 0931 | N/A | JUNCTION BOX PTZ CAMERA-2 |  | Field | Ind - IP 55 | M20 | PS5-08-52TK- 0931 | N/A | CCTV CAMERA Water Tank |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151106 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EITS
216 | PS5-08-61BT- 0002-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 65 |  | PS5-08-14CB- 1201 | N/A | TELECOM SIE Cabinet |  | Office Building |  |  | PS5-08-61BT- 0002 | N/A | JB Meteocean - 2 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151106 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
217 | PS5-08-85CP- 0024-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 290 |  | PS5-08-15CB- 1001 | N/A | TELECOM SII SP3 SEC Cabinet |  | EITS Building |  |  | PS5-08-85CP- 0024 | N/A | CONTROL PANEL POB-1 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151120, 151122 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
218 | PS5-08-85CP- 0025-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 290 |  | PS5-08-15CB- 1001 | N/A | TELECOM SII SP3 SEC Cabinet |  | EITS Building |  |  | PS5-08-85CP- 0025 | N/A | CONTROL PANEL POB-2 |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151120, 151122 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
219 | PS5-08-85CP- 1201-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 0 |  | PS5-08-11CB- 1201 | N/A | TELECOM SIE Cabinet |  | Office Building |  |  | PS5-08-85CP- 1201 | N/A | CONTROL PANEL POB-1 |  | Office Building | Ind - IP 55 | M20 |  | - | 17.2 | Telecom Field Equipment (Refer Note 17, 19 & 20) | 07 | Contract or
220 | PS5-08-85CP- 1202-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 0 |  | PS5-08-11CB- 1201 | N/A | TELECOM SIE Cabinet |  | Office Building |  |  | PS5-08-85CP- 1202 | N/A | CONTROL PANEL POB-2 |  | Office Building | Ind - IP 55 | M20 |  | - | 17.2 | Telecom Field Equipment (Refer Note 17, 19 & 20) | 07 | Contract or
221 | PS5-08-85CP- 1501-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 10 |  | PS5-08-11CB- 1501 | N/A | TELECOM SIE Cabinet |  | Guard House Building |  |  | PS5-08-85CP- 1501 | N/A | ACS CONTROLLER ENCLOSURE |  | Guard House | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151106 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
222 | PS5-08-85CP- 1601-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 0 |  | PS5-08-11CB- 1601 | N/A | TELECOM SIE Cabinet |  | Workshop & warehouse |  |  | PS5-08-85CP- 1601 | N/A | ACS CONTROLLER ENCLOSURE |  | Workshop & Warehouse | Ind - IP 55 | M20 |  | - | 17.2 | Telecom Field Equipment (Refer Note 17, 19 & 20) | 07 | Contract or
223 | PS5-08-85CP- 1901-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 20 |  | PS5-08-11CB- 1901 | N/A | TELECOM SIE Cabinet |  | Generator Electrical Building |  |  | PS5-08-85CP- 1901 | N/A | ACS CONTROLLER ENCLOSURE |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 06 | EPS
224 | PS5-08-85LA- 1601-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 160 |  | PS5-08-11CB- 1601 | N/A | TELECOM SIE Cabinet |  | Workshop & warehouse |  |  | PS5-82-MTL- 0001 | N/A | Turnstile |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151105, 151106 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 07 | EPS
225 | PS5-08-85LA- 1602-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 115 |  | PS5-08-11CB- 1601 | N/A | TELECOM SIE Cabinet |  | Workshop & warehouse |  |  | PS5-82-MBA- 0001 | N/A | Vehicle Barrier |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151105 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 07 | EPS
226 | PS5-08-85LA- 1603-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 225 |  | PS5-08-11CB- 1601 | N/A | TELECOM SIE Cabinet |  | Workshop & warehouse |  |  | PS5-82-MBA- 0002 | N/A | Vehicle Barrier |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151105, 151106 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 07 | EPS
227 | PS5-08-85LA- 1604-CS01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 160 |  | PS5-08-11CB- 1601 | N/A | TELECOM SIE Cabinet |  | Workshop & warehouse |  |  | PS5-82-MBA- 0003 | N/A | Vehicle Barrier |  | Field | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151105, 151106 | 17.2 | Telecom Field Equipment (Refer Note 19 & 20) | 07 | EPS
228 | PS5-09-LB-0008 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 15 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-09-LB-0008 | N/A | HVAC UCP |  | Generator Electrical Buidling | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 07 | EPS
229 | PS5-09-LB-0008 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 15 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-09-LB-0008 | N/A | HVAC UCP |  | Generator Electrical Buidling | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 07 | EPS
230 | PS5-09-LB-7001 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 30 |  | PS5-05-IG-0007 | N/A | Indoor Emergency L&SP DB - Guard House |  | Guard House | Ind - IP 55 | M20 | PS5-09-LB-7001 | N/A | HVAC UCP - Guard House |  | Guard House | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151185 | 18.5 | HVAC UCP Power Cable | 07 | EPS
231 | PS5-25-DM- 3100A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWB/LSZH | - |  | 6Tr | 2.5 | 280 |  | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M32 | PS5-25-DM- 3100A | N/A | Crude Oil Export Pump A |  | Export Pump area | Ex'd - IP 66 | M32 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 25.1 | A=2 B=2 C=0 | 05 | EPS | 2026-04-24 00:00:00 | CPP-RFI-68-331-05-0225
232 | PS5-25-DM- 3100A-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 120 | 280 |  | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 | PS5-25-DM- 3100A | N/A | Crude Oil Export Pump A |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 19.5 | A=0 B=2 C=0 | 05 | Contract or | 2026-05-10 00:00:00 | CPP-RFI-68-331-05-0260
233 | PS5-25-DM- 3100A-CG02 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 120 | 280 |  | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 | PS5-25-DM- 3100A | N/A | Crude Oil Export Pump A |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 19.5 | A=0 B=2 C=0 | 05 | Contract or | 2026-05-10 00:00:00 | CPP-RFI-68-331-05-0260
234 | PS5-25-DM- 3100A-CH01 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 280 |  | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100A | N/A | Crude Oil Export Pump A |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase A | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
235 | PS5-25-DM- 3100A-CH02 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 280 |  | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100A | N/A | Crude Oil Export Pump A |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase B | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
236 | PS5-25-DM- 3100A-CH03 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 280 |  | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100A | N/A | Crude Oil Export Pump A |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase C | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
237 | PS5-25-DM- 3100A-CH04 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 280 |  | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100A | N/A | Crude Oil Export Pump A |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase A | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
238 | PS5-25-DM- 3100A-CH05 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 280 |  | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100A | N/A | Crude Oil Export Pump A |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase B | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
239 | PS5-25-DM- 3100A-CH06 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 280 |  | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100A | N/A | Crude Oil Export Pump A |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase C | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
240 | PS5-25-DM- 3100A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 280 |  | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 | PS5-25-DM- 3100A | N/A | Crude Oil Export Pump A |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 19.5 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
241 | PS5-25-DM- 3100A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 265 |  | PS5-61-IG-0014 | N/A | Outdoor Power DB - Field(North) |  | Near EITS | Ind - IP 55 | M20 | PS5-25-DM- 3100A | N/A | Crude Oil Export Pump A |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111, 151115, 151117, 151114 | 18.5 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
242 | PS5-25-DM- 3100B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWB/LSZH | - |  | 6Tr | 2.5 | 285 |  | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M32 | PS5-25-DM- 3100B | N/A | Crude Oil Export Pump B |  | Export Pump area | Ex'd - IP 66 | M32 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 25.1 | A=2 B=2 C=0 | 05 | EPS | 2026-04-24 00:00:00 | CPP-RFI-68-331-05-0225
243 | PS5-25-DM- 3100B-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 120 | 285 |  | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 | PS5-25-DM- 3100B | N/A | Crude Oil Export Pump B |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 19.5 | A=0 B=3 C=0 | 05 | Contract or | 2026-05-05 00:00:00 | CPP-RFI-68-331-05-0244
244 | PS5-25-DM- 3100B-CG02 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 120 | 285 |  | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 | PS5-25-DM- 3100B | N/A | Crude Oil Export Pump B |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 19.5 | A=0 B=3 C=0 | 05 | Contract or | 2026-05-05 00:00:00 | CPP-RFI-68-331-05-0244
245 | PS5-25-DM- 3100B-CH01 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 285 |  | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100B | N/A | Crude Oil Export Pump B |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase A | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
246 | PS5-25-DM- 3100B-CH02 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 285 |  | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100B | N/A | Crude Oil Export Pump B |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase B | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
247 | PS5-25-DM- 3100B-CH03 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 285 |  | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100B | N/A | Crude Oil Export Pump B |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase C | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
248 | PS5-25-DM- 3100B-CH04 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 285 |  | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100B | N/A | Crude Oil Export Pump B |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase A | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
249 | PS5-25-DM- 3100B-CH05 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 285 |  | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100B | N/A | Crude Oil Export Pump B |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase B | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
250 | PS5-25-DM- 3100B-CH06 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 285 |  | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100B | N/A | Crude Oil Export Pump B |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase C | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
251 | PS5-25-DM- 3100B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 285 |  | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 | PS5-25-DM- 3100B | N/A | Crude Oil Export Pump B |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 19.5 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
252 | PS5-25-DM- 3100B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 255 |  | PS5-61-IG-0014 | N/A | Outdoor Power DB - Field(North) |  | Near EITS | Ind - IP 55 | M20 | PS5-25-DM- 3100B | N/A | Crude Oil Export Pump B |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111, 151115, 151117, 151114 | 18.5 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
253 | PS5-25-DM- 3100C-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWB/LSZH | - |  | 6Tr | 2.5 | 290 |  | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M32 | PS5-25-DM- 3100C | N/A | Crude Oil Export Pump C |  | Export Pump area | Ex'd - IP 66 | M32 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 25.1 | A=2 B=2 C=0 | 05 | EPS | 2026-04-24 00:00:00 | CPP-RFI-68-331-05-0225
254 | PS5-25-DM- 3100C-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 120 | 290 |  | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 | PS5-25-DM- 3100C | N/A | Crude Oil Export Pump C |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 19.5 | A=0 B=3 C=0 | 05 | Contract or | 2026-05-05 00:00:00 | CPP-RFI-68-331-05-0244
255 | PS5-25-DM- 3100C-CG02 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 120 | 290 |  | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 | PS5-25-DM- 3100C | N/A | Crude Oil Export Pump C |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 19.5 | A=0 B=3 C=0 | 05 | Contract or | 2026-05-05 00:00:00 | CPP-RFI-68-331-05-0244
256 | PS5-25-DM- 3100C-CH01 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 290 |  | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100C | N/A | Crude Oil Export Pump C |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase A | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
257 | PS5-25-DM- 3100C-CH02 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 290 |  | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100C | N/A | Crude Oil Export Pump C |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase B | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
258 | PS5-25-DM- 3100C-CH03 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 290 |  | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100C | N/A | Crude Oil Export Pump C |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase C | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
259 | PS5-25-DM- 3100C-CH04 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 290 |  | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100C | N/A | Crude Oil Export Pump C |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase A | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
260 | PS5-25-DM- 3100C-CH05 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 290 |  | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100C | N/A | Crude Oil Export Pump C |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase B | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
261 | PS5-25-DM- 3100C-CH06 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 3000V AC |  | 1C | 300 | 290 |  | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 | PS5-25-DM- 3100C | N/A | Crude Oil Export Pump C |  | Export Pump area | Ex'd - IP 66 | M50 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 41.9 | Phase C | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0216
262 | PS5-25-DM- 3100C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 290 |  | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 | PS5-25-DM- 3100C | N/A | Crude Oil Export Pump C |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 19.5 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
263 | PS5-25-DM- 3100C-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 245 |  | PS5-61-IG-0014 | N/A | Outdoor Power DB - Field(North) |  | Near EITS | Ind - IP 55 | M20 | PS5-25-DM- 3100C | N/A | Crude Oil Export Pump C |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111, 151115, 151117, 151114 | 18.5 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
264 | PS5-25-DM- 3200A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 385 |  | PS5-61-IK-0001 | A0325 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-25-DM- 3200A | N/A | Crude Oil Export Pump A -Lube OilPump 1 Motor |  | Export Pump area | Ex'd - IP 66 | M25 / M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
265 | PS5-25-DM- 3200B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 385 |  | PS5-61-IK-0001 | B0521 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-25-DM- 3200B | N/A | Crude Oil Export Pump A -Lube OilPump 2 Motor |  | Export Pump area | Ex'd - IP 66 | M25 / M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
266 | PS5-25-DM- 3300A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 375 |  | PS5-61-IK-0001 | A0323 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-25-DM- 3300A | N/A | Crude Oil Export Pump B -Lube OilPump 1 Motor |  | Export Pump area | Ex'd - IP 66 | M25 / M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
267 | PS5-25-DM- 3300B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 375 |  | PS5-61-IK-0001 | B0519 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-25-DM- 3300B | N/A | Crude Oil Export Pump B -Lube OilPump 2 Motor |  | Export Pump area | Ex'd - IP 66 | M25 / M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
268 | PS5-25-DM- 3400A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 365 |  | PS5-61-IK-0001 | B0517 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-25-DM- 3400A | N/A | Crude Oil Export Pump C -Lube OilPump 1 Motor |  | Export Pump area | Ex'd - IP 66 | M25 / M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
269 | PS5-25-DM- 3400B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 365 |  | PS5-61-IK-0001 | B0515 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-25-DM- 3400B | N/A | Crude Oil Export Pump C -Lube OilPump 2 Motor |  | Export Pump area | Ex'd - IP 66 | M25 / M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0279
270 | PS5-25-DM- 6400A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 385 |  | PS5-61-IK-0001 | A0227 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-DM- 6400A | N/A | Crude Oil Export Pump A -Lube Oil Heat Exchanger Fan Motor 1 |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0279
271 | PS5-25-DM- 6400B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 385 |  | PS5-61-IK-0001 | B0627 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-DM- 6400B | N/A | Crude Oil Export Pump A -Lube Oil Heat Exchanger Fan Motor 2 |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0279
272 | PS5-25-DM- 6500A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 375 |  | PS5-61-IK-0001 | A0225 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-DM- 6500A | N/A | Crude Oil Export Pump B -Lube Oil Heat Exchanger Fan Motor 1 |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0279
273 | PS5-25-DM- 6500B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 375 |  | PS5-61-IK-0001 | B0629 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-DM- 6500B | N/A | Crude Oil Export Pump B -Lube Oil Heat Exchanger Fan Motor 2 |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0279
274 | PS5-25-DM- 6600A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 365 |  | PS5-61-IK-0001 | B0625 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-DM- 6600A | N/A | Crude Oil Export Pump C -Lube Oil Heat Exchanger Fan Motor 1 |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0279
275 | PS5-25-DM- 6600B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 365 |  | PS5-61-IK-0001 | B0631 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-DM- 6600B | N/A | Crude Oil Export Pump C -Lube Oil Heat Exchanger Fan Motor 2 |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0279
276 | PS5-25-ESDV- 0021-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 110 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-ESDV- 0021 | N/A | Emergency Shutdown Valve |  | EXPORT PUMP AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=2 B=1 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-331-05-0226
277 | PS5-25-ESDV- 0023-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 135 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-ESDV- 0023 | N/A | Emergency Shutdown Valve |  | EXPORT PUMP AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=2 B=1 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-331-05-0226
278 | PS5-25-FCV- 0003A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 85 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-FCV- 0003A | N/A | Flow Control Valve |  | Export Pump Area | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-331-05-0226
279 | PS5-25-FCV- 0003B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 90 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-FCV- 0003B | N/A | Flow Control Valve |  | Export Pump Area | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=2 B=1 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-331-05-0226
280 | PS5-25-FCV- 0003C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 55 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-FCV- 0003C | N/A | Flow Control Valve |  | Export Pump Area | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=2 B=1 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-331-05-0226
281 | PS5-25-FCV- 0004-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 105 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-FCV- 0004 | N/A | Flow Control Valve |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | LV Power (Refer Note 13) | 05 | EPS
282 | PS5-25-FIT- 0001-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 365 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-25-FIT-0001 | N/A | Ultrasonic Flow Ind Transmitter |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151117, 151114 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0279
283 | PS5-25-FIT- 0003A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 345 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-25-FIT- 0003A | N/A | Ultrasonic Flow Ind Transmitter |  | Field_EXPORT PUMP AREA | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151117, 151114 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0279
284 | PS5-25-FIT- 0003B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 335 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-25-FIT- 0003B | N/A | Ultrasonic Flow Ind Transmitter |  | Field_EXPORT PUMP AREA | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151117, 151114 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0279
285 | PS5-25-FIT- 0003C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 325 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-25-FIT- 0003C | N/A | Ultrasonic Flow Ind Transmitter |  | Field_EXPORT PUMP AREA | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151117, 151114 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0279
286 | PS5-25-FIT- 0004-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 320 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-25-FIT-0004 | N/A | Ultrasonic Flow Ind Transmitter |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151117, 151114 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-06-02 00:00:00 | CPP-RFI-68-33/1-07-0308
287 | PS5-25-HE- 2100-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 385 |  | PS5-61-IK-0001 | A0417 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-HE-2100 | N/A | Crude Oil Export Pump A -Lube Oil System Oil Reservoir Heater |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0279
288 | PS5-25-HE- 2100-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 385 |  | PS5-61-IK-0001 | A0417 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-25-HE-2100 | N/A | Crude Oil Export Pump A -Lube Oil System Oil Reservoir Heater |  | Export Pump area | Ex'd - IP 66 | M25 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0279
289 | PS5-25-HE- 2200-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 375 |  | PS5-61-IK-0001 | A0414 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-HE-2200 | N/A | Crude Oil Export Pump B -Lube Oil System Oil Reservoir Heater |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-20 00:00:00 | CPP-RFI-68-331-07-0279
290 | PS5-25-HE- 2200-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 375 |  | PS5-61-IK-0001 | A0414 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-25-HE-2200 | N/A | Crude Oil Export Pump B -Lube Oil System Oil Reservoir Heater |  | Export Pump area | Ex'd - IP 66 | M25 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-15 00:00:00 | CPP-RFI-68-331-07-0287
291 | PS5-25-HE- 2300-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 365 |  | PS5-61-IK-0001 | A0216 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-HE-2300 | N/A | Crude Oil Exp Pump C - Lube Oil System Oil Reservoir Heater |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-15 00:00:00 | CPP-RFI-68-331-07-0287
292 | PS5-25-HE- 2300-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 365 |  | PS5-61-IK-0001 | A0216 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-25-HE-2300 | N/A | Crude Oil Exp Pump C - Lube Oil System Oil Reservoir Heater |  | Export Pump area | Ex'd - IP 66 | M25 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-15 00:00:00 | CPP-RFI-68-331-07-0287
293 | PS5-25-IE-0001- CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 10 | 0 |  | PS5-06-IG- 0001A | N/A | AC UPS Distribution Board (A) Dual supply loads - 230VAC, 50Hz, 320A, 25KA/1s |  | EITS Building | Ind - IP 55 | M25 | PS5-25-IE-0001 | N/A | VTMS Cabinet for Export Pump cabinet |  | EITS Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112 | 22.6 | UPS A_VTMS cabinet ( Refer Note 06) | 06 | EITS
294 | PS5-25-IE-0001- CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 10 | 0 |  | PS5-06-IG- 0001B | N/A | AC UPS Distribution Board (B) Dual supply loads - 230VAC, 50Hz, 320A, 25KA/1s |  | EITS Building | Ind - IP 55 | M25 | PS5-25-IE-0001 | N/A | VTMS Cabinet for Export Pump cabinet |  | EITS Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112 | 22.6 | UPS B_VTMS cabinet ( Refer Note 06) | 06 | EITS
295 | PS5-25-IE-0001- CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 0 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-25-IE-0001 | N/A | VTMS Cabinet for Export Pump cabinet |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 18.5 | Auxillary supply_VTMS cabinet ( Refer Note 06) | 06 | EITS
296 | PS5-25-IES- 3100A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 280 |  | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 | PS5-25-IES- 3100A | N/A | Crude Oil Export Pump A -LCS |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
297 | PS5-25-IES- 3100B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 285 |  | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 | PS5-25-IES- 3100B | N/A | Crude Oil Export Pump B -LCS |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
298 | PS5-25-IES- 3100C-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 290 |  | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 | PS5-25-IES- 3100C | N/A | Crude Oil Export Pump C -LCS |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
299 | PS5-25-IES- 3200A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 385 |  | PS5-61-IK-0001 | A0325 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-IES- 3200A | N/A | Crude Oil Export Pump A -Lube OilPump 1 Motor- LCS |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=4 C=0 | 05 | EPS | 2026-05-15 00:00:00 | CPP-RFI-68-331-07-0287
300 | PS5-25-IES- 3200B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 385 |  | PS5-61-IK-0001 | B0521 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-IES- 3200B | N/A | Crude Oil Export Pump A -Lube OilPump 2 Motor- LCS |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=4 C=0 | 05 | EPS | 2026-05-15 00:00:00 | CPP-RFI-68-331-07-0287
301 | PS5-25-IES- 3300A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 375 |  | PS5-61-IK-0001 | A0323 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-IES- 3300A | N/A | Crude Oil Export Pump B -Lube OilPump 1 Motor- LCS |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=4 C=0 | 05 | EPS | 2026-05-15 00:00:00 | CPP-RFI-68-331-07-0287
302 | PS5-25-IES- 3300B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 375 |  | PS5-61-IK-0001 | B0519 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-IES- 3300B | N/A | Crude Oil Export Pump B -Lube OilPump 2 Motor- LCS |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=4 C=0 | 05 | EPS | 2026-05-15 00:00:00 | CPP-RFI-68-331-07-0287
303 | PS5-25-IES- 3400A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 365 |  | PS5-61-IK-0001 | B0517 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-IES- 3400A | N/A | Crude Oil Export Pump C -Lube OilPump 1 Motor- LCS |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=4 C=0 | 05 | EPS | 2026-05-15 00:00:00 | CPP-RFI-68-331-07-0287
304 | PS5-25-IES- 3400B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 365 |  | PS5-61-IK-0001 | B0515 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-IES- 3400B | N/A | Crude Oil Export Pump C -Lube OilPump 2 Motor- LCS |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=4 C=0 | 05 | EPS | 2026-05-15 00:00:00 | CPP-RFI-68-331-07-0287
305 | PS5-25-IES- 6400A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 385 |  | PS5-61-IK-0001 | A0227 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-IES- 6400A | N/A | Crude Oil Export Pump A -Lube Oil Heat Exchanger Fan Motor 1-LCS |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=4 C=0 | 05 | EPS | 2026-05-15 00:00:00 | CPP-RFI-68-331-07-0287
306 | PS5-25-IES- 6400B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 385 |  | PS5-61-IK-0001 | B0627 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-IES- 6400B | N/A | Crude Oil Export Pump A -Lube Oil Heat Exchanger Fan Motor 2-LCS |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=4 C=0 | 05 | EPS | 2026-05-15 00:00:00 | CPP-RFI-68-331-07-0287
307 | PS5-25-IES- 6500A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 375 |  | PS5-61-IK-0001 | A0225 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-IES- 6500A | N/A | Crude Oil Export Pump B -Lube Oil Heat Exchanger Fan Motor 1-LCS |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=4 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-331-07-0291
308 | PS5-25-IES- 6500B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 375 |  | PS5-61-IK-0001 | B0629 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-IES- 6500B | N/A | Crude Oil Export Pump B -Lube Oil Heat Exchanger Fan Motor 2-LCS |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=4 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-331-07-0291
309 | PS5-25-IES- 6600A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 365 |  | PS5-61-IK-0001 | B0625 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-IES- 6600A | N/A | Crude Oil Export Pump C -Lube Oil Heat Exchanger Fan Motor 1-LCS |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=4 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-331-07-0291
310 | PS5-25-IES- 6600B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 365 |  | PS5-61-IK-0001 | B0631 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-25-IES- 6600B | N/A | Crude Oil Export Pump C -Lube Oil Heat Exchanger Fan Motor 2-LCS |  | Export Pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=4 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-331-07-0291
311 | PS5-25-MOV- 0001-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 145 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-MOV- 0001 | N/A | Motor Operated Valve |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
312 | PS5-25-MOV- 0002-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 140 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-MOV- 0002 | N/A | Motor Operated Valve |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
313 | PS5-25-MOV- 0003-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 140 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-MOV- 0003 | N/A | Motor Operated Valve |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
314 | PS5-25-MOV- 0008-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-MOV- 0008 | N/A | Motor Operated Valve |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-13 00:00:00 | CPP-RFI-68-331-05-0266
315 | PS5-25-MOV- 0011-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-MOV- 0011 | N/A | Motor Operated Valve |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
316 | PS5-25-MOV- 0012-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-MOV- 0012 | N/A | Motor Operated Valve |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
317 | PS5-25-MOV- 0025-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-MOV- 0025 | N/A | Motor Operated Valve |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-13 00:00:00 | CPP-RFI-68-331-05-0266
318 | PS5-25-MOV- 0026-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 125 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-MOV- 0026 | N/A | Motor Operated Valve |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-13 00:00:00 | CPP-RFI-68-331-05-0266
319 | PS5-25-MOV- 0027-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 135 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-MOV- 0027 | N/A | Motor Operated Valve |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
320 | PS5-25-MOV- 0028-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 125 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-MOV- 0028 | N/A | Motor Operated Valve |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
321 | PS5-25-SDV- 0022-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 105 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-SDV- 0022 | N/A | Shutdown Valve |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
322 | PS5-25-SDV- 0035A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 100 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-SDV- 0035A | N/A | Shutdown Valve |  | EXPORT PUMP AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
323 | PS5-25-SDV- 0035B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 90 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-SDV- 0035B | N/A | Shutdown Valve |  | EXPORT PUMP AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
324 | PS5-25-SDV- 0035C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 70 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-SDV- 0035C | N/A | Shutdown Valve |  | EXPORT PUMP AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
325 | PS5-25-SDV- 0036A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 80 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-SDV- 0036A | N/A | Shutdown Valve |  | EXPORT PUMP AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
326 | PS5-25-SDV- 0036B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 75 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-SDV- 0036B | N/A | Shutdown Valve |  | EXPORT PUMP AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
327 | PS5-25-SDV- 0036C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 40 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-SDV- 0036C | N/A | Shutdown Valve |  | EXPORT PUMP AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
328 | PS5-25-SDV- 0046-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 90 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-SDV- 0046 | N/A | Shutdown Valve |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-13 00:00:00 | CPP-RFI-68-331-05-0266
329 | PS5-25-SDV- 0052-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 135 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-SDV- 0052 | N/A | Shutdown Valve |  | EXPORT PUMP AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
330 | PS5-25-SDV- 0054A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 75 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-SDV- 0054A | N/A | Shutdown Valve |  | EXPORT PUMP AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-331-05-0226
331 | PS5-25-SDV- 0054B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 50 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-SDV- 0054B | N/A | Shutdown Valve |  | EXPORT PUMP AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=2 B=1 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-331-05-0226
332 | PS5-25-SDV- 0054C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 50 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-SDV- 0054C | N/A | Shutdown Valve |  | EXPORT PUMP AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=2 B=1 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-331-05-0226
333 | PS5-25-UD- 3100A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 6 | 385 |  | PS5-61-IK-0001 | A0210 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-25-UD- 3100A | N/A | 5 pin 32A plug and socket for Oil Purifier Control Panel |  | Export pump area | Ex'd - IP 66 | M25 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 22.9 | A=0 B=2 C=0 | 05 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0292
334 | PS5-25-XV-0053 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 90 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-XV-0053 | N/A | On / Off Valve |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0210
335 | PS5-25-XV-0070 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 85 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-25-XV-0070 | N/A | On / Off Valve |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | LV Power (Refer Note 13) | 05 | EPS
336 | PS5-26-LA-0001 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 0 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-26-LA-0001 | N/A | UCP for PS5 Crude Fuel Oil Consumption Meter for Power Gen Package |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 18.5 | Normal auxillary supply for CFO metering package control panel ( Refer Note 06) | 05 | EITS
337 | PS5-26-LA-0001 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 0 |  | PS5-06-IG- 0001A | N/A | AC UPS Distribution Board (A) Dual supply loads - 230VAC, 50Hz, 320A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-26-LA-0001 | N/A | UCP for PS5 Crude Fuel Oil Consumption Meter for Power Gen Package |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | UPS Supply for CFO metering package control panel ( Refer Note 06) | 05 | EITS
338 | PS5-26-LA-0001 -CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 0 |  | PS5-06-IG- 0001B | N/A | AC UPS Distribution Board (B) Dual supply loads - 230VAC, 50Hz, 320A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-26-LA-0001 | N/A | UCP for PS5 Crude Fuel Oil Consumption Meter for Power Gen Package |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | UPS Supply for CFO metering package control panel( Refer Note 06) | 05 | EITS
339 | PS5-28-BE- 0002A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 370 |  | PS5-61-IK-0001 | A0508 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-BE- 0002A | N/A | Reinjection Pump A Electrical Junction box |  | Reinjection Pump | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
340 | PS5-28-BE- 0002A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 270 |  | PS5-61-IG-0007 | N/A | Outdoor Normal Lighting DB - Field - (North Side) |  | Near EDG package | Ind - IP 55 | M20 | PS5-28-BE- 0002A | N/A | Reinjection Pump A Electrical Junction box |  | Reinjection Pump | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 17.2 | A=2 B=2 C=0 | 06 | EPS | 2026-04-30 00:00:00 | CPP-RFI-68-331-05-0238
341 | PS5-28-BE- 0002B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 375 |  | PS5-61-IK-0001 | B0208 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-BE- 0002B | N/A | Reinjection Pump B Electrical Junction box |  | Reinjection Pump | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
342 | PS5-28-BE- 0002B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 275 |  | PS5-61-IG-0007 | N/A | Outdoor Normal Lighting DB - Field - (North Side) |  | Near EDG package | Ind - IP 55 | M20 | PS5-28-BE- 0002B | N/A | Reinjection Pump B Electrical Junction box |  | Reinjection Pump | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 17.2 | A=2 B=2 C=0 | 06 | EPS | 2026-04-30 00:00:00 | CPP-RFI-68-331-05-0238
343 | PS5-28-DM- 31100-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 20 |  | PS5-28-ISO- 2008 | N/A | Socket Outlet - Oil Skimmer package |  | Near Observation Basin | Ex'd - IP 66 | M20 | PS5-28-DM- 31100 | N/A | Oil Skimmer Motor |  | Oil Skimmer Package | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151110 | 19.5 | Oil Skimmer Motor Incomer From Socket | 05 | Vendor
344 | PS5-28-DM- 3300-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 10 | 450 |  | PS5-61-IK-0001 | B0611 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-28-DM- 3300 | N/A | Relief Drum Pump |  | Relief Drum Area | Ex'd - IP 66 | M25 / M32 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 24.1 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
345 | PS5-28-DM- 3400-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 410 |  | PS5-61-IK-0001 | A0333 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-28-DM- 3400 | N/A | Closed Drain Drum 01 Pump Motor |  | Closed Drain Drum Area | Ex'd - IP 66 | M32 / M40 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 27.5 | A=1 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0253
346 | PS5-28-DM- 3500-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 230 |  | PS5-61-IK-0001 | B0511 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-28-DM- 3500 | N/A | Oily Water Sump Pump |  | Oily Water Sump Pump Area | Ex'd - IP 66 | M25 / M32 |  | TZ-MID-68-WPR2- 151112,151108,151111 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
347 | PS5-28-DM- 3600A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 35 | 220 |  | PS5-61-IK-0001 | A0406 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-28-DM- 3600A | N/A | Open Drain Sump Pump A |  | Oily Water Sump Pump Area | Ex'd - IP 66 | M32 / M50 |  | TZ-MID-68-WPR2- 151112,151108,151111 | 29.3 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
348 | PS5-28-DM- 3600A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 220 |  | PS5-61-IK-0001 | A0406 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-DM- 3600A | N/A | Open Drain Sump Pump A |  | Oily Water Sump Pump Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151108,151111 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 30-May-2026 | CPP-RFI-68-33/1-07-0307
349 | PS5-28-DM- 3600B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 35 | 225 |  | PS5-61-IK-0001 | B0401 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-28-DM- 3600B | N/A | Open Drain Sump Pump B |  | Oily Water Sump Pump Area | Ex'd - IP 66 | M32 / M50 |  | TZ-MID-68-WPR2- 151112,151108,151111 | 29.3 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
350 | PS5-28-DM- 3600B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 225 |  | PS5-61-IK-0001 | B0401 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-DM- 3600B | N/A | Open Drain Sump Pump B |  | Oily Water Sump Pump Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151108,151111 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
351 | PS5-28-DM- 3700A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 16 | 310 |  | PS5-61-IK-0001 | B0205 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-28-DM- 3700A | N/A | Closed Drain Drum 02 Pump Motor A |  | Near CRO Gen Area | Ex'd - IP 66 | M32 / M40 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151118 | 26.4 | A=1 B=2 C=0 | 05 | EPS | 2026-05-08 00:00:00 | CPP-RFI-68-331-07-0255
352 | PS5-28-DM- 3700B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 16 | 310 |  | PS5-61-IK-0001 | B0415 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-28-DM- 3700B | N/A | Closed Drain Drum 02 Pump Motor B |  | Closed Drain Drum Area | Ex'd - IP 66 | M32 / M40 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151118 | 26.4 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
353 | PS5-28-DM- 3800A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 360 |  | PS5-61-IK-0001 | A0229 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-DM- 3800A | N/A | Seal Oil Drain Drum Pump A |  | Export pump area | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
354 | PS5-28-DM- 3800B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 350 |  | PS5-61-IK-0001 | B0609 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-DM- 3800B | N/A | Seal Oil Drain Drum Pump B |  | Export pump area | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
355 | PS5-28-DM- 3800C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 340 |  | PS5-61-IK-0001 | B0607 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-DM- 3800C | N/A | Seal Oil Drain Drum Pump C |  | Export pump area | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
356 | PS5-28-DM- 3900A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 50 | 380 |  | PS5-61-IK-0001 | A0508 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 | PS5-28-DM- 3900A | N/A | Reinjection Pump A |  | Closed Drain Drum Area | Ex'd - IP 66 | M40 / M50 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 32.9 | A=0 B=1 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-07-0249
357 | PS5-28-DM- 3900B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 50 | 385 |  | PS5-61-IK-0001 | B0208 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 | PS5-28-DM- 3900B | N/A | Reinjection Pump B |  | Closed Drain Drum Area | Ex'd - IP 66 | M40 / M50 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 32.9 | A=0 B=2 C=0 | 05 | EPS | 30-May-2026 | CPP-RFI-68-33/1-07-0307
358 | PS5-28-HE- 2100-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 410 |  | PS5-61-IK-0001 | A0420 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-HE-2100 | N/A | Closed Drain Drum 01 Heater |  | Closed Drain Drum Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
359 | PS5-28-HE- 2100-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 410 |  | PS5-61-IK-0001 | A0420 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-28-HE-2100 | N/A | Closed Drain Drum 01 Heater |  | Closed Drain Drum Area | Ex'd - IP 66 | M25 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
360 | PS5-28-HE- 2100-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 290 |  | PS5-61-IG-0007 | N/A | Outdoor Normal Lighting DB - Field - (North Side) |  | Near EDG package | Ind - IP 55 | M20 | PS5-28-HE-2100 | N/A | Closed Drain Drum 01 Heater |  | Closed Drain Drum Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111,151115,151117, 151114 | 17.2 | A=1 B=2 C=0 | 06 | EPS | 2026-04-30 00:00:00 | CPP-RFI-68-331-05-0238
361 | PS5-28-HE- 2200-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 310 |  | PS5-61-IK-0001 | B0420 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-HE-2200 | N/A | Closed Drain Drum 02 Heater |  | Closed Drain Drum Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151118 | 17.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-07-0249
362 | PS5-28-HE- 2200-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 310 |  | PS5-61-IK-0001 | B0420 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-HE-2200 | N/A | Closed Drain Drum 02 Heater |  | Closed Drain Drum Area | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151118 | 19.5 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
363 | PS5-28-HE- 2200-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 190 |  | PS5-61-IG-0007 | N/A | Outdoor Normal Lighting DB - Field - (North Side) |  | Near EDG package | Ind - IP 55 | M20 | PS5-28-HE-2200 | N/A | Closed Drain Drum 02 Heater |  | Closed Drain Drum Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111,151115,151118 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
364 | PS5-28-IES- 2008-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 5C | 2.5 | 260 |  | PS5-61-IK-0001 | B0523 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-IES-2008 | N/A | Oil Skimmer Package - LCS |  | Near Oil skimmer package | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112,151108,151111 | 19.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
365 | PS5-28-IES- 3300-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 450 |  | PS5-61-IK-0001 | B0611 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-IES-3300 | N/A | Relief Drum Pump-LCS |  | Relief Drum Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
366 | PS5-28-IES- 3400-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 410 |  | PS5-61-IK-0001 | A0333 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-IES-3400 | N/A | Closed Drain Drum 01 Pump Motor-LCS |  | Closed Drain Drum Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
367 | PS5-28-IES- 3500-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 230 |  | PS5-61-IK-0001 | B0511 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-IES-3500 | N/A | Oily Water Sump Pump- LCS |  | Oily Water Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151108,151111 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
368 | PS5-28-IES- 3600A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 220 |  | PS5-61-IK-0001 | A0406 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-IES- 3600A | N/A | Open Drain Sump Pump A-LCS |  | Oily Water Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151108,151111 | 17.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0261
369 | PS5-28-IES- 3600B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 225 |  | PS5-61-IK-0001 | B0401 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-IES- 3600B | N/A | Open Drain Sump Pump B-LCS |  | Oily Water Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151108,151111 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
370 | PS5-28-IES- 3700A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 310 |  | PS5-61-IK-0001 | B0205 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-IES- 3700A | N/A | Closed Drain Drum 02 Pump Motor A-LCS |  | Near CRO Gen Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151118 | 17.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0254
371 | PS5-28-IES- 3700B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 310 |  | PS5-61-IK-0001 | B0415 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-IES- 3700B | N/A | Closed Drain Drum 02 Pump Motor B-LCS |  | Closed Drain Drum Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151118 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 30-May-2026 | CPP-RFI-68-33/1-07-0307
372 | PS5-28-IES- 3800A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 360 |  | PS5-61-IK-0001 | A0229 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-IES- 3800A | N/A | Seal Oil Drain Drum Pump A -LCS |  | Export pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
373 | PS5-28-IES- 3800B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 350 |  | PS5-61-IK-0001 | B0609 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-IES- 3800B | N/A | Seal Oil Drain Drum Pump B-LCS |  | Export pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
374 | PS5-28-IES- 3800C-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 340 |  | PS5-61-IK-0001 | B0607 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-IES- 3800C | N/A | Seal Oil Drain Drum Pump C-LCS |  | Export pump area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
375 | PS5-28-IES- 3900A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 380 |  | PS5-61-IK-0001 | A0508 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-IES- 3900A | N/A | Reinjection Pump A-LCS |  | Closed Drain Drum Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 17.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
376 | PS5-28-IES- 3900B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 385 |  | PS5-61-IK-0001 | B0208 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-28-IES- 3900B | N/A | Reinjection Pump B-LCS |  | Closed Drain Drum Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
377 | PS5-28-ISO- 2008-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 10 | 260 |  | PS5-61-IK-0001 | B0523 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-28-ISO- 2008 | N/A | Socket Outlet - Oil Skimmer package |  | Near Observation Basin | Ex'd - IP 66 | M25 |  | TZ-MID-68-WPR2- 151112,151108,151111 | 24.1 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
378 | PS5-28-LB-8200 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 130 |  | PS5-61-IG-0007 | N/A | Outdoor Normal Lighting DB - Field - (North Side) |  | Near EDG package | Ind - IP 55 | M20 | PS5-28-LB-8200 | N/A | Open Drain Interceptor Panel |  | OPERATION AND M AINTENANCE AREA | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151111 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
379 | PS5-28-SDV- 0045-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 115 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-28-SDV- 0045 | N/A | Shutdown Valve |  | LAUNCHER/RECEIVE R AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | LV Power (Refer Note 13) | 05 | EPS
380 | PS5-28-SDV- 0053A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 95 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-28-SDV- 0053A | N/A | Shutdown Valve |  | EXPORT PUMP AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=2 B=1 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-331-05-0226
381 | PS5-28-SDV- 0053B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 80 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-28-SDV- 0053B | N/A | Shutdown Valve |  | EXPORT PUMP AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 30-April-20206 | CPP-RFI-68-331-05-0239
382 | PS5-28-SDV- 0053C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 70 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-28-SDV- 0053C | N/A | Shutdown Valve |  | EXPORT PUMP AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-04-30 00:00:00 | CPP-RFI-68-331-05-0238
383 | PS5-50-IE-0001- CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 16 | 420 |  | PS5-61-IK-0001 | A0431 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-50-IE-0001 | N/A | Water Well Submersible Pump Control Panel A |  | Near Submerssiblre pump | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151119 | 28.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
384 | PS5-50-IE-0002- CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 16 | 550 |  | PS5-61-IK-0001 | B0423 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-50-IE-0002 | N/A | Water Well Submersible Pump Control Panel B |  | Near Submerssiblre pump | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112,151111,151108, 151107,151105 | 28.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
385 | PS5-53-DM- 3100A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 145 |  | PS5-61-IK-0001 | A0317 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-53-DM- 3100A | N/A | Water Distribution Pump A |  | Water Treatment Package Area | Ind - IP 55 | M25 / M32 |  | TZ-MID-68-WPR2- 151112,151109 | 21.6 | A=0 B=1 C=0 | 05 | EPS | 2026-04-16 00:00:00 | CPP-RFI-68-33/1-05-0219
386 | PS5-53-DM- 3100B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 150 |  | PS5-61-IK-0001 | B0623 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-53-DM- 3100B | N/A | Water Distribution Pump B |  | Water Treatment Package Area | Ind - IP 55 | M25 / M32 |  | TZ-MID-68-WPR2- 151112,151109 | 21.6 | A=0 B=1 C=0 | 05 | EPS | 2026-04-16 00:00:00 | CPP-RFI-68-33/1-05-0219
387 | PS5-53-IES- 3100A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 145 |  | PS5-61-IK-0001 | A0317 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-53-IES- 3100A | N/A | Water Distribution Pump A-LCS |  | Water Treatment Package Area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112,151109 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0219
388 | PS5-53-IES- 3100B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 150 |  | PS5-61-IK-0001 | B0623 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-53-IES- 3100B | N/A | Water Distribution Pump B-LCS |  | Water Treatment Package Area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112,151109 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0219
389 | PS5-53-IN-0001 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 16 | 190 |  | PS5-61-IK-0001 | C0307 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-53-IN-0001 | N/A | Water Treatment Package MCC |  | Water Treatment Pre Package | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112,151111,151108, 151109 | 28.2 | A=0 B=2 C=0 | 05 | EPS | 30-May-2026 | CPP-RFI-68-33/1-07-0307
390 | PS5-53-IN-0001 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 10 | 190 |  | PS5-06-IG- 0001A | N/A | AC UPS Distribution Board (A) Dual supply loads - 230VAC, 50Hz, 320A, 25KA/1s |  | EITS Building | Ind - IP 55 | M25 | PS5-53-IN-0001 | N/A | Water Treatment Package MCC |  | Water Treatment Pre Package | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112,151111,151108, 151109 | 22.6 | A=1 B=2 C=0 | 07 | EPS | 2026-05-24 00:00:00 | CPP-RFI-68-331-05-0295
391 | PS5-53-IN-0001 -CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 10 | 190 |  | PS5-06-IG- 0001B | N/A | AC UPS Distribution Board (B) Dual supply loads - 230VAC, 50Hz, 320A, 25KA/1s |  | EITS Building | Ind - IP 55 | M25 | PS5-53-IN-0001 | N/A | Water Treatment Package MCC |  | Water Treatment Pre Package | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112,151111,151108, 151109 | 22.6 | A=1 B=2 C=0 | 07 | EPS | 2026-05-24 00:00:00 | CPP-RFI-68-331-07-0296
392 | PS5-60-BE-0001 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 165 |  | PS5-60-IH-0002 | C5D | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE-0001 | N/A | Compressed air skid Battery Charger - JB |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
393 | PS5-60-BE-0001 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 165 |  | PS5-60-IH-0002 | C1A | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE-0001 | N/A | Compressed air skid Battery Charger - JB |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
394 | PS5-60-BE-0001 | 0.6/1KV | CU/XLPE/LSZH/ | 230V AC |  | 2C+E | 6 | 0 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical | Ind - IP | M20 | PS5-60-BE-0001 | N/A | Compressed air skid Battery Charger - JB |  | Generator Building | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, | 19.5 | UPS A | 08 | EPS
395 | PS5-60-BE-0001 -CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 210 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE-0001 | N/A | Compressed air skid Battery Charger - JB |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 19.5 | A=1 B=2 C=0 | 08 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
396 | PS5-60-BE-0002 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 165 |  | PS5-60-IH-0002 | C5A | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE-0002 | N/A | Compressed air Instru. skid Battery Charger - JB |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=1 B=2 C=0 | 06 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
397 | PS5-60-BE-0002 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 165 |  | PS5-60-IH-0002 | C1B | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE-0002 | N/A | Compressed air Instru. skid Battery Charger - JB |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=1 B=2 C=0 | 06 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
398 | PS5-60-BE-0002 -CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 165 |  | PS5-60-IH-0002 | C5C | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE-0002 | N/A | Compressed air Instru. skid Battery Charger - JB |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
399 | PS5-60-BE-0002 | 0.6/1KV | CU/XLPE/LSZH/ | 230V AC |  | 2C+E | 4 | 0 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical | Ind - IP | M20 | PS5-60-BE-0002 | N/A | Compressed air Instru. skid Battery Charger - JB |  | Generator Building | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, | 18.5 | UPS A | 08 | EPS
400 | PS5-60-BE-0002 -CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 210 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE-0002 | N/A | Compressed air Instru. skid Battery Charger - JB |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 18.5 | A=1 B=2 C=0 | 08 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
401 | PS5-60-BE- 0003A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 150 |  | PS5-60-IH- 0001A | C2I | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-60-BE- 0003A | N/A | JWH- Generator set-1 (A) - JW power connection JB |  | Generator Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 27.5 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
402 | PS5-60-BE- 0003B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 140 |  | PS5-60-IH- 0001B | C2I | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-60-BE- 0003B | N/A | JWH- Generator set-1 (B) - JW power connection JB |  | Generator Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 27.5 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
403 | PS5-60-BE- 0003C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 130 |  | PS5-60-IH- 0001C | C2I | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-60-BE- 0003C | N/A | JWH- Generator set-1 (C) - JW power connection JB |  | Generator Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 27.5 | LV Power_JW Heater_PS5- 60-HE-2100C | 05 | EPS
404 | PS5-60-BE- 0003D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 120 |  | PS5-60-IH- 0001D | C2I | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-60-BE- 0003D | N/A | JWH- Generator set-1 (D) - JW power connection JB |  | Generator Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 27.5 | LV Power_JW Heater_PS5- 60-HE-2100D | 05 | EPS
405 | PS5-60-BE- 0003E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 110 |  | PS5-60-IH- 0001E | C2I | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-60-BE- 0003E | N/A | JWH- Generator set-1 (E) - JW power connection JB |  | Generator Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 27.5 | LV Power_JW Heater_PS5- 60-HE-2100E | 05 | EPS
406 | PS5-60-BE- 0003F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 100 |  | PS5-60-IH-0001F | C2I | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-60-BE- 0003F | N/A | JWH- Generator set-1 (F) - JW power connection JB |  | Generator Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167,151116,151179 | 27.5 | LV Power_JW Heater_PS5- 60-HE-2100F | 05 | EPS
407 | PS5-60-BE- 0003G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 90 |  | PS5-60-IH- 0001G | C2I | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-60-BE- 0003G | N/A | JWH- Generator set-1 (G) - JW power connection JB |  | Generator Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167,151116,151179 | 27.5 | LV Power_JW Heater_PS5- 60-HE-2100G | 05 | EPS
408 | PS5-60-BE- 0004A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 150 |  | PS5-60-IH- 0001A | C2H | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-60-BE- 0004A | N/A | Lube oil separator (heater) - JB |  | Generator Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 27.5 | CRO MCC AUX Cable - Lube Oil Seperator (A) JB | 05 | EPS
409 | PS5-60-BE- 0004B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 140 |  | PS5-60-IH- 0001B | C2H | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-60-BE- 0004B | N/A | Lube oil separator (heater) - JB |  | Generator Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 27.5 | CRO MCC AUX Cable - Lube Oil Seperator (B) JB | 05 | EPS
410 | PS5-60-BE- 0004C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 130 |  | PS5-60-IH- 0001C | C2H | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-60-BE- 0004C | N/A | Lube oil separator (heater) - JB |  | Generator Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 27.5 | CRO MCC AUX Cable - Lube Oil Seperator (C) JB | 05 | EPS
411 | PS5-60-BE- 0004D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 120 |  | PS5-60-IH- 0001D | C2H | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-60-BE- 0004D | N/A | Lube oil separator (heater) - JB |  | Generator Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 27.5 | CRO MCC AUX Cable - Lube Oil Seperator (D) JB | 05 | EPS
412 | PS5-60-BE- 0004E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 110 |  | PS5-60-IH- 0001E | C2H | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-60-BE- 0004E | N/A | Lube oil separator (heater) - JB |  | Generator Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 27.5 | CRO MCC AUX Cable - Lube Oil Seperator (E) JB | 05 | EPS
413 | PS5-60-BE- 0004F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 100 |  | PS5-60-IH-0001F | C2H | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-60-BE- 0004F | N/A | Lube oil separator (heater) - JB |  | Generator Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167,151116,151179 | 27.5 | CRO MCC AUX Cable - Lube Oil Seperator (F) JB | 05 | EPS
414 | PS5-60-BE- 0004G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 90 |  | PS5-60-IH- 0001G | C2H | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-60-BE- 0004G | N/A | Lube oil separator (heater) - JB |  | Generator Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167,151116,151179 | 27.5 | CRO MCC AUX Cable - Lube Oil Seperator (G) JB | 05 | EPS
415 | PS5-60-BE- 0005A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 150 |  | PS5-60-IH- 0001A | C2F | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0005A | N/A | CRO Gen Pre-Lube and Barring Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
416 | PS5-60-BE- 0005B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 140 |  | PS5-60-IH- 0001B | C2F | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0005B | N/A | CRO Gen Pre-Lube and Barring Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
417 | PS5-60-BE- 0005C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-60-IH- 0001C | C2F | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0005C | N/A | CRO Gen Pre-Lube and Barring Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 18.1 | LV Power_Pre-lubrication pump motor_PS5-60-DM- 32300C | 05 | EPS
418 | PS5-60-BE- 0005D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 120 |  | PS5-60-IH- 0001D | C2F | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0005D | N/A | CRO Gen Pre-Lube and Barring Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
419 | PS5-60-BE- 0005E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 110 |  | PS5-60-IH- 0001E | C2F | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0005E | N/A | CRO Gen Pre-Lube and Barring Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 18.1 | LV Power_Pre-lubrication pump motor_PS5-60-DM- 32300E | 05 | EPS
420 | PS5-60-BE- 0005F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 100 |  | PS5-60-IH-0001F | C2F | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0005F | N/A | CRO Gen Pre-Lube and Barring Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151116,151179 | 18.1 | LV Power_Pre-lubrication pump motor_PS5-60-DM- 32300F | 05 | EPS
421 | PS5-60-BE- 0005G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 90 |  | PS5-60-IH- 0001G | C2F | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0005G | N/A | CRO Gen Pre-Lube and Barring Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151116,151179 | 18.1 | LV Power_Pre-lubrication pump motor_PS5-60-DM- 32300G | 05 | EPS
422 | PS5-60-BE- 0007A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007A | N/A | FCU- fuel conditioning module Generator set-1 (A) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | A=1 B=2 C=0 | 07 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
423 | PS5-60-BE- 0007A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007A | N/A | FCU- fuel conditioning module Generator set-1 (A) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | A=1 B=2 C=0 | 08 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
424 | PS5-60-BE- 0007A-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007A | N/A | FCU- fuel conditioning module Generator set-1 (A) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | A=1 B=2 C=0 | 08 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
425 | PS5-60-BE- 0007B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007B | N/A | FCU- fuel conditioning module Generator set-2 (B) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | A=1 B=2 C=0 | 07 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
426 | PS5-60-BE- 0007B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007B | N/A | FCU- fuel conditioning module Generator set-2 (B) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | A=1 B=2 C=0 | 08 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
427 | PS5-60-BE- 0007B-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007B | N/A | FCU- fuel conditioning module Generator set-2 (B) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | A=1 B=2 C=0 | 08 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
428 | PS5-60-BE- 0007C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007C | N/A | FCU- fuel conditioning module Generator set-3 (C) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | TRACE HEATER MODULE E03.1 | 07 | EPS
429 | PS5-60-BE- 0007C-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007C | N/A | FCU- fuel conditioning module Generator set-3 (C) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | POWER CABLE_DUPLEXFUEL FILTER ELEMENT-1 GENERATOR-C) | 08 | EPS
430 | PS5-60-BE- 0007C-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007C | N/A | FCU- fuel conditioning module Generator set-3 (C) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | POWER CABLE_DUPLEXFUEL FILTER ELEMENT-2 GENERATOR-C) | 08 | EPS
431 | PS5-60-BE- 0007D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007D | N/A | FCU- fuel conditioning module Generator set-4 (D) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | A=0 B=1 C=0 | 07 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
432 | PS5-60-BE- 0007D-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007D | N/A | FCU- fuel conditioning module Generator set-4 (D) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | A=1 B=2 C=0 | 08 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
433 | PS5-60-BE- 0007D-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007D | N/A | FCU- fuel conditioning module Generator set-4 (D) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | A=1 B=2 C=0 | 08 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
434 | PS5-60-BE- 0007E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007E | N/A | FCU- fuel conditioning module Generator set-5 (E) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | TRACE HEATER MODULE E03.1 | 07 | EPS
435 | PS5-60-BE- 0007E-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007E | N/A | FCU- fuel conditioning module Generator set-5 (E) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | POWER CABLE_DUPLEXFUEL FILTER ELEMENT-1 GENERATOR-E) | 08 | EPS
436 | PS5-60-BE- 0007E-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007E | N/A | FCU- fuel conditioning module Generator set-5 (E) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | POWER CABLE_DUPLEXFUEL FILTER ELEMENT-2 GENERATOR-E) | 08 | EPS
437 | PS5-60-BE- 0007F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007F | N/A | FCU- fuel conditioning module Generator set-6 (6) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | TRACE HEATER MODULE E03.1 | 07 | EPS
438 | PS5-60-BE- 0007F-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007F | N/A | FCU- fuel conditioning module Generator set-6 (6) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | POWER CABLE_DUPLEXFUEL FILTER ELEMENT-1 GENERATOR-F) | 08 | EPS
439 | PS5-60-BE- 0007F-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007F | N/A | FCU- fuel conditioning module Generator set-6 (6) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | POWER CABLE_DUPLEXFUEL FILTER ELEMENT-2 GENERATOR-F) | 08 | EPS
440 | PS5-60-BE- 0007G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007G | N/A | FCU- fuel conditioning module Generator set-7 (G) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | TRACE HEATER MODULE E03.1 | 07 | EPS
441 | PS5-60-BE- 0007G-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007G | N/A | FCU- fuel conditioning module Generator set-7 (G) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | POWER CABLE_DUPLEXFUEL FILTER ELEMENT-1 GENERATOR-G) | 08 | EPS
442 | PS5-60-BE- 0007G-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0007G | N/A | FCU- fuel conditioning module Generator set-7 (G) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | POWER CABLE_DUPLEXFUEL FILTER ELEMENT-2 GENERATOR-G) | 08 | EPS
443 | PS5-60-BE- 0011A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 150 |  | PS5-60-IH- 0001A | C4B | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0011A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
444 | PS5-60-BE- 0011A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 150 |  | PS5-60-IH- 0001A | C4C | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0011A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
445 | PS5-60-BE- 0011A-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 150 |  | PS5-60-IH- 0001A | C4D | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0011A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
446 | PS5-60-BE- 0011A-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 150 |  | PS5-60-IH- 0001A | C4E | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0011A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
447 | PS5-60-BE- 0011A-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 150 |  | PS5-60-IH- 0001A | C4F | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0011A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
448 | PS5-60-BE- 0011A-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 150 |  | PS5-60-IH- 0001A | C4G | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0011A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
449 | PS5-60-BE- 0011B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 150 |  | PS5-60-IH- 0001A | C4H | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0011B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
450 | PS5-60-BE- 0011B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 150 |  | PS5-60-IH- 0001A | C4I | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0011B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
451 | PS5-60-BE- 0011B-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 150 |  | PS5-60-IH- 0001A | C4J | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0011B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
452 | PS5-60-BE- 0011B-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 150 |  | PS5-60-IH- 0001A | C4K | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0011B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
453 | PS5-60-BE- 0011B-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 150 |  | PS5-60-IH- 0001A | C4L | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0011B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
454 | PS5-60-BE- 0011B-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 150 |  | PS5-60-IH- 0001A | C4M | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0011B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
455 | PS5-60-BE- 0012A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 140 |  | PS5-60-IH- 0001B | C4B | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0012A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
456 | PS5-60-BE- 0012A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 140 |  | PS5-60-IH- 0001B | C4C | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0012A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
457 | PS5-60-BE- 0012A-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 140 |  | PS5-60-IH- 0001B | C4D | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0012A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
458 | PS5-60-BE- 0012A-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 140 |  | PS5-60-IH- 0001B | C4E | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0012A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
459 | PS5-60-BE- 0012A-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 140 |  | PS5-60-IH- 0001B | C4F | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0012A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
460 | PS5-60-BE- 0012A-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 140 |  | PS5-60-IH- 0001B | C4G | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0012A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
461 | PS5-60-BE- 0012B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 140 |  | PS5-60-IH- 0001B | C4H | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0012B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
462 | PS5-60-BE- 0012B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 140 |  | PS5-60-IH- 0001B | C4I | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0012B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
463 | PS5-60-BE- 0012B-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 140 |  | PS5-60-IH- 0001B | C4J | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0012B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
464 | PS5-60-BE- 0012B-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 140 |  | PS5-60-IH- 0001B | C4K | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0012B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
465 | PS5-60-BE- 0012B-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 140 |  | PS5-60-IH- 0001B | C4L | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0012B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
466 | PS5-60-BE- 0012B-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 140 |  | PS5-60-IH- 0001B | C4M | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0012B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
467 | PS5-60-BE- 0013A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 130 |  | PS5-60-IH- 0001C | C4B | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0013A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-1A_PS5-60-DM -6900A | 05 | EPS
468 | PS5-60-BE- 0013A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 130 |  | PS5-60-IH- 0001C | C4C | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0013A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-2A_PS5-60-DM -6900B | 05 | EPS
469 | PS5-60-BE- 0013A-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 130 |  | PS5-60-IH- 0001C | C4D | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0013A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-3A_PS5-60-DM -6900C | 05 | EPS
470 | PS5-60-BE- 0013A-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 130 |  | PS5-60-IH- 0001C | C4E | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0013A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-4A_PS5-60-DM -6900D | 05 | EPS
471 | PS5-60-BE- 0013A-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 130 |  | PS5-60-IH- 0001C | C4F | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0013A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-5A_PS5-60-DM -6900E | 05 | EPS
472 | PS5-60-BE- 0013A-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 130 |  | PS5-60-IH- 0001C | C4G | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0013A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-6A_PS5-60-DM -6900F | 05 | EPS
473 | PS5-60-BE- 0013B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 130 |  | PS5-60-IH- 0001C | C4H | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0013B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-1B_PS5-60-DM -61100A | 05 | EPS
474 | PS5-60-BE- 0013B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 130 |  | PS5-60-IH- 0001C | C4I | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0013B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-2B_PS5-60-DM -61100B | 05 | EPS
475 | PS5-60-BE- 0013B-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 130 |  | PS5-60-IH- 0001C | C4J | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0013B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-3B_PS5-60-DM -61100C | 05 | EPS
476 | PS5-60-BE- 0013B-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 130 |  | PS5-60-IH- 0001C | C4K | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0013B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-4B_PS5-60-DM -61100D | 05 | EPS
477 | PS5-60-BE- 0013B-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 130 |  | PS5-60-IH- 0001C | C4L | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0013B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-5B_PS5-60-DM -61100E | 05 | EPS
478 | PS5-60-BE- 0013B-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 130 |  | PS5-60-IH- 0001C | C4M | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0013B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-6B_PS5-60-DM -61100F | 05 | EPS
479 | PS5-60-BE- 0014A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 120 |  | PS5-60-IH- 0001D | C4B | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0014A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-1A_PS5-60-DM -61200A | 05 | EPS
480 | PS5-60-BE- 0014A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 120 |  | PS5-60-IH- 0001D | C4C | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0014A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-2A_PS5-60-DM -61200B | 05 | EPS
481 | PS5-60-BE- 0014A-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 120 |  | PS5-60-IH- 0001D | C4D | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0014A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-3A_PS5-60-DM -61200C | 05 | EPS
482 | PS5-60-BE- 0014A-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 120 |  | PS5-60-IH- 0001D | C4E | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0014A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-4A_PS5-60-DM -61200D | 05 | EPS
483 | PS5-60-BE- 0014A-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 120 |  | PS5-60-IH- 0001D | C4F | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0014A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-5A_PS5-60-DM -61200E | 05 | EPS
484 | PS5-60-BE- 0014A-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 120 |  | PS5-60-IH- 0001D | C4G | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0014A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-6A_PS5-60-DM -61200F | 05 | EPS
485 | PS5-60-BE- 0014B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 120 |  | PS5-60-IH- 0001D | C4H | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0014B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-1B_PS5-60-DM -61300A | 05 | EPS
486 | PS5-60-BE- 0014B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 120 |  | PS5-60-IH- 0001D | C4I | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0014B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-2B_PS5-60-DM -61300B | 05 | EPS
487 | PS5-60-BE- 0014B-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 120 |  | PS5-60-IH- 0001D | C4J | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0014B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-3B_PS5-60-DM -61300C | 05 | EPS
488 | PS5-60-BE- 0014B-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 120 |  | PS5-60-IH- 0001D | C4K | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0014B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-4B_PS5-60-DM -61300D | 05 | EPS
489 | PS5-60-BE- 0014B-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 120 |  | PS5-60-IH- 0001D | C4L | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0014B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-5B_PS5-60-DM -61300E | 05 | EPS
490 | PS5-60-BE- 0014B-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 120 |  | PS5-60-IH- 0001D | C4M | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0014B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-6B_PS5-60-DM -61300F | 05 | EPS
491 | PS5-60-BE- 0015A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 110 |  | PS5-60-IH- 0001E | C4B | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0015A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-1A_PS5-60-DM -61400A | 05 | EPS
492 | PS5-60-BE- 0015A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 110 |  | PS5-60-IH- 0001E | C4C | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0015A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-2A_PS5-60-DM -61400B | 05 | EPS
493 | PS5-60-BE- 0015A-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 110 |  | PS5-60-IH- 0001E | C4D | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0015A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-3A_PS5-60-DM -61400C | 05 | EPS
494 | PS5-60-BE- 0015A-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 110 |  | PS5-60-IH- 0001E | C4E | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0015A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-4A_PS5-60-DM -61400D | 05 | EPS
495 | PS5-60-BE- 0015A-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 110 |  | PS5-60-IH- 0001E | C4F | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0015A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-5A_PS5-60-DM -61400E | 05 | EPS
496 | PS5-60-BE- 0015A-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 110 |  | PS5-60-IH- 0001E | C4G | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0015A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-6A_PS5-60-DM -61400F | 05 | EPS
497 | PS5-60-BE- 0015B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 110 |  | PS5-60-IH- 0001E | C4H | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0015B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-1B_PS5-60-DM -61500A | 05 | EPS
498 | PS5-60-BE- 0015B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 110 |  | PS5-60-IH- 0001E | C4I | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0015B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-2B_PS5-60-DM -61500B | 05 | EPS
499 | PS5-60-BE- 0015B-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 110 |  | PS5-60-IH- 0001E | C4J | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0015B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-3B_PS5-60-DM -61500C | 05 | EPS
500 | PS5-60-BE- 0015B-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 110 |  | PS5-60-IH- 0001E | C4K | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0015B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-4B_PS5-60-DM -61500D | 05 | EPS
501 | PS5-60-BE- 0015B-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 110 |  | PS5-60-IH- 0001E | C4L | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0015B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-5B_PS5-60-DM -61500E | 05 | EPS
502 | PS5-60-BE- 0015B-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 110 |  | PS5-60-IH- 0001E | C4M | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0015B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-6B_PS5-60-DM -61500F | 05 | EPS
503 | PS5-60-BE- 0016A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 100 |  | PS5-60-IH-0001F | C4B | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0016A | N/A | CRO Generator- Control JB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-1A_PS5-60-DM -61600A | 05 | EPS
504 | PS5-60-BE- 0016A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 100 |  | PS5-60-IH-0001F | C4C | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0016A | N/A | CRO Generator- Control JB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-2A_PS5-60-DM -61600B | 05 | EPS
505 | PS5-60-BE- 0016A-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 100 |  | PS5-60-IH-0001F | C4D | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0016A | N/A | CRO Generator- Control JB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-3A_PS5-60-DM -61600C | 05 | EPS
506 | PS5-60-BE- 0016A-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 100 |  | PS5-60-IH-0001F | C4E | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0016A | N/A | CRO Generator- Control JB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-4A_PS5-60-DM -61600D | 05 | EPS
507 | PS5-60-BE- 0016A-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 100 |  | PS5-60-IH-0001F | C4F | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0016A | N/A | CRO Generator- Control JB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-5A_PS5-60-DM -61600E | 05 | EPS
508 | PS5-60-BE- 0016A-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 100 |  | PS5-60-IH-0001F | C4G | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0016A | N/A | CRO Generator- Control JB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-6A_PS5-60-DM -61600F | 05 | EPS
509 | PS5-60-BE- 0016B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 100 |  | PS5-60-IH-0001F | C4H | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0016B | N/A | CRO Generator- Control JB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-1B_PS5-60-DM -61700A | 05 | EPS
510 | PS5-60-BE- 0016B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 100 |  | PS5-60-IH-0001F | C4I | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0016B | N/A | CRO Generator- Control JB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-2B_PS5-60-DM -61700B | 05 | EPS
511 | PS5-60-BE- 0016B-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 100 |  | PS5-60-IH-0001F | C4J | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0016B | N/A | CRO Generator- Control JB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-3B_PS5-60-DM -61700C | 05 | EPS
512 | PS5-60-BE- 0016B-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 100 |  | PS5-60-IH-0001F | C4K | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0016B | N/A | CRO Generator- Control JB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-4B_PS5-60-DM -61700D | 05 | EPS
513 | PS5-60-BE- 0016B-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 100 |  | PS5-60-IH-0001F | C4L | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0016B | N/A | CRO Generator- Control JB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-5B_PS5-60-DM -61700E | 05 | EPS
514 | PS5-60-BE- 0016B-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 100 |  | PS5-60-IH-0001F | C4M | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0016B | N/A | CRO Generator- Control JB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-6B_PS5-60-DM -61700F | 05 | EPS
515 | PS5-60-BE- 0017A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 90 |  | PS5-60-IH- 0001G | C4B | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0017A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-1A_PS5-60-DM -61800A | 05 | EPS
516 | PS5-60-BE- 0017A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 90 |  | PS5-60-IH- 0001G | C4C | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0017A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-2A_PS5-60-DM -61800B | 05 | EPS
517 | PS5-60-BE- 0017A-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 90 |  | PS5-60-IH- 0001G | C4D | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0017A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-3A_PS5-60-DM -61800C | 05 | EPS
518 | PS5-60-BE- 0017A-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 90 |  | PS5-60-IH- 0001G | C4E | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0017A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-4A_PS5-60-DM -61800D | 05 | EPS
519 | PS5-60-BE- 0017A-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 90 |  | PS5-60-IH- 0001G | C4F | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0017A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-5A_PS5-60-DM -61800E | 05 | EPS
520 | PS5-60-BE- 0017A-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 90 |  | PS5-60-IH- 0001G | C4G | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0017A | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-6A_PS5-60-DM -61800F | 05 | EPS
521 | PS5-60-BE- 0017B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 90 |  | PS5-60-IH- 0001G | C4H | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0017B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-1B_PS5-60-DM -61900A | 05 | EPS
522 | PS5-60-BE- 0017B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 90 |  | PS5-60-IH- 0001G | C4I | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0017B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-2B_PS5-60-DM -61900B | 05 | EPS
523 | PS5-60-BE- 0017B-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 90 |  | PS5-60-IH- 0001G | C4J | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0017B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-3B_PS5-60-DM -61900C | 05 | EPS
524 | PS5-60-BE- 0017B-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 90 |  | PS5-60-IH- 0001G | C4K | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0017B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-4B_PS5-60-DM -61900D | 05 | EPS
525 | PS5-60-BE- 0017B-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 90 |  | PS5-60-IH- 0001G | C4L | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0017B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-5B_PS5-60-DM -61900E | 05 | EPS
526 | PS5-60-BE- 0017B-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 90 |  | PS5-60-IH- 0001G | C4M | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0017B | N/A | CRO Generator- PowerJB |  | Near Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118 | 19.5 | LV Power_Engine cooling Radiator Fan-6B_PS5-60-DM -61900F | 05 | EPS
527 | PS5-60-BE- 0021A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 160 |  | PS5-60-IH-0002 | C1E | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0021A | N/A | Chimney (1) Aviation Lights - JB |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=1 B=2 C=0 | 06 | EPS | 2026-06-04 00:00:00 | CPP-RFI-68-33/1-05-0309
528 | PS5-60-BE- 0021B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 160 |  | PS5-60-IH-0002 | C1D | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0021B | N/A | Chimney (2) Aviation Lights - JB |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=1 B=2 C=0 | 06 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
529 | PS5-60-BE- 0024A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 150 |  | PS5-60-IH- 0001A | C2A | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0024A | N/A | Tip Cooling Pump motor - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
530 | PS5-60-BE- 0024A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 150 |  | PS5-60-IH- 0001A | C2E | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0024A | N/A | Tip Cooling Pump motor - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
531 | PS5-60-BE- 0024B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 140 |  | PS5-60-IH- 0001B | C2A | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0024B | N/A | Tip Cooling Pump motor - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
532 | PS5-60-BE- 0024B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 140 |  | PS5-60-IH- 0001B | C2E | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0024B | N/A | Tip Cooling Pump motor - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
533 | PS5-60-BE- 0024C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-60-IH- 0001C | C2A | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0024C | N/A | Tip Cooling Pump motor - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | LV Power_ INJECTOR TIP COOLING PUMP MOTOR- 1_PS5-60-DM-3500C | 05 | EPS
534 | PS5-60-BE- 0024C-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-60-IH- 0001C | C2E | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0024C | N/A | Tip Cooling Pump motor - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | LV Power_INJECTOR TIP COOLING PUMP MOTOR- 2_PS5-60-DM-32700C | 05 | EPS
535 | PS5-60-BE- 0024D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 120 |  | PS5-60-IH- 0001D | C2A | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0024D | N/A | Tip Cooling Pump motor - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
536 | PS5-60-BE- 0024D-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 120 |  | PS5-60-IH- 0001D | C2E | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0024D | N/A | Tip Cooling Pump motor - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
537 | PS5-60-BE- 0024E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 110 |  | PS5-60-IH- 0001E | C2A | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0024E | N/A | Tip Cooling Pump motor - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | LV Power_INJECTOR TIP COOLING PUMP MOTOR- 1_PS5-60-DM-3500E | 05 | EPS
538 | PS5-60-BE- 0024E-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 110 |  | PS5-60-IH- 0001E | C2E | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0024E | N/A | Tip Cooling Pump motor - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | LV Power_ INJECTOR TIP COOLING PUMP MOTOR- 2_PS5-60-DM-32700E | 05 | EPS
539 | PS5-60-BE- 0024F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 100 |  | PS5-60-IH-0001F | C2A | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0024F | N/A | Tip Cooling Pump motor - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | LV Power_INJECTOR TIP COOLING PUMP MOTOR- 1_PS5-60-DM-3500F | 05 | EPS
540 | PS5-60-BE- 0024F-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 100 |  | PS5-60-IH-0001F | C2E | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0024F | N/A | Tip Cooling Pump motor - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | LV Power_INJECTOR TIP COOLING PUMP MOTOR- 2_PS5-60-DM-32700F | 05 | EPS
541 | PS5-60-BE- 0024G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 90 |  | PS5-60-IH- 0001G | C2A | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0024G | N/A | Tip Cooling Pump motor - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | LV Power_INJECTOR TIP COOLING PUMP MOTOR- 1_PS5-60-DM-3500G | 05 | EPS
542 | PS5-60-BE- 0024G-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 90 |  | PS5-60-IH- 0001G | C2E | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0024G | N/A | Tip Cooling Pump motor - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | LV Power_INJECTOR TIP COOLING PUMP MOTOR- 2_PS5-60-DM-32700G | 05 | EPS
543 | PS5-60-BE- 0025A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 150 |  | PS5-60-IH- 0001A | C3B | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0025A | N/A | Junction Box - Injector Tip Cooling Radiator (A)- OIL cooler |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
544 | PS5-60-BE- 0025B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 140 |  | PS5-60-IH- 0001B | C3B | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0025B | N/A | Junction Box - Injector Tip Cooling Radiator (B)- OIL cooler |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
545 | PS5-60-BE- 0025C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-60-IH- 0001C | C3B | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0025C | N/A | Junction Box - Injector Tip Cooling Radiator (C)- OIL cooler |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | LV Power_Tip Cooling Cooler Motor_PS5-60-DM- 6100C | 05 | EPS
546 | PS5-60-BE- 0025D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 120 |  | PS5-60-IH- 0001D | C3B | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0025D | N/A | Junction Box - njector Tip Cooling Radiator (D)- OIL cooler |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
547 | PS5-60-BE- 0025E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 110 |  | PS5-60-IH- 0001E | C3B | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0025E | N/A | Junction Box - Injector Tip Cooling Radiator (E)- OIL cooler |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | LV Power_Tip Cooling Cooler Motor_PS5-60-DM- 6100E | 05 | EPS
548 | PS5-60-BE- 0025F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 100 |  | PS5-60-IH-0001F | C3B | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0025F | N/A | Junction Box - Injector Tip Cooling Radiator (F)- OIL cooler |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | LV Power_Tip Cooling Cooler Motor_PS5-60-DM- 6100F | 05 | EPS
549 | PS5-60-BE- 0025G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 90 |  | PS5-60-IH- 0001G | C3B | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0025G | N/A | Junction Box - Injector Tip Cooling Radiator (G)- OIL cooler |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | LV Power_Tip Cooling Cooler Motor_PS5-60-DM- 6100G | 05 | EPS
550 | PS5-60-BE- 0026A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 150 |  | PS5-60-IH- 0001A | C2C | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0026A | N/A | CW Module - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
551 | PS5-60-BE- 0026A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 150 |  | PS5-60-IH- 0001A | C3A | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0026A | N/A | CW Module - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
552 | PS5-60-BE- 0026B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 140 |  | PS5-60-IH- 0001B | C2C | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0026B | N/A | CW Module - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
553 | PS5-60-BE- 0026B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 140 |  | PS5-60-IH- 0001B | C3A | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0026B | N/A | CW Module - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
554 | PS5-60-BE- 0026C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-60-IH- 0001C | C2C | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0026C | N/A | CW Module - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | LV Power_Drive END DE Bearing Water circulation pump_PS5-60-DM-33100C | 05 | EPS
555 | PS5-60-BE- 0026C-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-60-IH- 0001C | C3A | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0026C | N/A | CW Module - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
556 | PS5-60-BE- 0026D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 120 |  | PS5-60-IH- 0001D | C2C | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0026D | N/A | CW Module - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
557 | PS5-60-BE- 0026D-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 120 |  | PS5-60-IH- 0001D | C3A | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0026D | N/A | CW Module - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
558 | PS5-60-BE- 0026E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 110 |  | PS5-60-IH- 0001E | C2C | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0026E | N/A | CW Module - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | LV Power_Drive END DE Bearing Water circulation pump_PS5-60-DM-33100E | 05 | EPS
559 | PS5-60-BE- 0026E-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 110 |  | PS5-60-IH- 0001E | C3A | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0026E | N/A | CW Module - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
560 | PS5-60-BE- 0026F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 100 |  | PS5-60-IH-0001F | C2C | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0026F | N/A | CW Module - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | LV Power_Drive END DE Bearing Water circulation pump_PS5-60-DM-33100F | 05 | EPS
561 | PS5-60-BE- 0026F-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 100 |  | PS5-60-IH-0001F | C3A | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0026F | N/A | CW Module - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-05-0329
562 | PS5-60-BE- 0026G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 90 |  | PS5-60-IH- 0001G | C2C | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0026G | N/A | CW Module - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | LV Power_Drive END DE Bearing Water circulation pump_PS5-60-DM-33100G | 05 | EPS
563 | PS5-60-BE- 0026G-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 90 |  | PS5-60-IH- 0001G | C3A | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BE- 0026G | N/A | CW Module - Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
564 | PS5-60-BE- 0027A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 30 |  | PS5-60-BE- 0007A | N/A | FCU- fuel conditioning module Generator set-1 (A) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 | PS5-60-BE- 0027A | N/A | Duplex fuel filter Element -1 trace heating Generator Set-1 (A) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | A=1 B=2 C=0 | 08 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
565 | PS5-60-BE- 0027B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 30 |  | PS5-60-BE- 0007B | N/A | FCU- fuel conditioning module Generator set-2 (B) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 | PS5-60-BE- 0027B | N/A | Duplex fuel filter Element -1 trace heating Generator Set-1 (B) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | Power cable_Duplex fuel filter -Element-1 (generator- B) | 08 | EPS
566 | PS5-60-BE- 0027C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 30 |  | PS5-60-BE- 0007C | N/A | FCU- fuel conditioning module Generator set-3 (C) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 | PS5-60-BE- 0027C | N/A | Duplex fuel filter Element -1 trace heating Generator Set-1 (C) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | Power cable_Duplex fuel filter -Element-1 (generator- C) | 08 | EPS
567 | PS5-60-BE- 0027D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 30 |  | PS5-60-BE- 0007D | N/A | FCU- fuel conditioning module Generator set-4 (D) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 | PS5-60-BE- 0027D | N/A | Duplex fuel filter Element -1 trace heating Generator Set-1 (D) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | Power cable_Duplex fuel filter -Element-1 (generator- D) | 08 | EPS
568 | PS5-60-BE- 0027E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 35 |  | PS5-60-BE- 0007E | N/A | FCU- fuel conditioning module Generator set-5 (E) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 | PS5-60-BE- 0027E | N/A | Duplex fuel filter Element -1 trace heating Generator Set-1 (E) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | Power cable_Duplex fuel filter -Element-1 (generator- E) | 08 | EPS
569 | PS5-60-BE- 0027F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 35 |  | PS5-60-BE- 0007F | N/A | FCU- fuel conditioning module Generator set-6 (6) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 | PS5-60-BE- 0027F | N/A | Duplex fuel filter Element -1 trace heating Generator Set-6 (F) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | Power cable_Duplex fuel filter -Element-1 (generator- F) | 08 | EPS
570 | PS5-60-BE- 0027G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 35 |  | PS5-60-BE- 0007G | N/A | FCU- fuel conditioning module Generator set-7 (G) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 | PS5-60-BE- 0027G | N/A | Duplex fuel filter Element -1 trace heating Generator Set-7 (G) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | Power cable_Duplex fuel filter -Element-1 (generator- G) | 08 | EPS
571 | PS5-60-BE- 0028A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 35 |  | PS5-60-BE- 0007A | N/A | FCU- fuel conditioning module Generator set-1 (A) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 | PS5-60-BE- 0028A | N/A | Duplex fuel filter Element -2 trace heating Generator Set-1 (A) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | A=1 B=2 C=0 | 08 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
572 | PS5-60-BE- 0028B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 35 |  | PS5-60-BE- 0007B | N/A | FCU- fuel conditioning module Generator set-2 (B) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 | PS5-60-BE- 0028B | N/A | Duplex fuel filter Element -2 trace heating Generator Set-2 (B) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | A=1 B=2 C=0 | 08 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
573 | PS5-60-BE- 0028C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 35 |  | PS5-60-BE- 0007C | N/A | FCU- fuel conditioning module Generator set-3 (C) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 | PS5-60-BE- 0028C | N/A | Duplex fuel filter Element -2 trace heating Generator Set-3 (C) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | Power cable_Duplex fuel filter -Element-2 (generator- C) | 08 | EPS
574 | PS5-60-BE- 0028D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 35 |  | PS5-60-BE- 0007D | N/A | FCU- fuel conditioning module Generator set-4 (D) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 | PS5-60-BE- 0028D | N/A | Duplex fuel filter Element -2 trace heating Generator Set-4 (D) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | Power cable_Duplex fuel filter -Element-2 (generator- D) | 08 | EPS
575 | PS5-60-BE- 0028E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 35 |  | PS5-60-BE- 0007E | N/A | FCU- fuel conditioning module Generator set-5 (E) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 | PS5-60-BE- 0028E | N/A | Duplex fuel filter Element -2 trace heating Generator Set-5 (E) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | Power cable_Duplex fuel filter -Element-2 (generator- E) | 08 | EPS
576 | PS5-60-BE- 0028F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 35 |  | PS5-60-BE- 0007F | N/A | FCU- fuel conditioning module Generator set-6 (6) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 | PS5-60-BE- 0028F | N/A | Duplex fuel filter Element -2 trace heating Generator Set-6 (F) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | Power cable_Duplex fuel filter -Element-2 (generator- F) | 08 | EPS
577 | PS5-60-BE- 0028G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 35 |  | PS5-60-BE- 0007G | N/A | FCU- fuel conditioning module Generator set-7 (G) Trace heater Power JB-3 |  | Generator Building | Ind - IP 55 | M20 | PS5-60-BE- 0028G | N/A | Duplex fuel filter Element -2 trace heating Generator Set-7 (G) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | Power cable_Duplex fuel filter -Element-2 (generator- G) | 08 | EPS
578 | PS5-60-BI- 0005A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 150 |  | PS5-60-IH- 0001A | C2B | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0005A | N/A | NER (A) Space Heater - Control Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 17.2 | A=1 B=2 C=0 | 05 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
579 | PS5-60-BI- 0005B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 140 |  | PS5-60-IH- 0001B | C2B | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0005B | N/A | NER (B) Space Heater - Control Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 17.2 | A=1 B=2 C=0 | 05 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
580 | PS5-60-BI- 0005C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 130 |  | PS5-60-IH- 0001C | C2B | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0005C | N/A | NER (C) Space Heater - Control Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 17.2 | A=1 B=2 C=0 | 05 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
581 | PS5-60-BI- 0005D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 120 |  | PS5-60-IH- 0001D | C2B | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0005D | N/A | NER (D) Space Heater - Control Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 17.2 | A=1 B=2 C=0 | 05 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
582 | PS5-60-BI- 0005E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 110 |  | PS5-60-IH- 0001E | C2B | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0005E | N/A | NER (E) Space Heater - Control Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 17.2 | A=1 B=2 C=0 | 05 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
583 | PS5-60-BI- 0005F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 100 |  | PS5-60-IH-0001F | C2B | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0005F | N/A | NER (F) Space Heater - Control Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=1 B=2 C=0 | 05 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
584 | PS5-60-BI- 0005G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 90 |  | PS5-60-IH- 0001G | C2B | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0005G | N/A | NER (G) Space Heater - Control Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=1 B=2 C=0 | 05 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
585 | PS5-60-BI- 0006A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 25 |  | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006A | N/A | FCU- fuel conditioning module Generator set-1 (A) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
586 | PS5-60-BI- 0006A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 25 |  | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006A | N/A | FCU- fuel conditioning module Generator set-1 (A) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | A=1 B=2 C=0 | 07 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
587 | PS5-60-BI- 0006A-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006A | N/A | FCU- fuel conditioning module Generator set-1 (A) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
588 | PS5-60-BI- 0006A-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006A | N/A | FCU- fuel conditioning module Generator set-1 (A) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
589 | PS5-60-BI- 0006A-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006A | N/A | FCU- fuel conditioning module Generator set-1 (A) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
590 | PS5-60-BI- 0006A-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006A | N/A | FCU- fuel conditioning module Generator set-1 (A) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
591 | PS5-60-BI- 0006A-CL07 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006A | N/A | FCU- fuel conditioning module Generator set-1 (A) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
592 | PS5-60-BI- 0006A-CL08 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006A | N/A | FCU- fuel conditioning module Generator set-1 (A) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
593 | PS5-60-BI- 0006A-CL09 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006A | N/A | FCU- fuel conditioning module Generator set-1 (A) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
594 | PS5-60-BI- 0006A-CL10 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006A | N/A | FCU- fuel conditioning module Generator set-1 (A) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
595 | PS5-60-BI- 0006A-CL11 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006A | N/A | FCU- fuel conditioning module Generator set-1 (A) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
596 | PS5-60-BI- 0006B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 25 |  | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006B | N/A | FCU- fuel conditioning module Generator set-2 (B) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
597 | PS5-60-BI- 0006B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 25 |  | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006B | N/A | FCU- fuel conditioning module Generator set-2 (B) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
598 | PS5-60-BI- 0006B-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006B | N/A | FCU- fuel conditioning module Generator set-2 (B) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
599 | PS5-60-BI- 0006B-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006B | N/A | FCU- fuel conditioning module Generator set-2 (B) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
600 | PS5-60-BI- 0006B-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006B | N/A | FCU- fuel conditioning module Generator set-2 (B) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
601 | PS5-60-BI- 0006B-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006B | N/A | FCU- fuel conditioning module Generator set-2 (B) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
602 | PS5-60-BI- 0006B-CL07 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006B | N/A | FCU- fuel conditioning module Generator set-2 (B) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
603 | PS5-60-BI- 0006B-CL08 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006B | N/A | FCU- fuel conditioning module Generator set-2 (B) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
604 | PS5-60-BI- 0006B-CL09 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006B | N/A | FCU- fuel conditioning module Generator set-2 (B) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
605 | PS5-60-BI- 0006B-CL10 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006B | N/A | FCU- fuel conditioning module Generator set-2 (B) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
606 | PS5-60-BI- 0006B-CL11 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006B | N/A | FCU- fuel conditioning module Generator set-2 (B) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
607 | PS5-60-BI- 0006C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 25 |  | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006C | N/A | FCU- fuel conditioning module Generator set-3 (C) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_BOOSTER PUMP A | 07 | EPS
608 | PS5-60-BI- 0006C-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 25 |  | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006C | N/A | FCU- fuel conditioning module Generator set-3 (C) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_BOOSTER PUMP B | 07 | EPS
609 | PS5-60-BI- 0006C-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006C | N/A | FCU- fuel conditioning module Generator set-3 (C) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.1_Stage 1 | 07 | EPS
610 | PS5-60-BI- 0006C-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006C | N/A | FCU- fuel conditioning module Generator set-3 (C) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.2_Stage 2 | 07 | EPS
611 | PS5-60-BI- 0006C-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006C | N/A | FCU- fuel conditioning module Generator set-3 (C) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.3 _Stage 3 | 07 | EPS
612 | PS5-60-BI- 0006C-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006C | N/A | FCU- fuel conditioning module Generator set-3 (C) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.4 _Stage 4 | 07 | EPS
613 | PS5-60-BI- 0006C-CL07 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006C | N/A | FCU- fuel conditioning module Generator set-3 (C) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.1 _Stage 1 | 07 | EPS
614 | PS5-60-BI- 0006C-CL08 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006C | N/A | FCU- fuel conditioning module Generator set-3 (C) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.2 _Stage 2 | 07 | EPS
615 | PS5-60-BI- 0006C-CL09 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006C | N/A | FCU- fuel conditioning module Generator set-3 (C) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.3_Stage 3 | 07 | EPS
616 | PS5-60-BI- 0006C-CL10 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006C | N/A | FCU- fuel conditioning module Generator set-3 (C) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.4_Stage 4 | 07 | EPS
617 | PS5-60-BI- 0006C-CL11 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006C | N/A | FCU- fuel conditioning module Generator set-3 (C) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | JB1_Space heater | 07 | EPS
618 | PS5-60-BI- 0006D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 25 |  | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006D | N/A | FCU- fuel conditioning module Generator set-4 (D) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_BOOSTER PUMP A | 07 | EPS
619 | PS5-60-BI- 0006D-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 25 |  | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006D | N/A | FCU- fuel conditioning module Generator set-4 (D) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_BOOSTER PUMP B | 07 | EPS
620 | PS5-60-BI- 0006D-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006D | N/A | FCU- fuel conditioning module Generator set-4 (D) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.1_Stage 1 | 07 | EPS
621 | PS5-60-BI- 0006D-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006D | N/A | FCU- fuel conditioning module Generator set-4 (D) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.2_Stage 2 | 07 | EPS
622 | PS5-60-BI- 0006D-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006D | N/A | FCU- fuel conditioning module Generator set-4 (D) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.3 _Stage 3 | 07 | EPS
623 | PS5-60-BI- 0006D-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006D | N/A | FCU- fuel conditioning module Generator set-4 (D) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.4 _Stage 4 | 07 | EPS
624 | PS5-60-BI- 0006D-CL07 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006D | N/A | FCU- fuel conditioning module Generator set-4 (D) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.1 _Stage 1 | 07 | EPS
625 | PS5-60-BI- 0006D-CL08 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006D | N/A | FCU- fuel conditioning module Generator set-4 (D) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.2 _Stage 2 | 07 | EPS
626 | PS5-60-BI- 0006D-CL09 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006D | N/A | FCU- fuel conditioning module Generator set-4 (D) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.3_Stage 3 | 07 | EPS
627 | PS5-60-BI- 0006D-CL10 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006D | N/A | FCU- fuel conditioning module Generator set-4 (D) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.4_Stage 4 | 07 | EPS
628 | PS5-60-BI- 0006D-CL11 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006D | N/A | FCU- fuel conditioning module Generator set-4 (D) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | JB1_Space heater | 07 | EPS
629 | PS5-60-BI- 0006E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 25 |  | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006E | N/A | FCU- fuel conditioning module Generator set-5 (E) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_BOOSTER PUMP A | 07 | EPS
630 | PS5-60-BI- 0006E-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 25 |  | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006E | N/A | FCU- fuel conditioning module Generator set-5 (E) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_BOOSTER PUMP B | 07 | EPS
631 | PS5-60-BI- 0006E-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006E | N/A | FCU- fuel conditioning module Generator set-5 (E) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.1_Stage 1 | 07 | EPS
632 | PS5-60-BI- 0006E-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006E | N/A | FCU- fuel conditioning module Generator set-5 (E) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.2_Stage 2 | 07 | EPS
633 | PS5-60-BI- 0006E-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006E | N/A | FCU- fuel conditioning module Generator set-5 (E) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.3 _Stage 3 | 07 | EPS
634 | PS5-60-BI- 0006E-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006E | N/A | FCU- fuel conditioning module Generator set-5 (E) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.4 _Stage 4 | 07 | EPS
635 | PS5-60-BI- 0006E-CL07 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006E | N/A | FCU- fuel conditioning module Generator set-5 (E) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.1 _Stage 1 | 07 | EPS
636 | PS5-60-BI- 0006E-CL08 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006E | N/A | FCU- fuel conditioning module Generator set-5 (E) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.2 _Stage 2 | 07 | EPS
637 | PS5-60-BI- 0006E-CL09 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006E | N/A | FCU- fuel conditioning module Generator set-5 (E) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.3_Stage 3 | 07 | EPS
638 | PS5-60-BI- 0006E-CL10 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006E | N/A | FCU- fuel conditioning module Generator set-5 (E) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.4_Stage 4 | 07 | EPS
639 | PS5-60-BI- 0006E-CL11 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006E | N/A | FCU- fuel conditioning module Generator set-5 (E) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | JB1_Space heater | 07 | EPS
640 | PS5-60-BI- 0006F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 25 |  | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006F | N/A | FCU- fuel conditioning module Generator set-6 (F) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_BOOSTER PUMP A | 07 | EPS
641 | PS5-60-BI- 0006F-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 25 |  | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006F | N/A | FCU- fuel conditioning module Generator set-6 (F) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_BOOSTER PUMP B | 07 | EPS
642 | PS5-60-BI- 0006F-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006F | N/A | FCU- fuel conditioning module Generator set-6 (F) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.1_Stage 1 | 07 | EPS
643 | PS5-60-BI- 0006F-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006F | N/A | FCU- fuel conditioning module Generator set-6 (F) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.2_Stage 2 | 07 | EPS
644 | PS5-60-BI- 0006F-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006F | N/A | FCU- fuel conditioning module Generator set-6 (F) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.3 _Stage 3 | 07 | EPS
645 | PS5-60-BI- 0006F-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006F | N/A | FCU- fuel conditioning module Generator set-6 (F) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.4 _Stage 4 | 07 | EPS
646 | PS5-60-BI- 0006F-CL07 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006F | N/A | FCU- fuel conditioning module Generator set-6 (F) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.1 _Stage 1 | 07 | EPS
647 | PS5-60-BI- 0006F-CL08 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006F | N/A | FCU- fuel conditioning module Generator set-6 (F) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.2 _Stage 2 | 07 | EPS
648 | PS5-60-BI- 0006F-CL09 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006F | N/A | FCU- fuel conditioning module Generator set-6 (F) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.3_Stage 3 | 07 | EPS
649 | PS5-60-BI- 0006F-CL10 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006F | N/A | FCU- fuel conditioning module Generator set-6 (F) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.4_Stage 4 | 07 | EPS
650 | PS5-60-BI- 0006F-CL11 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0006F | N/A | FCU- fuel conditioning module Generator set-6 (F) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | JB1_Space heater | 07 | EPS
651 | PS5-60-BI- 0006G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 25 |  | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006G | N/A | FCU- fuel conditioning module Generator set-7 (G) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_BOOSTER PUMP A | 07 | EPS
652 | PS5-60-BI- 0006G-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 25 |  | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006G | N/A | FCU- fuel conditioning module Generator set-7 (G) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_BOOSTER PUMP B | 07 | EPS
653 | PS5-60-BI- 0006G-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006G | N/A | FCU- fuel conditioning module Generator set-7 (G) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.1_Stage 1 | 07 | EPS
654 | PS5-60-BI- 0006G-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006G | N/A | FCU- fuel conditioning module Generator set-7 (G) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.2_Stage 2 | 07 | EPS
655 | PS5-60-BI- 0006G-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006G | N/A | FCU- fuel conditioning module Generator set-7 (G) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.3 _Stage 3 | 07 | EPS
656 | PS5-60-BI- 0006G-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006G | N/A | FCU- fuel conditioning module Generator set-7 (G) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH01.4 _Stage 4 | 07 | EPS
657 | PS5-60-BI- 0006G-CL07 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006G | N/A | FCU- fuel conditioning module Generator set-7 (G) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.1 _Stage 1 | 07 | EPS
658 | PS5-60-BI- 0006G-CL08 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006G | N/A | FCU- fuel conditioning module Generator set-7 (G) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.2 _Stage 2 | 07 | EPS
659 | PS5-60-BI- 0006G-CL09 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006G | N/A | FCU- fuel conditioning module Generator set-7 (G) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.3_Stage 3 | 07 | EPS
660 | PS5-60-BI- 0006G-CL10 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 25 |  | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006G | N/A | FCU- fuel conditioning module Generator set-7 (G) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | LV Power cable_CH02.4_Stage 4 | 07 | EPS
661 | PS5-60-BI- 0006G-CL11 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0006G | N/A | FCU- fuel conditioning module Generator set-7 (G) control junction box- Exe |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | JB1_Space heater | 07 | EPS
662 | PS5-60-BI- 0015A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 150 |  | PS5-60-IH- 0001A | C3E | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0015A | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.5 | LV Power_Generator space heater | 05 | EPS
663 | PS5-60-BI- 0015A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 150 |  | PS5-60-IH- 0001A | C2D | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0015A | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
664 | PS5-60-BI- 0015A-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 150 |  | PS5-60-IH- 0001A | C3K | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0015A | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
665 | PS5-60-BI- 0015B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 140 |  | PS5-60-IH- 0001B | C3E | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0015B | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.5 | LV Power_Generator space heater | 05 | EPS
666 | PS5-60-BI- 0015B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 140 |  | PS5-60-IH- 0001B | C2D | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0015B | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
667 | PS5-60-BI- 0015B-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 140 |  | PS5-60-IH- 0001B | C3K | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0015B | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
668 | PS5-60-BI- 0015C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 130 |  | PS5-60-IH- 0001C | C3E | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0015C | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.5 | LV Power_Generator space heater | 05 | EPS
669 | PS5-60-BI- 0015C-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-60-IH- 0001C | C2D | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0015C | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | LV Power_Drive End oil circulation pump motor_PS5 -60-DM-32900C | 05 | EPS
670 | PS5-60-BI- 0015C-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-60-IH- 0001C | C3K | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0015C | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | LV Power_Non Drive End oil circulation pump motor_PS5 -60-DM-32800C | 05 | EPS
671 | PS5-60-BI- 0015D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 120 |  | PS5-60-IH- 0001D | C3E | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0015D | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.5 | LV Power_Generator space heater | 05 | EPS
672 | PS5-60-BI- 0015D-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 120 |  | PS5-60-IH- 0001D | C2D | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0015D | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
673 | PS5-60-BI- 0015D-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 120 |  | PS5-60-IH- 0001D | C3K | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0015D | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
674 | PS5-60-BI- 0015E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 110 |  | PS5-60-IH- 0001E | C3E | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0015E | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.5 | LV Power_Generator space heater | 05 | EPS
675 | PS5-60-BI- 0015E-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 110 |  | PS5-60-IH- 0001E | C2D | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0015E | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | LV Power_Drive End oil circulation pump motor_PS5 -60-DM-32900E | 05 | EPS
676 | PS5-60-BI- 0015E-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 110 |  | PS5-60-IH- 0001E | C3K | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0015E | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | LV Power_Non Drive End oil circulation pump motor_PS5 -60-DM-32800E | 05 | EPS
677 | PS5-60-BI- 0015F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 100 |  | PS5-60-IH-0001F | C3E | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0015F | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.5 | LV Power_Generator space heater | 05 | EPS
678 | PS5-60-BI- 0015F-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 100 |  | PS5-60-IH-0001F | C2D | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0015F | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | LV Power_Drive End oil circulation pump motor_PS5 -60-DM-32900F | 05 | EPS
679 | PS5-60-BI- 0015F-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 100 |  | PS5-60-IH-0001F | C3K | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0015F | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | LV Power_Non Drive End oil circulation pump motor_PS5 -60-DM-32800F | 05 | EPS
680 | PS5-60-BI- 0015G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 90 |  | PS5-60-IH- 0001G | C3E | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0015G | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.5 | LV Power_Generator space heater | 05 | EPS
681 | PS5-60-BI- 0015G-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 90 |  | PS5-60-IH- 0001G | C2D | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0015G | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | LV Power_Drive End oil circulation pump motor_PS5 -60-DM-32900G | 05 | EPS
682 | PS5-60-BI- 0015G-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 90 |  | PS5-60-IH- 0001G | C3K | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0015G | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | LV Power_Non Drive End oil circulation pump motor_PS5 -60-DM-32800G | 05 | EPS
683 | PS5-60-BI- 0017A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0017A | N/A | FCU- fuel conditioning module Generator set-1 (A) control junction box- EX-i |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
684 | PS5-60-BI- 0017B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0017B | N/A | FCU- fuel conditioning module Generator set-2 (B) control junction box- EX-i |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | A=1 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
685 | PS5-60-BI- 0017C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0017C | N/A | FCU- fuel conditioning module Generator set-3 (C) control junction box- EX-i |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | JB2_Space heater | 07 | EPS
686 | PS5-60-BI- 0017D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0017D | N/A | FCU- fuel conditioning module Generator set-4 (D) control junction box- EX-i |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | JB2_Space heater | 07 | EPS
687 | PS5-60-BI- 0017E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0017E | N/A | FCU- fuel conditioning module Generator set-5 (E) control junction box- EX-i |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | JB2_Space heater | 07 | EPS
688 | PS5-60-BI- 0017F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI-0017F | N/A | FCU- fuel conditioning module Generator set-6 (F) control junction box- EX-i |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | JB2_Space heater | 07 | EPS
689 | PS5-60-BI- 0017G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 25 |  | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-BI- 0017G | N/A | FCU- fuel conditioning module Generator set-7 (G) control junction box- EX-i |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 17.2 | JB2_Space heater | 07 | EPS
690 | PS5-60-DD- 62800B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ | 400V AC |  | 3C+E | 2.5 | 0 |  | PS5-60-IH- 0001B | C3G | GENERATOR B AUXILIARY |  | Generator Electrical | Ind - IP | M20 | PS5-60-DD- 62800B | N/A | Eletrical barring device |  | Generator Building | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | LV power_Electrical barring | 08 | EPS
691 | PS5-60-DD- 62800D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ | 400V AC |  | 3C+E | 2.5 | 0 |  | PS5-60-IH- 0001D | C3G | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical | Ind - IP | M20 | PS5-60-DD- 62800D | N/A | Eletrical barring device |  | Generator Building | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | LV power_Electrical barring | 08 | EPS
692 | PS5-60-DD- 62800F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ | 400V AC |  | 3C+E | 2.5 | 0 |  | PS5-60-IH-0001F | C3G | GENERATOR F AUXILIARY |  | Generator Electrical | Ind - IP | M20 | PS5-60-DD- 62800F | N/A | Eletrical barring device |  | Generator Building | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | LV power_Electrical barring | 08 | EPS
693 | PS5-60-DM- 3300-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 300 |  | PS5-61-IK-0001 | A0221 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-60-DM- 3300 | N/A | Cooling Water Pump |  | Deluge skid Area | Ex'd - IP 66 | M25 / M32 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
694 | PS5-60-DM- 3400-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 310 |  | PS5-61-IK-0001 | A0319 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-60-DM- 3400 | N/A | Cooling Water Return Pump |  | Closed Drain Drum Power Gen | Ex'd - IP 66 | M25 / M32 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151118 | 21.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-08 00:00:00 | CPP-RFI-68-331-07-0255
695 | PS5-60-EA- 2900A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 40 |  | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-EA- 2900A | N/A | DIESEL OIL COOLER A |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_Diesel oil cooler | 07 | EPS
696 | PS5-60-EA- 2900B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 40 |  | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-EA- 2900B | N/A | DIESEL OIL COOLER B |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_Diesel oil cooler | 07 | EPS
697 | PS5-60-EA- 2900C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 40 |  | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-EA- 2900C | N/A | DIESEL OIL COOLER C |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_Diesel oil cooler | 07 | EPS
698 | PS5-60-EA- 2900D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 40 |  | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-EA- 2900D | N/A | DIESEL OIL COOLER D |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_Diesel oil cooler | 07 | EPS
699 | PS5-60-EA- 2900E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 40 |  | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-EA- 2900E | N/A | DIESEL OIL COOLER E |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_Diesel oil cooler | 07 | EPS
700 | PS5-60-EA- 2900F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 40 |  | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-EA- 2900F | N/A | DIESEL OIL COOLER F |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_Diesel oil cooler | 07 | EPS
701 | PS5-60-EA- 2900G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 40 |  | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-EA- 2900G | N/A | DIESEL OIL COOLER G |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 18.1 | LV Power cable_Diesel oil cooler | 07 | EPS
702 | PS5-60-IE- 0002A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | - |  | 7C | 2.5 | 50 |  | PS5-60-BI- 0015A | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0002A | N/A | Local Display Panel (LDP) for Generator Set A |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
703 | PS5-60-IE- 0002A-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 50 |  | PS5-60-BI- 0015A | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0002A | N/A | Local Display Panel (LDP) for Generator Set A |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
704 | PS5-60-IE- 0002A-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 50 |  | PS5-60-BI- 0015A | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0002A | N/A | Local Display Panel (LDP) for Generator Set A |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
705 | PS5-60-IE- 0002A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 120 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0002A | N/A | Local Display Panel (LDP) for Generator Set A |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 17.2 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
706 | PS5-60-IE- 0002A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 120 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0002A | N/A | Local Display Panel (LDP) for Generator Set A |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 17.2 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
707 | PS5-60-IE- 0002A-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 50 |  | PS5-60-BI- 0015A | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 | PS5-60-IE-0002A | N/A | Local Display Panel (LDP) for Generator Set A |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
708 | PS5-60-IE- 0002B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | - |  | 7C | 2.5 | 50 |  | PS5-60-BI- 0015B | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0002B | N/A | Local Display Panel (LDP) for Generator Set B |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
709 | PS5-60-IE- 0002B-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 50 |  | PS5-60-BI- 0015B | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0002B | N/A | Local Display Panel (LDP) for Generator Set B |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
710 | PS5-60-IE- 0002B-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 50 |  | PS5-60-BI- 0015B | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0002B | N/A | Local Display Panel (LDP) for Generator Set B |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
711 | PS5-60-IE- 0002B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 110 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0002B | N/A | Local Display Panel (LDP) for Generator Set B |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 17.2 | A=1 B=2 C=0 | 05 | EPS | 2026-06-04 00:00:00 | CPP-RFI-68-33/1-05-0309
712 | PS5-60-IE- 0002B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 110 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0002B | N/A | Local Display Panel (LDP) for Generator Set B |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 17.2 | A=1 B=2 C=0 | 05 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-05-0275
713 | PS5-60-IE- 0002B-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 50 |  | PS5-60-BI- 0015B | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 | PS5-60-IE-0002B | N/A | Local Display Panel (LDP) for Generator Set B |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
714 | PS5-60-IE- 0002C-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | - |  | 7C | 2.5 | 50 |  | PS5-60-BI-0015C | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0002C | N/A | Local Display Panel (LDP) for Generator Set C |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | Current transformer Measuring_To LDP 3 | 05 | EPS | 2026-07-02 00:00:00 | CPP-RFI-68-331-05-0399
715 | PS5-60-IE- 0002C-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 50 |  | PS5-60-BI-0015C | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0002C | N/A | Local Display Panel (LDP) for Generator Set C |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | Current transformer AVR_To LDP 3 | 05 | EPS | 2026-07-02 00:00:00 | CPP-RFI-68-331-05-0399
716 | PS5-60-IE- 0002C-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 50 |  | PS5-60-BI-0015C | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0002C | N/A | Local Display Panel (LDP) for Generator Set C |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | Generator Voltage Measuring_To LDP 3 | 05 | EPS | 2026-07-02 00:00:00 | CPP-RFI-68-331-05-0399
717 | PS5-60-IE- 0002C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 100 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0002C | N/A | Local Display Panel (LDP) for Generator Set C |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 17.2 | UPS A | 05 | EPS
718 | PS5-60-IE- 0002C-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 100 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0002C | N/A | Local Display Panel (LDP) for Generator Set C |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 17.2 | UPS B | 05 | EPS
719 | PS5-60-IE- 0002C-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 50 |  | PS5-60-BI-0015C | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 | PS5-60-IE-0002C | N/A | Local Display Panel (LDP) for Generator Set C |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | Input Power_To LDP 3 | 05 | EPS
720 | PS5-60-IE- 0002D-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | - |  | 7C | 2.5 | 50 |  | PS5-60-BI- 0015D | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE- 0002D | N/A | Local Display Panel (LDP) for Generator Set D |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | Current transformer Measuring_To LDP 4 | 05 | EPS | 2026-07-02 00:00:00 | CPP-RFI-68-331-05-0399
721 | PS5-60-IE- 0002D-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 50 |  | PS5-60-BI- 0015D | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE- 0002D | N/A | Local Display Panel (LDP) for Generator Set D |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | Current transformer AVR_To LDP 4 | 05 | EPS | 2026-07-02 00:00:00 | CPP-RFI-68-331-05-0399
722 | PS5-60-IE- 0002D-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 50 |  | PS5-60-BI- 0015D | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE- 0002D | N/A | Local Display Panel (LDP) for Generator Set D |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | Generator Voltage Measuring_To LDP 4 | 05 | EPS
723 | PS5-60-IE- 0002D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 90 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE- 0002D | N/A | Local Display Panel (LDP) for Generator Set D |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 17.2 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
724 | PS5-60-IE- 0002D-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 90 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE- 0002D | N/A | Local Display Panel (LDP) for Generator Set D |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 17.2 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
725 | PS5-60-IE- 0002D-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 50 |  | PS5-60-BI- 0015D | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 | PS5-60-IE- 0002D | N/A | Local Display Panel (LDP) for Generator Set D |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | Input Power_To LDP 4 | 05 | EPS
726 | PS5-60-IE- 0002E-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | - |  | 7C | 2.5 | 50 |  | PS5-60-BI-0015E | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0002E | N/A | Local Display Panel (LDP) for Generator Set E |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | Current transformer Measuring_To LDP 5 | 05 | EPS
727 | PS5-60-IE- 0002E-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 50 |  | PS5-60-BI-0015E | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0002E | N/A | Local Display Panel (LDP) for Generator Set E |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | Current transformer AVR_To LDP 5 | 05 | EPS
728 | PS5-60-IE- 0002E-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 50 |  | PS5-60-BI-0015E | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0002E | N/A | Local Display Panel (LDP) for Generator Set E |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | Generator Voltage Measuring_To LDP 5 | 05 | EPS
729 | PS5-60-IE- 0002E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 80 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0002E | N/A | Local Display Panel (LDP) for Generator Set E |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 17.2 | UPS A | 05 | EPS
730 | PS5-60-IE- 0002E-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 80 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0002E | N/A | Local Display Panel (LDP) for Generator Set E |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 17.2 | UPS B | 05 | EPS
731 | PS5-60-IE- 0002E-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 50 |  | PS5-60-BI-0015E | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 | PS5-60-IE-0002E | N/A | Local Display Panel (LDP) for Generator Set E |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | Input Power_To LDP 5 | 05 | EPS
732 | PS5-60-IE- 0002F-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | - |  | 7C | 2.5 | 50 |  | PS5-60-BI-0015F | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0002F | N/A | Local Display Panel (LDP) for Generator Set F |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | Current transformer Measuring_To LDP 6 | 05 | EPS
733 | PS5-60-IE- 0002F-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 50 |  | PS5-60-BI-0015F | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0002F | N/A | Local Display Panel (LDP) for Generator Set F |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | Current transformer AVR_To LDP 6 | 05 | EPS
734 | PS5-60-IE- 0002F-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 50 |  | PS5-60-BI-0015F | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0002F | N/A | Local Display Panel (LDP) for Generator Set F |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | Generator Voltage Measuring_To LDP 6 | 05 | EPS
735 | PS5-60-IE- 0002F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 70 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0002F | N/A | Local Display Panel (LDP) for Generator Set F |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 17.2 | UPS A | 05 | EPS
736 | PS5-60-IE- 0002F-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 70 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0002F | N/A | Local Display Panel (LDP) for Generator Set F |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 17.2 | UPS B | 05 | EPS
737 | PS5-60-IE- 0002F-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 50 |  | PS5-60-BI-0015F | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 | PS5-60-IE-0002F | N/A | Local Display Panel (LDP) for Generator Set F |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | Input Power_To LDP 6 | 05 | EPS
738 | PS5-60-IE- 0002G-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | - |  | 7C | 2.5 | 50 |  | PS5-60-BI- 0015G | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE- 0002G | N/A | Local Display Panel (LDP) for Generator Set G |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | Current transformer Measuring_To LDP 7 | 05 | EPS
739 | PS5-60-IE- 0002G-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 50 |  | PS5-60-BI- 0015G | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE- 0002G | N/A | Local Display Panel (LDP) for Generator Set G |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | Current transformer AVR_To LDP 7 | 05 | EPS
740 | PS5-60-IE- 0002G-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 50 |  | PS5-60-BI- 0015G | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE- 0002G | N/A | Local Display Panel (LDP) for Generator Set G |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179 | 21.6 | Generator Voltage Measuring_To LDP 7 | 05 | EPS
741 | PS5-60-IE- 0002G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 60 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE- 0002G | N/A | Local Display Panel (LDP) for Generator Set G |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 17.2 | UPS A | 05 | EPS
742 | PS5-60-IE- 0002G-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 60 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE- 0002G | N/A | Local Display Panel (LDP) for Generator Set G |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 17.2 | UPS B | 05 | EPS
743 | PS5-60-IE- 0002G-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 50 |  | PS5-60-BI- 0015G | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M20 | PS5-60-IE- 0002G | N/A | Local Display Panel (LDP) for Generator Set G |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151179 | 19.5 | Input Power_To LDP 7 | 05 | EPS
744 | PS5-60-IE- 0003A-CD01 | 0.6/1KV | CU/PVC/LSZH/G | 110V AC |  | 7C | 2.5 | 0 |  | PS5-60-BI- 0015A | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP | M25 | PS5-60-IE-0003A | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, | 21.6 | Generator Voltage Measuring_GCP A | 05 | EPS
745 | PS5-60-IE- 0003A-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 160 |  | PS5-60-BI- 0015A | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003A | N/A | Generator control panel for generator set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
746 | PS5-60-IE- 0003A-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | - |  | 7C | 2.5 | 160 |  | PS5-60-BI- 0015A | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003A | N/A | Generator control panel for generator set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | A=1 B=1 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
747 | PS5-60-IE- 0003A-CD04 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 160 |  | PS5-60-BI- 0005A | N/A | NER (A) Space Heater - Control Junction Box |  | Generator Building | Ind - IP 55 | M20 | PS5-60-IE-0003A | N/A | Generator control panel for generator set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151116, 151118, 151179 | 17.6 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
748 | PS5-60-IE- 0003A-CD05 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 160 |  | PS5-60-BI- 0015A | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003A | N/A | Generator control panel for generator set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | A=1 B=1 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
749 | PS5-60-IE- 0003A-CD06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | A03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0003A | N/A | Generator control panel for generator set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
750 | PS5-60-IE- 0003A-CD07 | 0.6/1KV | CU/XLPE/LSZH/ | - |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | A03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003A | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Current Transformer Measuring_GCP A | 08 | EPS
751 | PS5-60-IE- 0003A-CD08 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 48V DC |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | A03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0003A | N/A | Generator control panel for generator set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
752 | PS5-60-IE- 0003A-CD09 | 0.6/1KV | CU/XLPE/LSZH/ | 48V DC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | A03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003A | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Current Transformer Protection_GCP A | 08 | EPS
753 | PS5-60-IE- 0003A-CD10 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 4C+E | 4 | 0 |  | PS5-61-IJ-0001 | A03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M25 | PS5-60-IE-0003A | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | Bus Voltage Synchronizing_GCP A | 08 | EPS
754 | PS5-60-IE- 0003A-CD11 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | A03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003A | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Bus Voltage Synchronizing_GCP A | 08 | EPS
755 | PS5-60-IE- 0003A-CD12 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 110V AC |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | A03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0003A | N/A | Generator control panel for generator set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
756 | PS5-60-IE- 0003A-CD13 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | A03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003A | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Generator Voltage Synchronizing_GCP A | 08 | EPS
757 | PS5-60-IE- 0003A-CD14 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 160 |  | PS5-60-IE-0002A | N/A | Local Display Panel (LDP) for Generator Set A |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003A | N/A | Generator control panel for generator set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
758 | PS5-60-IE- 0003A-CD15 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 110V AC |  | 3C+E | 4 | 40 |  | PS5-60-IE-0004 | N/A | Master Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IE-0003A | N/A | Generator control panel for generator set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 19.5 | A=0 B=2 C=0 | 08 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
759 | PS5-60-IE- 0003A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 15 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0003A | N/A | Generator control panel for generator set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
760 | PS5-60-IE- 0003A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 20 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0003A | N/A | Generator control panel for generator set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
761 | PS5-60-IE- 0003B-CD01 | 0.6/1KV | CU/PVC/LSZH/G | 110V AC |  | 7C | 2.5 | 0 |  | PS5-60-BI- 0015B | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP | M25 | PS5-60-IE-0003B | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, | 21.6 | Generator Voltage Measuring_GCP B | 05 | EPS
762 | PS5-60-IE- 0003B-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 160 |  | PS5-60-BI- 0015B | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003B | N/A | Generator control panel for generator set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
763 | PS5-60-IE- 0003B-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | - |  | 7C | 2.5 | 160 |  | PS5-60-BI- 0015B | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003B | N/A | Generator control panel for generator set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
764 | PS5-60-IE- 0003B-CD04 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 160 |  | PS5-60-BI- 0005B | N/A | NER (B) Space Heater - Control Junction Box |  | Generator Building | Ind - IP 55 | M20 | PS5-60-IE-0003B | N/A | Generator control panel for generator set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151116, 151118, 151179 | 17.6 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
765 | PS5-60-IE- 0003B-CD05 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 160 |  | PS5-60-BI- 0015B | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003B | N/A | Generator control panel for generator set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
766 | PS5-60-IE- 0003B-CD06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | A02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0003B | N/A | Generator control panel for generator set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
767 | PS5-60-IE- 0003B-CD07 | 0.6/1KV | CU/XLPE/LSZH/ | - |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | A02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003B | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Current Transformer Measuring_GCP B | 08 | EPS
768 | PS5-60-IE- 0003B-CD08 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 48V DC |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | A02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0003B | N/A | Generator control panel for generator set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
769 | PS5-60-IE- 0003B-CD09 | 0.6/1KV | CU/XLPE/LSZH/ | 48V DC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | A02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003B | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Current Transformer Protection_GCP B | 08 | EPS
770 | PS5-60-IE- 0003B-CD10 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 4C+E | 4 | 0 |  | PS5-61-IJ-0001 | A02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M25 | PS5-60-IE-0003B | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | Bus Voltage Synchronizing_GCP B | 08 | EPS
771 | PS5-60-IE- 0003B-CD11 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | A02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003B | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Bus Voltage Synchronizing_GCP B | 08 | EPS
772 | PS5-60-IE- 0003B-CD12 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 110V AC |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | A02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0003B | N/A | Generator control panel for generator set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
773 | PS5-60-IE- 0003B-CD13 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | A02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003B | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Generator Voltage Synchronizing_GCP B | 08 | EPS
774 | PS5-60-IE- 0003B-CD14 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 150 |  | PS5-60-IE-0002B | N/A | Local Display Panel (LDP) for Generator Set B |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003B | N/A | Generator control panel for generator set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
775 | PS5-60-IE- 0003B-CD15 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 110V AC |  | 3C+E | 4 | 35 |  | PS5-60-IE-0004 | N/A | Master Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IE-0003B | N/A | Generator control panel for generator set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 19.5 | A=0 B=2 C=0 | 08 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
776 | PS5-60-IE- 0003B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 10 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0003B | N/A | Generator control panel for generator set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
777 | PS5-60-IE- 0003B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 15 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0003B | N/A | Generator control panel for generator set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
778 | PS5-60-IE- 0003C-CD01 | 0.6/1KV | CU/PVC/LSZH/G | 110V AC |  | 7C | 2.5 | 0 |  | PS5-60-BI-0015C | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP | M25 | PS5-60-IE-0003C | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, | 21.6 | Generator Voltage Measuring_GCP C | 05 | EPS
779 | PS5-60-IE- 0003C-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 160 |  | PS5-60-BI-0015C | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003C | N/A | Generator control panel for generator set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | Generator Voltage Protection_GCP C | 05 | EPS
780 | PS5-60-IE- 0003C-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | - |  | 7C | 2.5 | 160 |  | PS5-60-BI-0015C | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003C | N/A | Generator control panel for generator set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | Current Transformer Measuring_GCP C | 05 | EPS
781 | PS5-60-IE- 0003C-CD04 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 160 |  | PS5-60-BI-0005C | N/A | NER (C) Space Heater - Control Junction Box |  | Generator Building | Ind - IP 55 | M20 | PS5-60-IE-0003C | N/A | Generator control panel for generator set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151116, 151118, 151179 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
782 | PS5-60-IE- 0003C-CD05 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 160 |  | PS5-60-BI-0015C | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003C | N/A | Generator control panel for generator set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | Current Transformer Protection_GCP C | 05 | EPS
783 | PS5-60-IE- 0003C-CD06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | A01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0003C | N/A | Generator control panel for generator set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
784 | PS5-60-IE- 0003C-CD07 | 0.6/1KV | CU/XLPE/LSZH/ | - |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | A01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003C | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Current Transformer Measuring_GCP C | 08 | EPS
785 | PS5-60-IE- 0003C-CD08 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 48V DC |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | A01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0003C | N/A | Generator control panel for generator set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
786 | PS5-60-IE- 0003C-CD09 | 0.6/1KV | CU/XLPE/LSZH/ | 48V DC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | A01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003C | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Current Transformer Protection_GCP C | 08 | EPS
787 | PS5-60-IE- 0003C-CD10 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 4C+E | 4 | 0 |  | PS5-61-IJ-0001 | A01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M25 | PS5-60-IE-0003C | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | Bus Voltage Synchronizing_GCP C | 08 | EPS
788 | PS5-60-IE- 0003C-CD11 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | A01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003C | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Bus Voltage Synchronizing_GCP C | 08 | EPS
789 | PS5-60-IE- 0003C-CD12 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 110V AC |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | A01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0003C | N/A | Generator control panel for generator set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
790 | PS5-60-IE- 0003C-CD13 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | A01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003C | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Generator Voltage Synchronizing_GCP C | 08 | EPS
791 | PS5-60-IE- 0003C-CD14 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 140 |  | PS5-60-IE-0002C | N/A | Local Display Panel (LDP) for Generator Set C |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003C | N/A | Generator control panel for generator set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | Generator Voltage Measuring_From LDP 3 | 05 | EPS
792 | PS5-60-IE- 0003C-CD15 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 110V AC |  | 3C+E | 4 | 35 |  | PS5-60-IE-0004 | N/A | Master Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IE-0003C | N/A | Generator control panel for generator set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 19.5 | Bus A - Voltage Measureing To GCP C | 08 | EPS
793 | PS5-60-IE- 0003C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 15 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0003C | N/A | Generator control panel for generator set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
794 | PS5-60-IE- 0003C-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 10 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0003C | N/A | Generator control panel for generator set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 05 | EPS
795 | PS5-60-IE- 0003D-CD01 | 0.6/1KV | CU/PVC/LSZH/G | 110V AC |  | 7C | 2.5 | 0 |  | PS5-60-BI- 0015D | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP | M25 | PS5-60-IE- 0003D | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, | 21.6 | Generator Voltage Measuring_GCP D | 05 | EPS
796 | PS5-60-IE- 0003D-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 160 |  | PS5-60-BI- 0015D | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE- 0003D | N/A | Generator control panel for generator set- 4 (D) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | Generator Voltage Protection_GCP D | 05 | EPS
797 | PS5-60-IE- 0003D-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | - |  | 7C | 2.5 | 160 |  | PS5-60-BI- 0015D | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE- 0003D | N/A | Generator control panel for generator set- 4 (D) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
798 | PS5-60-IE- 0003D-CD04 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 160 |  | PS5-60-BI- 0005D | N/A | NER (D) Space Heater - Control Junction Box |  | Generator Building | Ind - IP 55 | M20 | PS5-60-IE- 0003D | N/A | Generator control panel for generator set- 4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151116, 151118, 151179 | 17.6 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
799 | PS5-60-IE- 0003D-CD05 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 160 |  | PS5-60-BI- 0015D | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE- 0003D | N/A | Generator control panel for generator set- 4 (D) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
800 | PS5-60-IE- 0003D-CD06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | B01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE- 0003D | N/A | Generator control panel for generator set- 4 (D) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
801 | PS5-60-IE- 0003D-CD07 | 0.6/1KV | CU/XLPE/LSZH/ | - |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | B01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE- 0003D | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Current Transformer Measuring_GCP D | 08 | EPS
802 | PS5-60-IE- 0003D-CD08 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 48V DC |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | B01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE- 0003D | N/A | Generator control panel for generator set- 4 (D) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
803 | PS5-60-IE- 0003D-CD09 | 0.6/1KV | CU/XLPE/LSZH/ | 48V DC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | B01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE- 0003D | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Current Transformer Protection_GCP D | 08 | EPS
804 | PS5-60-IE- 0003D-CD10 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 4C+E | 4 | 0 |  | PS5-61-IJ-0001 | B01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M25 | PS5-60-IE- 0003D | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | Bus Voltage Synchronizing_GCP D | 08 | EPS
805 | PS5-60-IE- 0003D-CD11 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | B01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE- 0003D | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Bus Voltage Synchronizing_GCP D | 08 | EPS
806 | PS5-60-IE- 0003D-CD12 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 110V AC |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | B01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE- 0003D | N/A | Generator control panel for generator set- 4 (D) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
807 | PS5-60-IE- 0003D-CD13 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | B01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE- 0003D | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Generator Voltage Synchronizing_GCP D | 08 | EPS
808 | PS5-60-IE- 0003D-CD14 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 130 |  | PS5-60-IE- 0002D | N/A | Local Display Panel (LDP) for Generator Set D |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE- 0003D | N/A | Generator control panel for generator set- 4 (D) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
809 | PS5-60-IE- 0003D-CD15 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 110V AC |  | 3C+E | 4 | 30 |  | PS5-60-IE-0004 | N/A | Master Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IE- 0003D | N/A | Generator control panel for generator set- 4 (D) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 19.5 | Bus B - Voltage Measureing To GCP D | 08 | EPS
810 | PS5-60-IE- 0003D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 10 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE- 0003D | N/A | Generator control panel for generator set- 4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
811 | PS5-60-IE- 0003D-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 15 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE- 0003D | N/A | Generator control panel for generator set- 4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
812 | PS5-60-IE- 0003E-CD01 | 0.6/1KV | CU/PVC/LSZH/G | 110V AC |  | 7C | 2.5 | 0 |  | PS5-60-BI-0015E | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP | M25 | PS5-60-IE-0003E | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, | 21.6 | Generator Voltage Measuring_GCP E | 05 | EPS
813 | PS5-60-IE- 0003E-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 160 |  | PS5-60-BI-0015E | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003E | N/A | Generator control panel for generator set- 5 (E) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | Generator Voltage Protection_GCP E | 05 | EPS
814 | PS5-60-IE- 0003E-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | - |  | 7C | 2.5 | 160 |  | PS5-60-BI-0015E | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003E | N/A | Generator control panel for generator set- 5 (E) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | Current Transformer Measuring_GCP E | 05 | EPS
815 | PS5-60-IE- 0003E-CD04 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 160 |  | PS5-60-BI-0005E | N/A | NER (E) Space Heater - Control Junction Box |  | Generator Building | Ind - IP 55 | M20 | PS5-60-IE-0003E | N/A | Generator control panel for generator set- 5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151116, 151118, 151179 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
816 | PS5-60-IE- 0003E-CD05 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 160 |  | PS5-60-BI-0015E | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003E | N/A | Generator control panel for generator set- 5 (E) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | Current Transformer Protection_GCP E | 05 | EPS
817 | PS5-60-IE- 0003E-CD06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | B02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0003E | N/A | Generator control panel for generator set- 5 (E) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=2 B=2 C=0 | 06 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0261
818 | PS5-60-IE- 0003E-CD07 | 0.6/1KV | CU/XLPE/LSZH/ | - |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | B02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003E | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Current Transformer Measuring_GCP E | 08 | EPS
819 | PS5-60-IE- 0003E-CD08 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 48V DC |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | B02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0003E | N/A | Generator control panel for generator set- 5 (E) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=2 B=2 C=0 | 06 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0261
820 | PS5-60-IE- 0003E-CD09 | 0.6/1KV | CU/XLPE/LSZH/ | 48V DC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | B02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003E | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Current Transformer Protection_GCP E | 08 | EPS
821 | PS5-60-IE- 0003E-CD10 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 4C+E | 4 | 0 |  | PS5-61-IJ-0001 | B02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M25 | PS5-60-IE-0003E | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | Bus Voltage Synchronizing_GCP E | 08 | EPS
822 | PS5-60-IE- 0003E-CD11 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | B02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003E | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Bus Voltage Synchronizing_GCP E | 08 | EPS
823 | PS5-60-IE- 0003E-CD12 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 110V AC |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | B02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0003E | N/A | Generator control panel for generator set- 5 (E) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
824 | PS5-60-IE- 0003E-CD13 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | B02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003E | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Generator Voltage Synchronizing_GCP E | 08 | EPS
825 | PS5-60-IE- 0003E-CD14 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 120 |  | PS5-60-IE-0002E | N/A | Local Display Panel (LDP) for Generator Set E |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003E | N/A | Generator control panel for generator set- 5 (E) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | Generator Voltage Measuring_From LDP 5 | 05 | EPS
826 | PS5-60-IE- 0003E-CD15 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 110V AC |  | 3C+E | 4 | 30 |  | PS5-60-IE-0004 | N/A | Master Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IE-0003E | N/A | Generator control panel for generator set- 5 (E) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 19.5 | Bus B - Voltage Measureing To GCP E | 08 | EPS
827 | PS5-60-IE- 0003E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 10 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0003E | N/A | Generator control panel for generator set- 5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
828 | PS5-60-IE- 0003E-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 15 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0003E | N/A | Generator control panel for generator set- 5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 05 | EPS
829 | PS5-60-IE- 0003F-CD01 | 0.6/1KV | CU/PVC/LSZH/G | 110V AC |  | 7C | 2.5 | 0 |  | PS5-60-BI-0015F | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP | M25 | PS5-60-IE-0003F | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151179,151116,151167 | 21.6 | Generator Voltage Measuring_GCP F | 05 | EPS
830 | PS5-60-IE- 0003F-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 160 |  | PS5-60-BI-0015F | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003F | N/A | Generator control panel for generator set- 6 (F) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151167 | 21.6 | Generator Voltage Protection_GCP F | 05 | EPS
831 | PS5-60-IE- 0003F-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | - |  | 7C | 2.5 | 160 |  | PS5-60-BI-0015F | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003F | N/A | Generator control panel for generator set- 6 (F) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151167 | 21.6 | Current Transformer Measuring_GCP F | 05 | EPS
832 | PS5-60-IE- 0003F-CD04 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 160 |  | PS5-60-BI-0005F | N/A | NER (F) Space Heater - Control Junction Box |  | Generator Building | Ind - IP 55 | M20 | PS5-60-IE-0003F | N/A | Generator control panel for generator set- 6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151116, 151118, 151179 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
833 | PS5-60-IE- 0003F-CD05 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 160 |  | PS5-60-BI-0015F | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003F | N/A | Generator control panel for generator set- 6 (F) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151167 | 21.6 | Current Transformer Protection_GCP F | 05 | EPS
834 | PS5-60-IE- 0003F-CD06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | B03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0003F | N/A | Generator control panel for generator set- 6 (F) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
835 | PS5-60-IE- 0003F-CD07 | 0.6/1KV | CU/XLPE/LSZH/ | - |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | B03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003F | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Current Transformer Measuring_GCP F | 08 | EPS
836 | PS5-60-IE- 0003F-CD08 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 48V DC |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | B03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0003F | N/A | Generator control panel for generator set- 6 (F) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
837 | PS5-60-IE- 0003F-CD09 | 0.6/1KV | CU/XLPE/LSZH/ | 48V DC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | B03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003F | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Current Transformer Protection_GCP F | 08 | EPS
838 | PS5-60-IE- 0003F-CD10 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 4C+E | 4 | 0 |  | PS5-61-IJ-0001 | B03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M25 | PS5-60-IE-0003F | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | Bus Voltage Synchronizing_GCP F | 08 | EPS
839 | PS5-60-IE- 0003F-CD11 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | B03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003F | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Bus Voltage Synchronizing_GCP F | 08 | EPS
840 | PS5-60-IE- 0003F-CD12 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 110V AC |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | B03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0003F | N/A | Generator control panel for generator set- 6 (F) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | Generator Voltage Synchronizing_GCP F | 06 | EPS
841 | PS5-60-IE- 0003F-CD13 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | B03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE-0003F | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Generator Voltage Synchronizing_GCP F | 08 | EPS
842 | PS5-60-IE- 0003F-CD14 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 110 |  | PS5-60-IE-0002F | N/A | Local Display Panel (LDP) for Generator Set F |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE-0003F | N/A | Generator control panel for generator set- 6 (F) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | Generator Voltage Measuring_From LDP 6 | 05 | EPS
843 | PS5-60-IE- 0003F-CD15 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 110V AC |  | 3C+E | 4 | 25 |  | PS5-60-IE-0004 | N/A | Master Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IE-0003F | N/A | Generator control panel for generator set- 6 (F) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 19.5 | Bus B - Voltage Measureing To GCP F | 08 | EPS
844 | PS5-60-IE- 0003F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 15 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0003F | N/A | Generator control panel for generator set- 6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
845 | PS5-60-IE- 0003F-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 20 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0003F | N/A | Generator control panel for generator set- 6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 05 | EPS
846 | PS5-60-IE- 0003G-CD01 | 0.6/1KV | CU/PVC/LSZH/G | 110V AC |  | 7C | 2.5 | 0 |  | PS5-60-BI- 0015G | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP | M25 | PS5-60-IE- 0003G | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151179,151116,151167 | 21.6 | Generator Voltage Measuring_GCP G | 05 | EPS
847 | PS5-60-IE- 0003G-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 160 |  | PS5-60-BI- 0015G | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE- 0003G | N/A | Generator control panel for GENERATOR SET- 7 (G) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151167 | 21.6 | Generator Voltage Protection_GCP G | 05 | EPS
848 | PS5-60-IE- 0003G-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | - |  | 7C | 2.5 | 160 |  | PS5-60-BI- 0015G | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE- 0003G | N/A | Generator control panel for GENERATOR SET- 7 (G) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151167 | 21.6 | Current Transformer Measuring_GCP G | 05 | EPS
849 | PS5-60-IE- 0003G-CD04 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 160 |  | PS5-60-BI- 0005G | N/A | NER (G) Space Heater - Control Junction Box |  | Generator Building | Ind - IP 55 | M20 | PS5-60-IE- 0003G | N/A | Generator control panel for GENERATOR SET- 7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151116, 151118, 151179 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
850 | PS5-60-IE- 0003G-CD05 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 7C | 2.5 | 160 |  | PS5-60-BI- 0015G | N/A | CRO Generator Space Heater - Control Terminal Box |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE- 0003G | N/A | Generator control panel for GENERATOR SET- 7 (G) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151167 | 21.6 | Current Transformer Protection_GCP G | 05 | EPS
851 | PS5-60-IE- 0003G-CD06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | B04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE- 0003G | N/A | Generator control panel for GENERATOR SET- 7 (G) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 30-May-2026 | CPP-RFI-68-33/1-07-0307
852 | PS5-60-IE- 0003G-CD07 | 0.6/1KV | CU/XLPE/LSZH/ | - |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | B04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE- 0003G | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Current Transformer Measuring_GCP G | 08 | EPS
853 | PS5-60-IE- 0003G-CD08 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 48V DC |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | B04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE- 0003G | N/A | Generator control panel for GENERATOR SET- 7 (G) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
854 | PS5-60-IE- 0003G-CD09 | 0.6/1KV | CU/XLPE/LSZH/ | 48V DC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | B04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE- 0003G | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Current Transformer Protection_GCP G | 08 | EPS
855 | PS5-60-IE- 0003G-CD10 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 4C+E | 4 | 0 |  | PS5-61-IJ-0001 | B04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M25 | PS5-60-IE- 0003G | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | Bus Voltage Synchronizing_GCP G | 08 | EPS
856 | PS5-60-IE- 0003G-CD11 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | B04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE- 0003G | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Bus Voltage Synchronizing_GCP G | 08 | EPS
857 | PS5-60-IE- 0003G-CD12 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 110V AC |  | 4C+E | 4 | 165 |  | PS5-61-IJ-0001 | B04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE- 0003G | N/A | Generator control panel for GENERATOR SET- 7 (G) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 21.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
858 | PS5-60-IE- 0003G-CD13 | 0.6/1KV | CU/XLPE/LSZH/ | 110V AC |  | 3C+E | 4 | 0 |  | PS5-61-IJ-0001 | B04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M20 | PS5-60-IE- 0003G | N/A | Generator control panel |  | Generator Electrical | Ind - IP | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | Generator Voltage Synchronizing_GCP G | 08 | EPS
859 | PS5-60-IE- 0003G-CD14 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 100 |  | PS5-60-IE- 0002G | N/A | Local Display Panel (LDP) for Generator Set G |  | Generator Building | Ind - IP 55 | M25 | PS5-60-IE- 0003G | N/A | Generator control panel for GENERATOR SET- 7 (G) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151179,151116,151118, 151167 | 21.6 | Generator VoltageMeasuring_From LDP 7 | 05 | EPS
860 | PS5-60-IE- 0003G-CD15 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 110V AC |  | 3C+E | 4 | 25 |  | PS5-60-IE-0004 | N/A | Master Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IE- 0003G | N/A | Generator control panel for GENERATOR SET- 7 (G) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 19.5 | Bus B - Voltage Measureing To GCP G | 08 | EPS
861 | PS5-60-IE- 0003G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 15 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE- 0003G | N/A | Generator control panel for GENERATOR SET- 7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
862 | PS5-60-IE- 0003G-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 20 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE- 0003G | N/A | Generator control panel for GENERATOR SET- 7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 05 | EPS
863 | PS5-60-IE-0004- CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 150 |  | PS5-61-IJ-0001 | AB01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0004 | N/A | Master Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112,151116 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
864 | PS5-60-IE-0004- CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 110V AC |  | 7C | 2.5 | 150 |  | PS5-61-IJ-0001 | AB01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-60-IE-0004 | N/A | Master Control Panel |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112,151116 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
865 | PS5-60-IE-0004- CD14 | 0.45/0.7 5 kV | CU/XLPE/ISOS/L SZH/GSWB/LSZ H | - |  | 6Pr | 0.75 | 190 |  | PS5-61-IJ-0001 | AB01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M20 | PS5-60-IE-0004 | N/A | Master Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116 | 19.5 | Buscoupler1 CB Status cable | 08 | EPS
866 | PS5-60-IE-0004- CD15 | 0.45/0.7 5 kV | CU/XLPE/ISOS/L SZH/GSWB/LSZ H | - |  | 6Pr | 0.75 | 190 |  | PS5-61-IJ-0001 | BC01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M20 | PS5-60-IE-0004 | N/A | Master Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116 | 19.5 | Buscoupler2 CB Status cable | 08 | EPS
867 | PS5-60-IE-0004- CD16 | 0.45/0.7 5 kV | CU/XLPE/ISOS/L SZH/GSWB/LSZ H | - |  | 6Pr | 0.75 | 190 |  | PS5-61-IJ-0001 | Note 16 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M20 | PS5-60-IE-0004 | N/A | Master Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116 | 19.5 | Buscoupler2 CB Status cable | 08 | EPS
868 | PS5-60-IE-0004- CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0004 | N/A | Master Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
869 | PS5-60-IE-0004- CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 35 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IE-0004 | N/A | Master Control Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
870 | PS5-60-IES- 3300-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 300 |  | PS5-61-IK-0001 | A0221 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-60-IES-3300 | N/A | Cooling Water Pump-LCS |  | Deluge skid Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
871 | PS5-60-IES- 3400-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 310 |  | PS5-61-IK-0001 | A0319 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-60-IES-3400 | N/A | Cooling Water Return Pump-LCS |  | Closed Drain Drum Power Gen | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151118 | 17.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-08 00:00:00 | CPP-RFI-68-331-07-0255
872 | PS5-60-IH- 0001A-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 240 | 45 |  | PS5-61-IK-0003 | A0201 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IH- 0001A | C1 | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 24 | PE Cable for Generator Aux. MCC-1 | 05 | Contract or
873 | PS5-60-IH- 0001A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 45 |  | PS5-61-IK-0003 | A0201 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001A | C1 | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
874 | PS5-60-IH- 0001A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 45 |  | PS5-61-IK-0003 | A0201 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001A | C1 | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
875 | PS5-60-IH- 0001A-CL03 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 45 |  | PS5-61-IK-0003 | A0201 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001A | C1 | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
876 | PS5-60-IH- 0001A-CL04 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 45 |  | PS5-61-IK-0003 | A0201 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001A | C1 | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
877 | PS5-60-IH- 0001A-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IH- 0001A | C5 | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
878 | PS5-60-IH- 0001A-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IH- 0001A | C5 | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
879 | PS5-60-IH- 0001B-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 240 | 40 |  | PS5-61-IK-0003 | A0217 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IH- 0001B | C1 | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 24 | PE Cable for Generator Aux. MCC-2 | 05 | Contract or
880 | PS5-60-IH- 0001B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 40 |  | PS5-61-IK-0003 | A0217 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001B | C1 | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
881 | PS5-60-IH- 0001B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 40 |  | PS5-61-IK-0003 | A0217 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001B | C1 | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
882 | PS5-60-IH- 0001B-CL03 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 40 |  | PS5-61-IK-0003 | A0217 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001B | C1 | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
883 | PS5-60-IH- 0001B-CL04 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 40 |  | PS5-61-IK-0003 | A0217 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001B | C1 | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
884 | PS5-60-IH- 0001B-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 35 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IH- 0001B | C5 | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
885 | PS5-60-IH- 0001B-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 35 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IH- 0001B | C5 | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
886 | PS5-60-IH- 0001C-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 240 | 40 |  | PS5-61-IK-0003 | B0301 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IH- 0001C | C1 | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 24 | PE Cable for Generator Aux. MCC-3 | 05 | Contract or
887 | PS5-60-IH- 0001C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 40 |  | PS5-61-IK-0003 | B0301 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001C | C1 | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | LV Power_Phase A | 05 | EPS
888 | PS5-60-IH- 0001C-CL02 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 40 |  | PS5-61-IK-0003 | B0301 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001C | C1 | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | LV Power_Phase B | 05 | EPS
889 | PS5-60-IH- 0001C-CL03 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 40 |  | PS5-61-IK-0003 | B0301 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001C | C1 | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | LV Power_Phase C | 05 | EPS
890 | PS5-60-IH- 0001C-CL04 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 40 |  | PS5-61-IK-0003 | B0301 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001C | C1 | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | Neutral | 05 | EPS
891 | PS5-60-IH- 0001C-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 35 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IH- 0001C | C5 | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 05 | EPS
892 | PS5-60-IH- 0001C-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 35 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IH- 0001C | C5 | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
893 | PS5-60-IH- 0001D-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 240 | 35 |  | PS5-61-IK-0003 | B0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IH- 0001D | C1 | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 24 | PE Cable for Generator Aux. MCC-D | 05 | Contract or
894 | PS5-60-IH- 0001D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 35 |  | PS5-61-IK-0003 | B0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001D | C1 | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | LV Power_Phase A | 05 | EPS
895 | PS5-60-IH- 0001D-CL02 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 35 |  | PS5-61-IK-0003 | B0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001D | C1 | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | LV Power_Phase B | 05 | EPS
896 | PS5-60-IH- 0001D-CL03 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 35 |  | PS5-61-IK-0003 | B0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001D | C1 | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | LV Power_Phase C | 05 | EPS
897 | PS5-60-IH- 0001D-CL04 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 35 |  | PS5-61-IK-0003 | B0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001D | C1 | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | Neutral | 05 | EPS
898 | PS5-60-IH- 0001D-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IH- 0001D | C5 | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
899 | PS5-60-IH- 0001D-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IH- 0001D | C5 | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
900 | PS5-60-IH- 0001E-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 240 | 35 |  | PS5-61-IK-0003 | A0301 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IH- 0001E | C1 | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 24 | PE Cable for Generator Aux. MCC-5 | 05 | Contract or
901 | PS5-60-IH- 0001E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 35 |  | PS5-61-IK-0003 | A0301 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001E | C1 | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | LV Power_Phase A | 05 | EPS
902 | PS5-60-IH- 0001E-CL02 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 35 |  | PS5-61-IK-0003 | A0301 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001E | C1 | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | LV Power_Phase B | 05 | EPS
903 | PS5-60-IH- 0001E-CL03 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 35 |  | PS5-61-IK-0003 | A0301 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001E | C1 | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | LV Power_Phase C | 05 | EPS
904 | PS5-60-IH- 0001E-CL04 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 35 |  | PS5-61-IK-0003 | A0301 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001E | C1 | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | Neutral | 05 | EPS
905 | PS5-60-IH- 0001E-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IH- 0001E | C5 | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 05 | EPS
906 | PS5-60-IH- 0001E-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IH- 0001E | C5 | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
907 | PS5-60-IH- 0001F-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 240 | 30 |  | PS5-61-IK-0003 | A0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IH-0001F | C1 | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 24 | PE Cable for Generator Aux. MCC-6 | 05 | Contract or
908 | PS5-60-IH- 0001F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 30 |  | PS5-61-IK-0003 | A0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH-0001F | C1 | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | LV Power_Phase A | 05 | EPS
909 | PS5-60-IH- 0001F-CL02 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 30 |  | PS5-61-IK-0003 | A0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH-0001F | C1 | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | LV Power_Phase B | 05 | EPS
910 | PS5-60-IH- 0001F-CL03 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 30 |  | PS5-61-IK-0003 | A0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH-0001F | C1 | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | LV Power_Phase C | 05 | EPS
911 | PS5-60-IH- 0001F-CL04 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 30 |  | PS5-61-IK-0003 | A0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH-0001F | C1 | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | Neutral | 05 | EPS
912 | PS5-60-IH- 0001F-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IH-0001F | C5 | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 05 | EPS
913 | PS5-60-IH- 0001F-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IH-0001F | C5 | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
914 | PS5-60-IH- 0001G-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 240 | 30 |  | PS5-61-IK-0003 | A0401 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IH- 0001G | C1 | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 24 | PE Cable for Generator Aux. MCC-7 | 05 | Contract or
915 | PS5-60-IH- 0001G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 30 |  | PS5-61-IK-0003 | A0401 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001G | C1 | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | LV Power_Phase A | 05 | EPS
916 | PS5-60-IH- 0001G-CL02 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 30 |  | PS5-61-IK-0003 | A0401 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001G | C1 | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | LV Power_Phase B | 05 | EPS
917 | PS5-60-IH- 0001G-CL03 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 30 |  | PS5-61-IK-0003 | A0401 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001G | C1 | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | LV Power_Phase C | 05 | EPS
918 | PS5-60-IH- 0001G-CL04 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 30 |  | PS5-61-IK-0003 | A0401 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH- 0001G | C1 | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | Neutral | 05 | EPS
919 | PS5-60-IH- 0001G-CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IH- 0001G | C5 | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
920 | PS5-60-IH- 0001G-CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IH- 0001G | C5 | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 05 | EPS
921 | PS5-60-IH-0002 -CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 240 | 25 |  | PS5-61-IK-0003 | A0417 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IH-0002 | C4 | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 24 | A=0 B=1 C=0 | 05 | Contract or | 12-June-2026 | CPP-RFI-68-33/1-07-0330
922 | PS5-60-IH-0002 -CG02 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 240 | 25 |  | PS5-61-IK-0003 | A0417 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IH-0002 | C2 | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 24 | A=0 B=1 C=0 | 05 | Contract or | 12-June-2026 | CPP-RFI-68-33/1-07-0330
923 | PS5-60-IH-0002 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 55 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IH-0002 | C6 | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
924 | PS5-60-IH-0002 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 55 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IH-0002 | C6 | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
925 | PS5-60-IH-0002 -CL03 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 25 |  | PS5-61-IK-0003 | A0417 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH-0002 | C4 | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
926 | PS5-60-IH-0002 -CL04 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 25 |  | PS5-61-IK-0003 | A0417 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH-0002 | C4 | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
927 | PS5-60-IH-0002 -CL05 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 25 |  | PS5-61-IK-0003 | A0417 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH-0002 | C4 | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
928 | PS5-60-IH-0002 -CL06 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 25 |  | PS5-61-IK-0003 | A0417 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH-0002 | C4 | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
929 | PS5-60-IH-0002 -CL07 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 25 |  | PS5-61-IK-0003 | C0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH-0002 | C2 | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
930 | PS5-60-IH-0002 -CL08 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 25 |  | PS5-61-IK-0003 | C0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH-0002 | C2 | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
931 | PS5-60-IH-0002 -CL09 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 25 |  | PS5-61-IK-0003 | C0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH-0002 | C2 | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
932 | PS5-60-IH-0002 -CL10 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 25 |  | PS5-61-IK-0003 | C0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IH-0002 | C2 | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151167 | 33.5 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
933 | PS5-60-IJ- 0001A-CH04 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 95 | 35 |  | PS5-60-GE- 8100A | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M40 | PS5-60-IJ-0001A | Note 16 | Neutral Grounding resistor for Generator set 1 (A) |  | CRO Generator Area | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 32.1 | NER | 05 | EPS | 2026-03-06 00:00:00 | CPP-RFI-68-33/1-05-168
934 | PS5-60-IJ- 0001B-CH04 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 95 | 35 |  | PS5-60-GE- 8100B | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M40 | PS5-60-IJ-0001B | Note 16 | Neutral Grounding resistor for Generator set 2 (B) |  | CRO Generator Area | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 32.1 | NER | 05 | EPS | 2026-03-06 00:00:00 | CPP-RFI-68-33/1-05-168
935 | PS5-60-IJ- 0001C-CH04 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 95 | 35 |  | PS5-60-GE- 8100C | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M40 | PS5-60-IJ-0001C | Note 16 | Neutral Grounding resistor for Generator set 3 (C) |  | CRO Generator Area | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 32.1 | NER | 05 | EPS | 2026-03-06 00:00:00 | CPP-RFI-68-33/1-05-168
936 | PS5-60-IJ- 0001D-CH04 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 95 | 35 |  | PS5-60-GE- 8100D | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M40 | PS5-60-IJ-0001D | Note 16 | Neutral Grounding resistor for Generator set 4 (D) |  | CRO Generator Area | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 32.1 | NER | 05 | EPS | 2026-03-06 00:00:00 | CPP-RFI-68-33/1-05-168
937 | PS5-60-IJ-0001E -CH04 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 95 | 35 |  | PS5-60-GE- 8100E | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M40 | PS5-60-IJ-0001E | Note 16 | Neutral Grounding resistor for Generator set 5 (E) |  | CRO Generator Area | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 32.1 | NER | 05 | EPS | 2026-03-06 00:00:00 | CPP-RFI-68-33/1-05-168
938 | PS5-60-IJ-0001F -CH04 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 95 | 35 |  | PS5-60-GE- 8100F | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M40 | PS5-60-IJ-0001F | Note 16 | Neutral Grounding resistor for Generator set 6 (F) |  | CRO Generator Area | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 32.1 | NER | 05 | EPS | 2026-03-06 00:00:00 | CPP-RFI-68-33/1-05-168
939 | PS5-60-IJ- 0001G-CH04 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 95 | 35 |  | PS5-60-GE- 8100G | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M40 | PS5-60-IJ-0001G | Note 16 | Neutral Grounding resistor for Generator set 7 (G) |  | CRO Generator Area | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 32.1 | NER | 05 | EPS | 2026-03-06 00:00:00 | CPP-RFI-68-33/1-05-0192
940 | PS5-60-IN- 0001A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 150 |  | PS5-60-IH- 0001A | C3I | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0001A | N/A | Lube oil separator genarator set-1 (A) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 19.5 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
941 | PS5-60-IN- 0001B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 140 |  | PS5-60-IH- 0001B | C3I | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0001B | N/A | Lube oil separator genarator set-2 (B) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 19.5 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
942 | PS5-60-IN- 0001C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 130 |  | PS5-60-IH- 0001C | C3I | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0001C | N/A | Lube oil separator genarator set-3 (C) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 19.5 | CRO MCC AUX Cable - MCC | 05 | EPS
943 | PS5-60-IN- 0001D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 120 |  | PS5-60-IH- 0001D | C3I | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0001D | N/A | Lube oil separator genarator set-4 (D) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 19.5 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
944 | PS5-60-IN- 0001E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 110 |  | PS5-60-IH- 0001E | C3I | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0001E | N/A | Lube oil separator genarator set-5 (E) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 19.5 | CRO MCC AUX Cable - MCC | 05 | EPS
945 | PS5-60-IN- 0001F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 100 |  | PS5-60-IH-0001F | C3I | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0001F | N/A | Lube oil separator genarator set-6 (F) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 19.5 | CRO MCC AUX Cable - MCC | 05 | EPS
946 | PS5-60-IN- 0001G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 4 | 90 |  | PS5-60-IH- 0001G | C3I | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0001G | N/A | Lube oil separator genarator set-7 (G) |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 19.5 | CRO MCC AUX Cable - MCC | 05 | EPS
947 | PS5-60-IN- 0002A-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | 400V AC |  | 1C | 25 | 150 |  | PS5-60-IH- 0001A | N/A | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18 | LV POWER TO FCU_PE CABLE | 08 | Contract or
948 | PS5-60-IN- 0002A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 50 | 150 |  | PS5-60-IH- 0001A | C2J | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151118,151116 | 32.9 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
949 | PS5-60-IN- 0002A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 10 | 150 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 22.6 | A=1 B=1 C=0 | 06 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
950 | PS5-60-IN- 0002A-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 10 | 150 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IN- 0002A | N/A | Fuel Conditioning Unit Control Panel - Generator Set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 22.6 | A=1 B=2 C=0 | 06 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
951 | PS5-60-IN- 0002B-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | 400V AC |  | 1C | 25 | 140 |  | PS5-60-IH- 0001B | N/A | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18 | LV POWER TO FCU_PE CABLE | 08 | Contract or
952 | PS5-60-IN- 0002B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 50 | 140 |  | PS5-60-IH- 0001B | C2J | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151118,151116 | 32.9 | A=1 B=2 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
953 | PS5-60-IN- 0002B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 10 | 140 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 22.6 | A=1 B=2 C=0 | 06 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
954 | PS5-60-IN- 0002B-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 10 | 140 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IN- 0002B | N/A | Fuel Conditioning Unit Control Panel - Generator Set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 22.6 | A=1 B=2 C=0 | 06 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
955 | PS5-60-IN- 0002C-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | 400V AC |  | 1C | 25 | 130 |  | PS5-60-IH- 0001C | N/A | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18 | LV POWER TO FCU_PE CABLE | 08 | Contract or
956 | PS5-60-IN- 0002C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 50 | 130 |  | PS5-60-IH- 0001C | C2J | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151118,151116 | 32.9 | LV POWER TO FCU | 05 | EPS
957 | PS5-60-IN- 0002C-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 10 | 130 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 22.6 | UPS A | 06 | EPS
958 | PS5-60-IN- 0002C-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 10 | 130 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-IN- 0002C | N/A | Fuel Conditioning Unit Control Panel - Generator Set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 22.6 | UPS B | 06 | EPS
959 | PS5-60-IN- 0002D-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | 400V AC |  | 1C | 25 | 120 |  | PS5-60-IH- 0001D | N/A | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18 | LV POWER TO FCU_PE CABLE | 08 | Contract or
960 | PS5-60-IN- 0002D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 50 | 120 |  | PS5-60-IH- 0001D | C2J | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151118,151116 | 32.9 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
961 | PS5-60-IN- 0002D-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 120 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 19.5 | A=1 B=1 C=0 | 06 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
962 | PS5-60-IN- 0002D-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 120 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0002D | N/A | Fuel Conditioning Unit Control Panel - Generator Set-4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 19.5 | A=1 B=1 C=0 | 06 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
963 | PS5-60-IN- 0002E-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | 400V AC |  | 1C | 25 | 110 |  | PS5-60-IH- 0001E | N/A | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18 | LV POWER TO FCU_PE CABLE | 08 | Contract or
964 | PS5-60-IN- 0002E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 50 | 110 |  | PS5-60-IH- 0001E | C2J | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151118,151116 | 32.9 | LV POWER TO FCU | 05 | EPS
965 | PS5-60-IN- 0002E-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 110 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 19.5 | UPS A | 06 | EPS
966 | PS5-60-IN- 0002E-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 110 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0002E | N/A | Fuel Conditioning Unit Control Panel - Generator Set-5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151118,151116, 151179 | 19.5 | UPS B | 06 | EPS
967 | PS5-60-IN- 0002F-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | 400V AC |  | 1C | 25 | 100 |  | PS5-60-IH-0001F | N/A | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18 | LV POWER TO FCU_PE CABLE | 08 | Contract or
968 | PS5-60-IN- 0002F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 50 | 100 |  | PS5-60-IH-0001F | C2J | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 32.9 | LV POWER TO FCU | 05 | EPS
969 | PS5-60-IN- 0002F-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 100 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151116,151179 | 19.5 | UPS A | 06 | EPS
970 | PS5-60-IN- 0002F-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 100 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0002F | N/A | Fuel Conditioning Unit Control Panel - Generator Set-6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151116,151179 | 19.5 | UPS B | 06 | EPS
971 | PS5-60-IN- 0002G-CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | 400V AC |  | 1C | 25 | 90 |  | PS5-60-IH- 0001G | N/A | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18 | LV POWER TO FCU_PE CABLE | 08 | Contract or
972 | PS5-60-IN- 0002G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 50 | 90 |  | PS5-60-IH- 0001G | C2J | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 32.9 | LV POWER TO FCU | 05 | EPS
973 | PS5-60-IN- 0002G-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 90 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151116,151179 | 19.5 | UPS A | 06 | EPS
974 | PS5-60-IN- 0002G-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 90 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IN- 0002G | N/A | Fuel Conditioning Unit Control Panel - Generator Set-7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167,151116,151179 | 19.5 | UPS B | 06 | EPS
975 | PS5-60-ISO- 62800A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 150 |  | PS5-60-IH- 0001A | C3K | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-ISO- 62800A | N/A | Socket For Barring Device (Gen. A & Gen. B) |  | Inside Power Gen. Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | 400V SUPPLY TO SOCKET FOR BARRING DEVICE (FOR GEN A & B ) | 08 | EPS
976 | PS5-60-ISO- 62800C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-60-IH- 0001C | C3G | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-ISO- 62800C | N/A | Socket For Barring Device (Gen. C & Gen. D) |  | Inside Power Gen. Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | 400V SUPPLY TO SOCKET FOR BARRING DEVICE (FOR GEN C & D ) | 08 | EPS
977 | PS5-60-ISO- 62800E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 110 |  | PS5-60-IH- 0001E | C3G | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-ISO- 62800E | N/A | Socket For Barring Device (Gen. E & Gen. F) |  | Inside Power Gen. Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | 400V SUPPLY TO SOCKET FOR BARRING DEVICE (FOR GEN E & F ) | 08 | EPS
978 | PS5-60-ISO- 62800G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 90 |  | PS5-60-IH- 0001G | C3G | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-ISO- 62800G | N/A | Socket For Barring Device (Gen. G) |  | Inside Power Gen. Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | 400V SUPPLY TO SOCKET FOR BARRING DEVICE (FOR GEN G ) | 08 | EPS
979 | PS5-60-IWK- 0001A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IWK- 0001A | N/A | OWS |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
980 | PS5-60-IWK- 0001A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IWK- 0001A | N/A | OWS |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 05 | EPS
981 | PS5-60-IWK- 0001B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IWK- 0001B | N/A | OWS |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
982 | PS5-60-IWK- 0001B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IWK- 0001B | N/A | OWS |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
983 | PS5-60-IWK- 0001C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IWK- 0001C | N/A | EWS |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
984 | PS5-60-IWK- 0001C-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-IWK- 0001C | N/A | EWS |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
985 | PS5-60-LA- 0002A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-LA- 0002A | N/A | VTMS 1 |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
986 | PS5-60-LA- 0002A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-LA- 0002A | N/A | VTMS 1 |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
987 | PS5-60-LA- 0002B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-LA- 0002B | N/A | VTMS 2 |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
988 | PS5-60-LA- 0002B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-LA- 0002B | N/A | VTMS 2 |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 05 | EPS
989 | PS5-60-LA- 0002C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-LA- 0002C | N/A | VTMS 3 |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
990 | PS5-60-LA- 0002C-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-LA- 0002C | N/A | VTMS 3 |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 05 | EPS
991 | PS5-60-LA-0003 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 10 | 40 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-LA-0003 | N/A | RAP |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 22.6 | A=1 B=1 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
992 | PS5-60-LA-0003 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 10 | 35 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-60-LA-0003 | N/A | RAP |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167 | 22.6 | A=1 B=1 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
993 | PS5-60-MOV- 0005-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 155 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-60-MOV- 0005 | N/A | Motor Operated Valve |  | Power generator building area | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151118 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-10 00:00:00 | CPP-RFI-68-331-05-0260
994 | PS5-60-MOV- 0006-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 170 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-60-MOV- 0006 | N/A | Motor Operated Valve |  | Power generator building area | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151118 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-10 00:00:00 | CPP-RFI-68-331-05-0260
995 | PS5-60-MOV- 0011-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 190 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-60-MOV- 0011 | N/A | Motor Operated Valve |  | Power generator building area | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151118 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-10 00:00:00 | CPP-RFI-68-331-05-0260
996 | PS5-60-MOV- 0012-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 220 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-60-MOV- 0012 | N/A | Motor Operated Valve |  | Power generator building area | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151118 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-10 00:00:00 | CPP-RFI-68-331-05-0260
997 | PS5-60-SEA- 0001-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 20 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-SEA- 0001 | N/A | FGS Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
998 | PS5-60-SEA- 0001-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 20 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-SEA- 0001 | N/A | FGS Panel |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 05 | EPS
999 | PS5-60-VS- 9100A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 150 |  | PS5-60-IH- 0001A | C3D | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-VS- 9100A | N/A | Oil Mist Eliminator- CCV |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
1000 | PS5-60-VS- 9100B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 140 |  | PS5-60-IH- 0001B | C3D | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-VS- 9100B | N/A | Oil Mist Eliminator- CCV |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
1001 | PS5-60-VS- 9100C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-60-IH- 0001C | C3D | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-VS- 9100C | N/A | Oil Mist Eliminator- CCV |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | CRO MCC AUX Cable - Oil Mist Eliminator | 05 | EPS
1002 | PS5-60-VS- 9100D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 120 |  | PS5-60-IH- 0001D | C3D | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-VS- 9100D | N/A | Oil Mist Eliminator- CCV |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
1003 | PS5-60-VS- 9100E-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 110 |  | PS5-60-IH- 0001E | C3D | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-VS- 9100E | N/A | Oil Mist Eliminator- CCV |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116 | 18.1 | CRO MCC AUX Cable - Oil Mist Eliminator | 05 | EPS
1004 | PS5-60-VS- 9100F-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 100 |  | PS5-60-IH-0001F | C3D | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-VS- 9100F | N/A | Oil Mist Eliminator- CCV |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | CRO MCC AUX Cable - Oil Mist Eliminator | 05 | EPS
1005 | PS5-60-VS- 9100G-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 90 |  | PS5-60-IH- 0001G | C3D | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-60-VS- 9100G | N/A | Oil Mist Eliminator- CCV |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 18.1 | CRO MCC AUX Cable - Oil Mist Eliminator | 05 | EPS
1006 | PS5-61-BI-0001 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 180 |  | PS5-60-IH- 0001A | C3F | GENERATOR A AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-BI-0001 | N/A | Power Transformer A Auxiliaries- Instrument Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116,151112 | 18.5 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1007 | PS5-61-BI-0002 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 170 |  | PS5-60-IH- 0001B | C3F | GENERATOR B AUXILIARY MCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-BI-0002 | N/A | Power Transformer B Auxiliaries - Instrument Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116,151112 | 18.5 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1008 | PS5-61-BI-0003 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 160 |  | PS5-60-IH- 0001C | C3F | GENERATOR C AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-BI-0003 | N/A | Power Transformer C Auxiliaries - Instrument Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151118,151116,151112 | 18.5 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1009 | PS5-61-BI-0004 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 150 |  | PS5-60-IH- 0001D | C3F | GENERATOR D AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-BI-0004 | N/A | Power Transformer D Auxiliaries - Instrument Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116,151112 | 18.5 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1010 | PS5-61-BI-0005 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 135 |  | PS5-60-IH- 0001E | C3F | GENERATOR E AUXILIARYMCC - Generator Elect.Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-BI-0005 | N/A | Power Transformer E - Auxiliaries Instrument Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116,151112 | 18.5 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1011 | PS5-61-BI-0006 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 125 |  | PS5-60-IH-0001F | C3F | GENERATOR F AUXILIARY MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-BI-0006 | N/A | Power Transformer F Auxiliaries - Instrument Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116,151112 | 18.5 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1012 | PS5-61-BI-0007 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 115 |  | PS5-60-IH- 0001G | C3F | GENERATOR G AUXILIARY MCC - Generator Electrical Building |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-BI-0007 | N/A | Power Transformer G Auxiliaries - Instrument Junction Box |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116,151112 | 18.5 | A=1 B=2 C=0 | 05 | EPS | 2026-05-10 00:00:00 | CPP-RFI-68-331-05-0260
1013 | PS5-61-IDH- 3100A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 12C | 2.5 | 170 |  | PS5-61-IJ-0001 | A09 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112,151111 | 25.3 | A=0 B=2 C=0 | 05 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0292
1014 | PS5-61-IDH- 3100A-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 170 |  | PS5-61-IE-0003 | N/A | ECS 3 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112,151111 | 17.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0292
1015 | PS5-61-IDH- 3100A-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 12C | 2.5 | 35 |  | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M25 | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151111 | 25.3 | A=0 B=2 C=0 | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0217
1016 | PS5-61-IDH- 3100A-CH01 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase A (Winding 1) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1017 | PS5-61-IDH- 3100A-CH02 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase B (Winding 1) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1018 | PS5-61-IDH- 3100A-CH03 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase C (Winding 1) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1019 | PS5-61-IDH- 3100A-CH04 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase A (Winding 2) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1020 | PS5-61-IDH- 3100A-CH05 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase B (Winding 2) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1021 | PS5-61-IDH- 3100A-CH06 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase C (Winding 2) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1022 | PS5-61-IDH- 3100A-CH07 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase A (Winding 3) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1023 | PS5-61-IDH- 3100A-CH08 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase B (Winding 3) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1024 | PS5-61-IDH- 3100A-CH09 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase C (Winding 3) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1025 | PS5-61-IDH- 3100A-CH10 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase A (Winding 4) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1026 | PS5-61-IDH- 3100A-CH11 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase B (Winding 4) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1027 | PS5-61-IDH- 3100A-CH12 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase C (Winding 4) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1028 | PS5-61-IDH- 3100A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 170 |  | PS5-06-IG- 0001A | N/A | AC UPS Distribution Board (A) Dual supply loads - 230VAC, 50Hz, 320A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112,151111 | 19.5 | A=0 B=2 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-07-0249
1029 | PS5-61-IDH- 3100B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 12C | 2.5 | 175 |  | PS5-61-IJ-0001 | B10 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112,151111 | 25.3 | A=0 B=2 C=0 | 05 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0292
1030 | PS5-61-IDH- 3100B-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 175 |  | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112,151111 | 17.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0254
1031 | PS5-61-IDH- 3100B-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 12C | 2.5 | 35 |  | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M25 | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151111 | 25.3 | A=0 B=1 C=0 | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0217
1032 | PS5-61-IDH- 3100B-CH01 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase A (Winding 1) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1033 | PS5-61-IDH- 3100B-CH02 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase B (Winding 1) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1034 | PS5-61-IDH- 3100B-CH03 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase C (Winding 1) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1035 | PS5-61-IDH- 3100B-CH04 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase A (Winding 2) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1036 | PS5-61-IDH- 3100B-CH05 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase B (Winding 2) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1037 | PS5-61-IDH- 3100B-CH06 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase C (Winding 2) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1038 | PS5-61-IDH- 3100B-CH07 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase A (Winding 3) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1039 | PS5-61-IDH- 3100B-CH08 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase B (Winding 3) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1040 | PS5-61-IDH- 3100B-CH09 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase C (Winding 3) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1041 | PS5-61-IDH- 3100B-CH10 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase A (Winding 4) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1042 | PS5-61-IDH- 3100B-CH11 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase B (Winding 4) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1043 | PS5-61-IDH- 3100B-CH12 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase C (Winding 4) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1044 | PS5-61-IDH- 3100B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 175 |  | PS5-06-IG- 0001B | N/A | AC UPS Distribution Board (B) Dual supply loads - 230VAC, 50Hz, 320A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112,151111 | 19.5 | A=0 B=3 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-07-0249
1045 | PS5-61-IDH- 3100C-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 12C | 2.5 | 180 |  | PS5-61-IJ-0001 | B11 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112,151111 | 25.3 | A=0 B=2 C=0 | 05 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0292
1046 | PS5-61-IDH- 3100C-CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 180 |  | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112,151111 | 17.6 | A=0 B=2 C=0 | 06 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0292
1047 | PS5-61-IDH- 3100C-CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 12C | 2.5 | 35 |  | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M25 | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151111 | 25.3 | A=0 B=1 C=0 | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0217
1048 | PS5-61-IDH- 3100C-CH01 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase A (Winding 1) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1049 | PS5-61-IDH- 3100C-CH02 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase B (Winding 1) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1050 | PS5-61-IDH- 3100C-CH03 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase C (Winding 1) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1051 | PS5-61-IDH- 3100C-CH04 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase A (Winding 2) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1052 | PS5-61-IDH- 3100C-CH05 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase B (Winding 2) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1053 | PS5-61-IDH- 3100C-CH06 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase C (Winding 2) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1054 | PS5-61-IDH- 3100C-CH07 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase A (Winding 3) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1055 | PS5-61-IDH- 3100C-CH08 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase B (Winding 3) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1056 | PS5-61-IDH- 3100C-CH09 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase C (Winding 3) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1057 | PS5-61-IDH- 3100C-CH10 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase A (Winding 4) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1058 | PS5-61-IDH- 3100C-CH11 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase B (Winding 4) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1059 | PS5-61-IDH- 3100C-CH12 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 1650V AC |  | 1C | 240 | 35 |  | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 39 | Phase C (Winding 4) | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1060 | PS5-61-IDH- 3100C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 180 |  | PS5-06-IG- 0001B | N/A | AC UPS Distribution Board (B) Dual supply loads - 230VAC, 50Hz, 320A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112,151111 | 19.5 | A=0 B=3 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-07-0249
1061 | PS5-61-IE-0002- CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 5C | 2.5 | 95 |  | PS5-61-IU-0010 | N/A | LLHT Oil Transformer, EACOP North , 0.696 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 3.35-1.75 Kv |  | Outdoor | Ind - IP 55 | M20 | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 19.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1062 | PS5-61-IE-0002- CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 19C | 2.5 | 95 |  | PS5-61-IU-0010 | N/A | LLHT Oil Transformer, EACOP North , 0.696 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 3.35-1.75 Kv |  | Outdoor | Ind - IP 55 | M32 | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112 | 29.7 | Status (DETC to ECS) | 05 | EPS | 2026-05-03 00:00:00 | CPP-RFI-68-331-05-0243
1063 | PS5-61-IE-0002- CD03 | 0.6/1KV | CU/XLPE/ISOS/L SZH/GSWB/LSZ H | - |  | 2Pr | 2.5 | 95 |  | PS5-61-IU-0010 | N/A | LLHT Oil Transformer, EACOP North , 0.696 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 3.35-1.75 Kv |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112 | 22 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1064 | PS5-61-IE-0002- CD04 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 5C | 2.5 | 95 |  | PS5-61-IU-0011 | N/A | LLHT Oil Transformer, EACOP South, 1.248 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 6-3.2 kV |  | Outdoor | Ind - IP 55 | M20 | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 19.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1065 | PS5-61-IE-0002- CD05 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 19C | 2.5 | 95 |  | PS5-61-IU-0011 | N/A | LLHT Oil Transformer, EACOP South, 1.248 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 6-3.2 kV |  | Outdoor | Ind - IP 55 | M32 | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112 | 29.7 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1066 | PS5-61-IE-0002- CD06 | 0.6/1KV | CU/XLPE/ISOS/L SZH/GSWB/LSZ H | - |  | 2Pr | 2.5 | 95 |  | PS5-61-IU-0011 | N/A | LLHT Oil Transformer, EACOP South, 1.248 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 6-3.2 kV |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112 | 22 | A=2 B=2 C=0 | 05 | EPS | 2026-05-09 00:00:00 | CPP-RFI-68-331-07-0268
1067 | PS5-61-IE-0002- CD41 | 0.45/0.7 5 kV | CU/XLPE/ISOS/L SZH/GSWB/LSZ H | 24V DC |  | 6Pr | 0.75 | 195 |  | PS5-60-IE- 0003D | N/A | Generator control panel for generator set- 4 (D) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | A=1 B=2 C=0 | 08 | EPS | 2026-05-24 00:00:00 | CPP-RFI-68-331-07-0296
1068 | PS5-61-IE-0002- CD42 | 0.45/0.7 5 kV | CU/XLPE/ISOS/L SZH/GSWB/LSZ H | 24V DC |  | 6Pr | 0.75 | 190 |  | PS5-60-IE-0003E | N/A | Generator control panel for generator set- 5 (E) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | A=1 B=2 C=0 | 08 | EPS | 2026-05-24 00:00:00 | CPP-RFI-68-331-07-0296
1069 | PS5-61-IE-0002- CD43 | 0.45/0.7 5 kV | CU/XLPE/ISOS/L SZH/GSWB/LSZ H | 24V DC |  | 6Pr | 0.75 | 190 |  | PS5-60-IE-0003F | N/A | Generator control panel for generator set- 6 (F) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | A=1 B=1 C=0 | 08 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0276
1070 | PS5-61-IE-0002- CD44 | 0.45/0.7 5 kV | CU/XLPE/ISOS/L SZH/GSWB/LSZ H | 24V DC |  | 6Pr | 0.75 | 190 |  | PS5-60-IE- 0003G | N/A | Generator control panel for GENERATOR SET- 7 (G) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | A=1 B=1 C=0 | 08 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0276
1071 | PS5-61-IE-0003- CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 385 |  | PS5-82-IN-0001 | N/A | MCC for Sewage Treatment Package |  | Sewage Treatment Pkge -North w | Ind - IP 55 | M20 | PS5-61-IE-0003 | N/A | ECS 3 Panelboard |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151105,151107,151108, 151111,151112 | 17.6 | A=0 B=2 C=0 | 07 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1072 | PS5-61-IE-0003- CD02 | 0.45/0.7 5 kV | CU/XLPE/ISOS/L SZH/GSWB/LSZ H | 24V DC |  | 6Pr | 0.75 | 200 |  | PS5-60-IE-0003A | N/A | Generator control panel for generator set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IE-0003 | N/A | ECS 3 Panelboard |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | A=1 B=1 C=0 | 08 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0276
1073 | PS5-61-IE-0003- CD03 | 0.45/0.7 5 kV | CU/XLPE/ISOS/L SZH/GSWB/LSZ H | 24V DC |  | 6Pr | 0.75 | 200 |  | PS5-60-IE-0003B | N/A | Generator control panel for generator set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IE-0003 | N/A | ECS 3 Panelboard |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | A=1 B=1 C=0 | 08 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0276
1074 | PS5-61-IE-0003- CD04 | 0.45/0.7 5 kV | CU/XLPE/ISOS/L SZH/GSWB/LSZ H | 24V DC |  | 6Pr | 0.75 | 195 |  | PS5-60-IE-0003C | N/A | Generator control panel for generator set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IE-0003 | N/A | ECS 3 Panelboard |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 19.5 | A=1 B=1 C=0 | 08 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0276
1075 | PS5-61-IG-0006 -CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 3C | 2.5 | 270 |  | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IG-0006 | N/A | Outdoor Normal L&SP DB - Field (South Side) |  | Export pump area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151115, 151117 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1076 | PS5-61-IG-0006 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 50 | 270 |  | PS5-61-IK-0001 | A0423 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 | PS5-61-IG-0006 | N/A | Outdoor Normal L&SP DB - Field (South Side) |  | Export pump area | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112, 151111, 151115, 151117 | 39 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1077 | PS5-61-IG-0007 -CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 3C | 2.5 | 130 |  | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IG-0007 | N/A | Outdoor Normal Lighting DB - Field - (North Side) |  | Near EDG package | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112,151111 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1078 | PS5-61-IG-0007 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 25 | 130 |  | PS5-61-IK-0001 | A0525 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-61-IG-0007 | N/A | Outdoor Normal Lighting DB - Field - (North Side) |  | Near EDG package | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112,151111 | 31.7 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1079 | PS5-61-IG- 0012A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 35 | 170 |  | PS5-61-IK-0001 | A0521 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 | PS5-61-IG- 0012A | N/A | VSD AUX. Distribution board (for VSD TAG PS5- 61-IDH-3100A) |  | VSD E house (PS5-83 -EHO-0001A) | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112,151111 | 34.5 | A=0 B=2 C=0 | 05 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0292
1080 | PS5-61-IG- 0012B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 35 | 175 |  | PS5-61-IK-0001 | A0517 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 | PS5-61-IG- 0012B | N/A | VSD AUX. Distribution board (for VSD TAG PS5- 61-IDH-3100B) |  | VSD E house (PS5-83 -EHO-0001B) | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112,151111 | 34.5 | A=0 B=2 C=0 | 05 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0292
1081 | PS5-61-IG- 0012C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 35 | 180 |  | PS5-61-IK-0001 | B0327 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 | PS5-61-IG- 0012C | N/A | VSD AUX. Distribution board (for VSD TAG PS5- 61-IDH-3100C) |  | VSD E house (PS5-83 -EHO-0001C) | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112,151111 | 34.5 | A=0 B=2 C=0 | 05 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0292
1082 | PS5-61-IG-0014 -CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 3C | 2.5 | 130 |  | PS5-61-IE-0003 | N/A | ECS 3 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IG-0014 | N/A | Outdoor Power DB - Field(North) |  | Near EITS | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151111 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 30-May-2026 | CPP-RFI-68-33/1-07-0307
1083 | PS5-61-IG-0014 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 35 | 130 |  | PS5-61-IK-0001 | A0427 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 | PS5-61-IG-0014 | N/A | Outdoor Power DB - Field(North) |  | Near EITS | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112, 151111 | 34.5 | A=0 B=2 C=0 | 05 | EPS | 30-May-2026 | CPP-RFI-68-33/1-07-0307
1084 | PS5-61-IG-0015 -CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 3C | 2.5 | 200 |  | PS5-61-IE-0003 | N/A | ECS 3 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IG-0015 | N/A | CRO Generator Building Normal L&SP Distribution Board PS-5 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 30-May-2026 | CPP-RFI-68-33/1-07-0307
1085 | PS5-61-IG-0015 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 16 | 100 |  | PS5-61-IK-0006 | A0332 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M32 | PS5-61-IG-0015 | N/A | CRO Generator Building Normal L&SP Distribution Board PS-5 |  | Generator Building | Ex'd - IP 66 | M32 |  | TZ-MID-68-WPR2- 151116 | 28.2 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
1086 | PS5-61-IG-0016 -CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 3C | 2.5 | 160 |  | PS5-61-IE-0003 | N/A | ECS 3 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IG-0016 | N/A | Generator Electrical Building Normal L&SP Distribution Board PS-5 |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151116 | 17.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-09 00:00:00 | CPP-RFI-68-331-07-0268
1087 | PS5-61-IG-0016 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 10 | 50 |  | PS5-61-IK-0006 | B0301 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M25 | PS5-61-IG-0016 | N/A | Generator Electrical Building Normal L&SP Distribution Board PS-5 |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 25.6 | A=1 B=1 C=0 | 05 | EPS | 2026-06-17 00:00:00 | CPP-RFI-68-331-05-0347
1088 | PS5-61-IG-0042 -CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 3C | 2.5 | 260 |  | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151115, 151117 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1089 | PS5-61-IG-0042 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 95 | 260 |  | PS5-61-IK-0001 | A0513 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112, 151111, 151115, 151117 | 49.5 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1090 | PS5-61-IG-0043 -CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 3C | 2.5 | 260 |  | PS5-61-IE-0002 | N/A | ECS 2 Panelboard |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112, 151111, 151115, 151117 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1091 | PS5-61-IG-0043 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 95 | 260 |  | PS5-61-IK-0001 | B0323 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112, 151111, 151115, 151117 | 49.5 | A=1 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0254
1092 | PS5-61-IH-0004 -CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 65 |  | PS5-61-IK-0006 | A0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M25 | PS5-61-IH-0004 | N/A | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 22.5 | SWGR - HVAC MCC_PE Cable_Incomer A | 06 | Contract or
1093 | PS5-61-IH-0004 -CG02 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 65 |  | PS5-61-IK-0006 | A0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M25 | PS5-61-IH-0004 | N/A | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 22.5 | SWGR - HVAC MCC_PE Cable_Incomer A | 06 | Contract or
1094 | PS5-61-IH-0004 -CG03 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 65 |  | PS5-61-IK-0006 | B0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M25 | PS5-61-IH-0004 | N/A | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 22.5 | SWGR - HVAC MCC_PE Cable_Incomer B | 06 | Contract or
1095 | PS5-61-IH-0004 -CG04 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 65 |  | PS5-61-IK-0006 | B0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M25 | PS5-61-IH-0004 | N/A | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 22.5 | SWGR - HVAC MCC_PE Cable_Incomer B | 06 | Contract or
1096 | PS5-61-IH-0004 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | A0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P1 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase A_Incomer A | 06 | EPS
1097 | PS5-61-IH-0004 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | A0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P1 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase B_Incomer A | 06 | EPS
1098 | PS5-61-IH-0004 -CL03 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | A0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P1 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase C_Incomer A | 06 | EPS
1099 | PS5-61-IH-0004 -CL04 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | A0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P1 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase A_Incomer A | 06 | EPS
1100 | PS5-61-IH-0004 -CL05 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | A0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P1 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase B_Incomer A | 06 | EPS
1101 | PS5-61-IH-0004 -CL06 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | A0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P1 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase C_Incomer A | 06 | EPS
1102 | PS5-61-IH-0004 -CL07 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | A0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P1 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase A_Incomer A | 06 | EPS
1103 | PS5-61-IH-0004 -CL08 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | A0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P1 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase B_Incomer A | 06 | EPS
1104 | PS5-61-IH-0004 -CL09 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | A0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P1 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase C_Incomer A | 06 | EPS
1105 | PS5-61-IH-0004 -CL10 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | A0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P1 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Neutral_Incomer A | 06 | EPS
1106 | PS5-61-IH-0004 -CL11 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | A0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P1 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Neutral_Incomer A | 06 | EPS
1107 | PS5-61-IH-0004 -CL12 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | B0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P2 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase A_Incomer B | 06 | EPS
1108 | PS5-61-IH-0004 -CL13 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | B0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P2 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase B_Incomer B | 06 | EPS
1109 | PS5-61-IH-0004 -CL14 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | B0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P2 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase C_Incomer B | 06 | EPS
1110 | PS5-61-IH-0004 -CL15 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | B0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P2 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase A_Incomer B | 06 | EPS
1111 | PS5-61-IH-0004 -CL16 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | B0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P2 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase B_Incomer B | 06 | EPS
1112 | PS5-61-IH-0004 -CL17 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | B0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P2 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase C_Incomer B | 06 | EPS
1113 | PS5-61-IH-0004 -CL18 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | B0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P2 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase A_Incomer B | 06 | EPS
1114 | PS5-61-IH-0004 -CL19 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | B0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P2 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase B_Incomer B | 06 | EPS
1115 | PS5-61-IH-0004 -CL20 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | B0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P2 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Phase C_Incomer B | 06 | EPS
1116 | PS5-61-IH-0004 -CL21 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | B0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P2 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Neutral_Incomer B | 06 | EPS
1117 | PS5-61-IH-0004 -CL22 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 300 | 65 |  | PS5-61-IK-0006 | B0201 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M40 | PS5-61-IH-0004 | P2 | HVAC MCC - Generator Building |  | Generator Electrical Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151116 | 35.8 | SWGR - HVAC MCC_Neutral_Incomer B | 06 | EPS
1118 | PS5-61-IJ-0001- CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 60 |  | PS5-63-IV-0010 | N/A | Earthing Transformer , 3368A, 33 kV |  | Outdoor | Ind - IP 55 | M32 | PS5-61-IJ-0001 | A08 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112 | 29.7 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1119 | PS5-61-IJ-0001- CD03 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 60 |  | PS5-63-IV-0011 | N/A | Earthing Transformer , 3368A, 33 kV |  | Outdoor | Ind - IP 55 | M32 | PS5-61-IJ-0001 | C06 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112 | 29.7 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1120 | PS5-61-IJ-0001- CD04 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 155 |  | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-61-IJ-0001 | A05 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167, 151116,151112 | 29.7 | A=1 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1121 | PS5-61-IJ-0001- CD05 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 155 |  | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-61-IJ-0001 | B06 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151167, 151116,151112 | 29.7 | A=1 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0261
1122 | PS5-61-IJ-0001- CD06 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 150 |  | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M32 | PS5-61-IJ-0001 | A06 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151116,151112 | 29.7 | A=1 B=1 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-07-0248
1123 | PS5-61-IJ-0001- CD07 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 150 |  | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M32 | PS5-61-IJ-0001 | B07 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151116,151112 | 29.7 | A=1 B=2 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-07-0247
1124 | PS5-61-IJ-0001- CD24 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 12C | 2.5 | 170 |  | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M25 | PS5-61-IJ-0001 | A09 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151111,151112 | 25.3 | A=0 B=2 C=0 | 05 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0292
1125 | PS5-61-IJ-0001- CD25 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 12C | 2.5 | 175 |  | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M25 | PS5-61-IJ-0001 | B10 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151111,151112 | 25.3 | A=0 B=2 C=0 | 05 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0292
1126 | PS5-61-IJ-0001- CD26 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 12C | 2.5 | 180 |  | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M25 | PS5-61-IJ-0001 | B11 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151111,151112 | 25.3 | A=0 B=2 C=0 | 05 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0292
1127 | PS5-61-IJ-0001- CD27 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 175 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M32 | PS5-61-IJ-0001 | A05 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151116, 151112 | 29.7 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1128 | PS5-61-IJ-0001- CD28 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 170 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M32 | PS5-61-IJ-0001 | B06 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151116, 151112 | 29.7 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1129 | PS5-61-IJ-0001- CD29 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 165 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M32 | PS5-61-IJ-0001 | A06 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151116, 151112 | 29.7 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1130 | PS5-61-IJ-0001- CD30 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 160 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M32 | PS5-61-IJ-0001 | B07 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151116, 151112 | 29.7 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1131 | PS5-61-IJ-0001- CD31 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 230 |  | PS5-61-IV- 0005A | N/A | Distribution Transformer, Office BLD 0.42kV, 1MVA, ONAN , Dyn11, 33 / 0.42 Kv |  | Outdoor | Ind - IP 55 | M32 | PS5-61-IJ-0001 | A07 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112,151109, 151106 | 29.7 | Control (Trafo - Alarm, Trip) | 04 | EPS
1132 | PS5-61-IJ-0001- CD32 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 225 |  | PS5-61-IV-0005B | N/A | Distribution Transformer, Office BLD 0.42kV, 1MVA, ONAN , Dyn11, 33 / 0.42 Kv |  | Outdoor | Ind - IP 55 | M32 | PS5-61-IJ-0001 | B08 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112,151109, 151106 | 29.7 | Control (Trafo - Alarm, Trip) | 04 | EPS
1133 | PS5-61-IJ-0001- CD33 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 55 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M32 | PS5-61-IJ-0001 | A04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112 | 29.7 | A=2 B=2 C=0 | 05 | EPS | 2026-05-08 00:00:00 | CPP-RFI-68-331-07-0255
1134 | PS5-61-IJ-0001- CD34 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 60 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M32 | PS5-61-IJ-0001 | B05 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112 | 29.7 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1135 | PS5-61-IJ-0001- CD35 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 3C | 2.5 | 95 |  | PS5-61-IU-0010 | N/A | LLHT Oil Transformer, EACOP North , 0.696 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 3.35-1.75 Kv |  | Outdoor | Ind - IP 55 | M20 | PS5-61-IJ-0001 | C04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1136 | PS5-61-IJ-0001- CD36 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 12C | 2.5 | 95 |  | PS5-61-IU-0010 | N/A | LLHT Oil Transformer, EACOP North , 0.696 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 3.35-1.75 Kv |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IJ-0001 | C04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112 | 25.3 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1137 | PS5-61-IJ-0001- CD37 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 100 |  | PS5-61-ISR-0101 | N/A | 33kV Shunt Reactor - 3.63 MVAr |  | Transformer area | Ind - IP 55 | M32 | PS5-61-IJ-0001 | C07 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112 | 29.7 | A=1 B=2 C=0 | 05 | EPS |  | CPP-RFI-68-33/1-07-0321
1138 | PS5-61-IJ-0001- CD38 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 110 |  | PS5-61-ISR-0102 | N/A | 33kV Shunt Reactor - 7.2 MVAR |  | Transformer area | Ind - IP 55 | M32 | PS5-61-IJ-0001 | B12 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112 | 29.7 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1139 | PS5-61-IJ-0001- CD39 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 5C | 2.5 | 95 |  | PS5-61-IU-0010 | N/A | LLHT Oil Transformer, EACOP North , 0.696 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 3.35-1.75 Kv |  | Outdoor | Ind - IP 55 | M20 | PS5-61-IJ-0001 | C04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 19.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1140 | PS5-61-IJ-0001- CD40 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 5C | 2.5 | 105 |  | PS5-61-IU-0011 | N/A | LLHT Oil Transformer, EACOP South, 1.248 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 6-3.2 kV |  | Outdoor | Ind - IP 55 | M20 | PS5-61-IJ-0001 | C05 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 19.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1141 | PS5-61-IJ-0001- CD41 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 12C | 2.5 | 105 |  | PS5-61-IU-0011 | N/A | LLHT Oil Transformer, EACOP South, 1.248 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 6-3.2 kV |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IJ-0001 | C05 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112 | 25.3 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1142 | PS5-61-IJ-0001- CD42 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 24V DC |  | 3C | 2.5 | 105 |  | PS5-61-IU-0011 | N/A | LLHT Oil Transformer, EACOP South, 1.248 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 6-3.2 kV |  | Outdoor | Ind - IP 55 | M20 | PS5-61-IJ-0001 | C05 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.6 | Control (Interlock from MV CB to the DETC) | 05 | EPS
1143 | PS5-61-IJ-0001- | 0.6/1KV | CU/PVC/LSZH/G | 48V DC |  | 12C | 2.5 | 0 |  | PS5-61-IU- 0001A | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP | M25 | PS5-61-IJ-0001 | A03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151112 | 25.3 | Control (Alarm & Trip) | 08 | EPS
1144 | PS5-61-IJ-0001- | 0.6/1KV | CU/PVC/LSZH/G | 48V DC |  | 12C | 2.5 | 0 |  | PS5-61-IU- 0001B | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP | M25 | PS5-61-IJ-0001 | A02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151112 | 25.3 | Control (Alarm & Trip) | 08 | EPS
1145 | PS5-61-IJ-0001- | 0.6/1KV | CU/PVC/LSZH/G | 48V DC |  | 12C | 2.5 | 0 |  | PS5-61-IU- 0001C | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP | M25 | PS5-61-IJ-0001 | A01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151112 | 25.3 | Control (Alarm & Trip) | 08 | EPS
1146 | PS5-61-IJ-0001- | 0.6/1KV | CU/PVC/LSZH/G | 48V DC |  | 12C | 2.5 | 0 |  | PS5-61-IU- 0001D | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP | M25 | PS5-61-IJ-0001 | B01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151112 | 25.3 | Control (Alarm & Trip) | 08 | EPS
1147 | PS5-61-IJ-0001- | 0.6/1KV | CU/PVC/LSZH/G | 48V DC |  | 12C | 2.5 | 0 |  | PS5-61-IU- 0001E | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP | M25 | PS5-61-IJ-0001 | B02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151112 | 25.3 | Control (Alarm & Trip) | 08 | EPS
1148 | PS5-61-IJ-0001- | 0.6/1KV | CU/PVC/LSZH/G | 48V DC |  | 12C | 2.5 | 0 |  | PS5-61-IU- 0001F | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP | M25 | PS5-61-IJ-0001 | B03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151112 | 25.3 | Control (Alarm & Trip) | 08 | EPS
1149 | PS5-61-IJ-0001- | 0.6/1KV | CU/PVC/LSZH/G | 48V DC |  | 12C | 2.5 | 0 |  | PS5-61-IU- 0001G | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP | M25 | PS5-61-IJ-0001 | B04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP | M25 |  | TZ-MID-68-WPR2- 151112 | 25.3 | Control (Alarm & Trip) | 08 | EPS
1150 | PS5-61-IJ-0001- CD61 | 0.6/1KV | CU/XLPE/OS/LSZ H/GSWB/LSZH | 48V DC |  | 12Pr | 0.75 | 200 |  | PS5-60-IE-0003A | N/A | Generator control panel for generator set-1 (A) |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-61-IJ-0001 | Note 16 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 29.8 | A=1 B=1 C=0 | 08 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0276
1151 | PS5-61-IJ-0001- CD62 | 0.6/1KV | CU/XLPE/OS/LSZ H/GSWB/LSZH | 48V DC |  | 12Pr | 0.75 | 200 |  | PS5-60-IE-0003B | N/A | Generator control panel for generator set-2 (B) |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-61-IJ-0001 | Note 16 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 29.8 | A=1 B=1 C=0 | 08 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0276
1152 | PS5-61-IJ-0001- CD63 | 0.6/1KV | CU/XLPE/OS/LSZ H/GSWB/LSZH | 48V DC |  | 12Pr | 0.75 | 200 |  | PS5-60-IE-0003C | N/A | Generator control panel for generator set-3 (C) |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-61-IJ-0001 | Note 16 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 29.8 | A=1 B=1 C=0 | 08 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0276
1153 | PS5-61-IJ-0001- CD64 | 0.6/1KV | CU/XLPE/OS/LSZ H/GSWB/LSZH | 48V DC |  | 12Pr | 0.75 | 190 |  | PS5-60-IE- 0003D | N/A | Generator control panel for generator set- 4 (D) |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-61-IJ-0001 | Note 16 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 29.8 | A=1 B=1 C=0 | 08 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0276
1154 | PS5-61-IJ-0001- CD65 | 0.6/1KV | CU/XLPE/OS/LSZ H/GSWB/LSZH | 48V DC |  | 12Pr | 0.75 | 190 |  | PS5-60-IE-0003E | N/A | Generator control panel for generator set- 5 (E) |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-61-IJ-0001 | Note 16 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 29.8 | A=1 B=1 C=0 | 08 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0276
1155 | PS5-61-IJ-0001- CD66 | 0.6/1KV | CU/XLPE/OS/LSZ H/GSWB/LSZH | 48V DC |  | 12Pr | 0.75 | 190 |  | PS5-60-IE-0003F | N/A | Generator control panel for generator set- 6 (F) |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-61-IJ-0001 | Note 16 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 29.8 | A=1 B=1 C=0 | 08 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0276
1156 | PS5-61-IJ-0001- CD67 | 0.6/1KV | CU/XLPE/OS/LSZ H/GSWB/LSZH | 48V DC |  | 12Pr | 0.75 | 190 |  | PS5-60-IE- 0003G | N/A | Generator control panel for GENERATOR SET- 7 (G) |  | Generator Electrical Building | Ind - IP 55 | M32 | PS5-61-IJ-0001 | Note 16 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112, 151116, 151167 | 29.8 | A=1 B=1 C=0 | 08 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0276
1157 | PS5-61-IJ-0001- CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 75 |  | PS5-61-IU- 0001A | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | A03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV-Phase A | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1158 | PS5-61-IJ-0001- CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 75 |  | PS5-61-IU- 0001A | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | A03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV-Phase B | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1159 | PS5-61-IJ-0001- CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 75 |  | PS5-61-IU- 0001A | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | A03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV-Phase C | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1160 | PS5-61-IJ-0001- CH04 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 70 |  | PS5-61-IU- 0001B | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | A02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase A | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1161 | PS5-61-IJ-0001- CH05 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 70 |  | PS5-61-IU- 0001B | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | A02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase B | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1162 | PS5-61-IJ-0001- CH06 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 70 |  | PS5-61-IU- 0001B | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | A02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase C | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1163 | PS5-61-IJ-0001- CH07 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 60 |  | PS5-61-IU- 0001C | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | A01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase A | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1164 | PS5-61-IJ-0001- CH08 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 60 |  | PS5-61-IU- 0001C | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | A01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase B | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1165 | PS5-61-IJ-0001- CH09 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 60 |  | PS5-61-IU- 0001C | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | A01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase C | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1166 | PS5-61-IJ-0001- CH10 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 55 |  | PS5-61-IU- 0001D | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | B01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase A | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1167 | PS5-61-IJ-0001- CH11 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 55 |  | PS5-61-IU- 0001D | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | B01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase B | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1168 | PS5-61-IJ-0001- CH12 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 55 |  | PS5-61-IU- 0001D | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | B01 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase C | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1169 | PS5-61-IJ-0001- CH13 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 55 |  | PS5-61-IU- 0001E | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | B02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase A | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1170 | PS5-61-IJ-0001- CH14 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 55 |  | PS5-61-IU- 0001E | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | B02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase B | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1171 | PS5-61-IJ-0001- CH15 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 55 |  | PS5-61-IU- 0001E | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | B02 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase C | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1172 | PS5-61-IJ-0001- CH16 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 60 |  | PS5-61-IU- 0001F | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | B03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase A | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1173 | PS5-61-IJ-0001- CH17 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 60 |  | PS5-61-IU- 0001F | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | B03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase B | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1174 | PS5-61-IJ-0001- CH18 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 60 |  | PS5-61-IU- 0001F | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | B03 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase C | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1175 | PS5-61-IJ-0001- CH19 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 65 |  | PS5-61-IU- 0001G | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | B04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase A | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1176 | PS5-61-IJ-0001- CH20 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 65 |  | PS5-61-IU- 0001G | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | B04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase B | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1177 | PS5-61-IJ-0001- CH21 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 65 |  | PS5-61-IU- 0001G | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 | PS5-61-IJ-0001 | B04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase C | 05 | EPS | 2026-03-31 00:00:00 | CPP-RFI-68-33/1-05-0196
1178 | PS5-61-IJ-0001- CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 2C+E | 2.5 | 60 |  | PS5-63-NER- 0010 | N/A | NER for Earthing Transformer (PS5-63-IV- 0010) |  | EITS Building (Outdoors) | Ind - IP 55 | M20 | PS5-61-IJ-0001 | A08 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1179 | PS5-61-IJ-0001- CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 2C+E | 2.5 | 60 |  | PS5-63-NER- 0011 | N/A | NER for Earthing Transformer (PS5-63-IV- 0011) |  | EITS Building (Outdoors) | Ind - IP 55 | M20 | PS5-61-IJ-0001 | C06 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1180 | PS5-61-IJ-0010- CH01 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 5550V AC |  | 1C | 95 | 90 |  | PS5-61-IU-0010 | N/A | LLHT Oil Transformer, EACOP North , 0.696 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 3.35-1.75 Kv |  | Outdoor |  |  | PS5-61-IJ-0010 | A01 | SM6 LLHT 7.2 kV MV Switchgear, 630A, 16kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112 | 30.1 | Phase A | 05 | EPS | 2026-03-02 00:00:00 | CPP-RFI-68-33/1-05-0198
1181 | PS5-61-IJ-0010- CH02 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 5550V AC |  | 1C | 95 | 90 |  | PS5-61-IU-0010 | N/A | LLHT Oil Transformer, EACOP North , 0.696 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 3.35-1.75 Kv |  | Outdoor |  |  | PS5-61-IJ-0010 | A01 | SM6 LLHT 7.2 kV MV Switchgear, 630A, 16kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112 | 30.1 | Phase B | 05 | EPS | 2026-03-02 00:00:00 | CPP-RFI-68-33/1-05-0198
1182 | PS5-61-IJ-0010- CH03 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 5550V AC |  | 1C | 95 | 90 |  | PS5-61-IU-0010 | N/A | LLHT Oil Transformer, EACOP North , 0.696 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 3.35-1.75 Kv |  | Outdoor |  |  | PS5-61-IJ-0010 | A01 | SM6 LLHT 7.2 kV MV Switchgear, 630A, 16kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112 | 30.1 | Phase C | 05 | EPS | 2026-03-02 00:00:00 | CPP-RFI-68-33/1-05-0198
1183 | PS5-61-IJ-0010- CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 2C+E | 2.5 | 95 |  | PS5-61-NER- 0010 | N/A | NER of LLHT Transformer 0.696MVA, Dyn11, 33/1.75-3.35kV |  | Outside EITS | Ind - IP 55 | M20 | PS5-61-IJ-0010 | A01 | SM6 LLHT 7.2 kV MV Switchgear, 630A, 16kA/3s |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1184 | PS5-61-IJ-0011- CH01 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 5550V AC |  | 1C | 95 | 100 |  | PS5-61-IU-0011 | N/A | LLHT Oil Transformer, EACOP South, 1.248 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 6-3.2 kV |  | Outdoor |  |  | PS5-61-IJ-0011 | A01 | SM6 LLHT 7.2 kV MV Switchgear, 630A, 16kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112 | 30.1 | Phase A | 05 | EPS | 2026-03-02 00:00:00 | CPP-RFI-68-33/1-05-0198
1185 | PS5-61-IJ-0011- CH02 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 5550V AC |  | 1C | 95 | 100 |  | PS5-61-IU-0011 | N/A | LLHT Oil Transformer, EACOP South, 1.248 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 6-3.2 kV |  | Outdoor |  |  | PS5-61-IJ-0011 | A01 | SM6 LLHT 7.2 kV MV Switchgear, 630A, 16kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112 | 30.1 | Phase B | 05 | EPS | 2026-03-02 00:00:00 | CPP-RFI-68-33/1-05-0198
1186 | PS5-61-IJ-0011- CH03 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 5550V AC |  | 1C | 95 | 100 |  | PS5-61-IU-0011 | N/A | LLHT Oil Transformer, EACOP South, 1.248 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 6-3.2 kV |  | Outdoor |  |  | PS5-61-IJ-0011 | A01 | SM6 LLHT 7.2 kV MV Switchgear, 630A, 16kA/3s |  | EITS Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112 | 30.1 | Phase C | 05 | EPS | 2026-03-02 00:00:00 | CPP-RFI-68-33/1-05-0198
1187 | PS5-61-IJ-0011- CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 2C+E | 2.5 | 105 |  | PS5-61-NER- 0011 | N/A | NER of LLHT Transformer 1.247MVA, Dyn11, 33/3.2-6kV |  | Outside EITS | Ind - IP 55 | M20 | PS5-61-IJ-0011 | A01 | SM6 LLHT 7.2 kV MV Switchgear, 630A, 16kA/3s |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1188 | PS5-61-IK-0001- CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112 | 22.5 | A=2 B=2 C=0 | 05 | Contract or | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0240
1189 | PS5-61-IK-0001- CG02 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112 | 22.5 | A=2 B=2 C=0 | 05 | Contract or | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1190 | PS5-61-IK-0001- CG03 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112 | 22.5 | A=2 B=2 C=0 | 05 | Contract or | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1191 | PS5-61-IK-0001- CG04 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151112 | 22.5 | A=2 B=2 C=0 | 05 | Contract or | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1192 | PS5-61-IK-0001- CL01 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1193 | PS5-61-IK-0001- CL02 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1194 | PS5-61-IK-0001- CL03 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1195 | PS5-61-IK-0001- CL04 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1196 | PS5-61-IK-0001- CL05 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1197 | PS5-61-IK-0001- CL06 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1198 | PS5-61-IK-0001- CL07 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1199 | PS5-61-IK-0001- CL08 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1200 | PS5-61-IK-0001- CL09 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1201 | PS5-61-IK-0001- CL10 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1202 | PS5-61-IK-0001- CL11 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1203 | PS5-61-IK-0001- CL12 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1204 | PS5-61-IK-0001- CL13 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1205 | PS5-61-IK-0001- CL14 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1206 | PS5-61-IK-0001- CL15 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1207 | PS5-61-IK-0001- CL16 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1208 | PS5-61-IK-0001- CL17 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1209 | PS5-61-IK-0001- CL18 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0257
1210 | PS5-61-IK-0001- CL19 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0251
1211 | PS5-61-IK-0001- CL20 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0251
1212 | PS5-61-IK-0001- CL21 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0251
1213 | PS5-61-IK-0001- CL22 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0251
1214 | PS5-61-IK-0001- CL23 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0251
1215 | PS5-61-IK-0001- CL24 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0251
1216 | PS5-61-IK-0001- CL25 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0251
1217 | PS5-61-IK-0001- CL26 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0251
1218 | PS5-61-IK-0001- CL27 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0251
1219 | PS5-61-IK-0001- CL28 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0251
1220 | PS5-61-IK-0001- CL29 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0251
1221 | PS5-61-IK-0001- CL30 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-331-07-0251
1222 | PS5-61-IK-0001- CL31 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1223 | PS5-61-IK-0001- CL32 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1224 | PS5-61-IK-0001- CL33 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-08 00:00:00 | CPP-RFI-68-331-07-0255
1225 | PS5-61-IK-0001- CL34 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-08 00:00:00 | CPP-RFI-68-331-07-0255
1226 | PS5-61-IK-0001- CL35 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-09 00:00:00 | CPP-RFI-68-331-07-0268
1227 | PS5-61-IK-0001- CL36 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-09 00:00:00 | CPP-RFI-68-331-07-0268
1228 | PS5-61-IK-0001- CL37 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 150 |  | PS5-61-IK-0003 | C0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-61-IK-0001 | C01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112,151116 | 33.5 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1229 | PS5-61-IK-0001- CL38 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 150 |  | PS5-61-IK-0003 | C0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-61-IK-0001 | C01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112,151116 | 33.5 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1230 | PS5-61-IK-0001- CL39 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 150 |  | PS5-61-IK-0003 | C0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-61-IK-0001 | C01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112,151116 | 33.5 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1231 | PS5-61-IK-0001- CL40 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 150 |  | PS5-61-IK-0003 | C0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-61-IK-0001 | C01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112,151116 | 33.5 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1232 | PS5-61-IK-0001- CL41 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 150 |  | PS5-61-IK-0003 | C0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-61-IK-0001 | C01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112,151116 | 33.5 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1233 | PS5-61-IK-0001- CL42 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 150 |  | PS5-61-IK-0003 | C0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-61-IK-0001 | C01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112,151116 | 33.5 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1234 | PS5-61-IK-0001- CL43 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 240 | 150 |  | PS5-61-IK-0003 | C0317 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M40 | PS5-61-IK-0001 | C01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112,151116 | 33.5 | A=0 B=2 C=0 | 05 | EPS | 2026-05-16 00:00:00 | CPP-RFI-68-33/1-07-0271
1235 | PS5-61-IK-0001- CL44 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 2C+E | 2.5 | 45 |  | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M20 | PS5-61-IK-0001 | A01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=1 B=2 C=0 | 05 | EPS | 2026-05-13 00:00:00 | CPP-RFI-68-331-07-0267
1236 | PS5-61-IK-0001- CL45 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 2C+E | 2.5 | 45 |  | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M20 | PS5-61-IK-0001 | B01 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-08 00:00:00 | CPP-RFI-68-331-07-0255
1237 | PS5-61-IK-0003- CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 35 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 22.5 | PE Cable | 05 | Contract or
1238 | PS5-61-IK-0003- CG02 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 35 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 22.5 | PE Cable | 05 | Contract or
1239 | PS5-61-IK-0003- CG03 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 35 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 22.5 | PE Cable | 05 | Contract or
1240 | PS5-61-IK-0003- CG04 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 22.5 | PE Cable | 05 | Contract or
1241 | PS5-61-IK-0003- CG05 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 22.5 | PE Cable | 05 | Contract or
1242 | PS5-61-IK-0003- CG06 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 22.5 | PE Cable | 05 | Contract or
1243 | PS5-61-IK-0003- CG07 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 240 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M25 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 24 | A=1 B=2 C=0 | 05 | Contract or | 2026-04-24 00:00:00 | CPP-RFI-68-331-05-0225
1244 | PS5-61-IK-0003- CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 55 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IK-0003 | B04 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 19.5 | A=0 B=2 C=0 | 06 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
1245 | PS5-61-IK-0003- CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 55 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IK-0003 | B04 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 19.5 | A=0 B=2 C=0 | 06 | EPS | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0368
1246 | PS5-61-IK-0003- CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 65 |  | PS5-61-IG-0016 | N/A | Generator Electrical Building Normal L&SP Distribution Board PS-5 |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
1247 | PS5-61-IK-0003- CL05 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 65 |  | PS5-61-IG-0016 | N/A | Generator Electrical Building Normal L&SP Distribution Board PS-5 |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=1 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
1248 | PS5-61-IK-0003- CL06 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 65 |  | PS5-61-IG-0016 | N/A | Generator Electrical Building Normal L&SP Distribution Board PS-5 |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
1249 | PS5-61-IK-0003- CL07 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1250 | PS5-61-IK-0003- CL08 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1251 | PS5-61-IK-0003- CL09 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1252 | PS5-61-IK-0003- CL10 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1253 | PS5-61-IK-0003- CL11 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1254 | PS5-61-IK-0003- CL12 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1255 | PS5-61-IK-0003- CL13 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1256 | PS5-61-IK-0003- CL14 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1257 | PS5-61-IK-0003- CL15 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1258 | PS5-61-IK-0003- CL16 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1259 | PS5-61-IK-0003- CL17 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1260 | PS5-61-IK-0003- CL18 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1261 | PS5-61-IK-0003- CL19 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1262 | PS5-61-IK-0003- CL20 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1263 | PS5-61-IK-0003- CL21 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1264 | PS5-61-IK-0003- CL22 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1265 | PS5-61-IK-0003- CL23 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1266 | PS5-61-IK-0003- CL24 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1267 | PS5-61-IK-0003- CL25 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1268 | PS5-61-IK-0003- CL26 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1269 | PS5-61-IK-0003- CL27 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1270 | PS5-61-IK-0003- CL28 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1271 | PS5-61-IK-0003- CL29 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1272 | PS5-61-IK-0003- CL30 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1273 | PS5-61-IK-0003- CL31 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1274 | PS5-61-IK-0003- CL32 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1275 | PS5-61-IK-0003- CL33 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1276 | PS5-61-IK-0003- CL34 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1277 | PS5-61-IK-0003- CL35 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1278 | PS5-61-IK-0003- CL36 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1279 | PS5-61-IK-0003- CL37 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-05-0250
1280 | PS5-61-IK-0003- CL38 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-05-0250
1281 | PS5-61-IK-0003- CL39 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-05-0250
1282 | PS5-61-IK-0003- CL40 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-05-0250
1283 | PS5-61-IK-0003- CL41 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1284 | PS5-61-IK-0003- CL42 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 40 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1285 | PS5-61-IK-0003- CL43 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-05-0250
1286 | PS5-61-IK-0003- CL44 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
1287 | PS5-61-IK-0003- CL45 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-05-0250
1288 | PS5-61-IK-0003- CL46 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-05-0250
1289 | PS5-61-IK-0003- CL47 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-05-0250
1290 | PS5-61-IK-0003- CL48 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-05-0250
1291 | PS5-61-IK-0003- CL49 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-05-0250
1292 | PS5-61-IK-0003- CL50 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-05-0250
1293 | PS5-61-IK-0003- CL51 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-05-0250
1294 | PS5-61-IK-0003- CL52 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-05-0250
1295 | PS5-61-IK-0003- CL53 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-05-0250
1296 | PS5-61-IK-0003- CL54 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-05-0250
1297 | PS5-61-IK-0003- CL55 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-04-30 00:00:00 | CPP-RFI-68-331-05-0238
1298 | PS5-61-IK-0003- CL56 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-04-30 00:00:00 | CPP-RFI-68-331-05-0238
1299 | PS5-61-IK-0003- CL57 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
1300 | PS5-61-IK-0003- CL58 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
1301 | PS5-61-IK-0003- CL59 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
1302 | PS5-61-IK-0003- CL60 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 200 |  | PS5-05-BE-0001 | N/A | EDG Power JB |  | Near EDG | Ind - IP 55 | M50 | PS5-61-IK-0003 | C01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111, 151112, 151116 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-331-05-0215
1303 | PS5-61-IK-0003- CL61 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 2C+E | 2.5 | 35 |  | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M20 | PS5-61-IK-0003 | A01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | Neutral CT to the LV incomer | 05 | EPS | 2026-06-04 00:00:00 | CPP-RFI-68-331-07-0310
1304 | PS5-61-IK-0003- CL62 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 2C+E | 2.5 | 30 |  | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M20 | PS5-61-IK-0003 | B01 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
1305 | PS5-61-IK-0005- CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 220 |  | PS5-61-IJ-0001 | A07 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 | PS5-61-IK-0005 | A01 | 0.4kV Switchboard |  | Office & Facilities Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112,151109,151106 | 29.7 | Control (Bi-directional Inter- trip / Bi-directional permissive close inerlock) | 05 | EPS
1306 | PS5-61-IK-0005- CD02 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 19C | 2.5 | 220 |  | PS5-61-IJ-0001 | B08 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M32 | PS5-61-IK-0005 | A01 | 0.4kV Switchboard |  | Office & Facilities Building | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112,151109,151106 | 29.7 | Control (Bi-directional Inter- trip / Bi-directional permissive close inerlock) | 05 | EPS
1307 | PS5-61-IK-0005- CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 150 | 260 |  | PS5-61-IK-0003 | C0223 | 0.4kV Switchboard |  | Generator Electrical Building | Ind - IP 55 | M63 | PS5-61-IK-0005 | C01 | 0.4kV Switchboard |  | Office & Facilities Building | Ind - IP 55 | M63 |  | TZ-MID-68-WPR2- 151167, 151116,151112,151109, 151106 | 61.3 | LV Power_Emergency section | 07 | EPS
1308 | PS5-61-IK-0006- CG01 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 22.5 | PE Cable | 05 | Contract or
1309 | PS5-61-IK-0006- CG02 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 22.5 | PE Cable | 05 | Contract or
1310 | PS5-61-IK-0006- CG03 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 22.5 | PE Cable | 05 | Contract or
1311 | PS5-61-IK-0006- CG04 | 0.45/0.7 5 kV | Stranded Cu , PVC G-Y Sheathed | - |  | 1C | 185 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M25 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 22.5 | PE Cable | 05 | Contract or
1312 | PS5-61-IK-0006- CL01 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1313 | PS5-61-IK-0006- CL02 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1314 | PS5-61-IK-0006- CL03 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1315 | PS5-61-IK-0006- CL04 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1316 | PS5-61-IK-0006- CL05 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1317 | PS5-61-IK-0006- CL06 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1318 | PS5-61-IK-0006- CL07 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1319 | PS5-61-IK-0006- CL08 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1320 | PS5-61-IK-0006- CL09 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=3 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1321 | PS5-61-IK-0006- CL10 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1322 | PS5-61-IK-0006- CL11 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1323 | PS5-61-IK-0006- CL12 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1324 | PS5-61-IK-0006- CL13 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1325 | PS5-61-IK-0006- CL14 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1326 | PS5-61-IK-0006- CL15 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1327 | PS5-61-IK-0006- CL16 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1328 | PS5-61-IK-0006- CL17 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1329 | PS5-61-IK-0006- CL18 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1330 | PS5-61-IK-0006- CL19 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-04-24 00:00:00 | CPP-RFI-68-331-05-0225
1331 | PS5-61-IK-0006- CL20 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-04-24 00:00:00 | CPP-RFI-68-331-05-0225
1332 | PS5-61-IK-0006- CL21 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-04-24 00:00:00 | CPP-RFI-68-331-05-0225
1333 | PS5-61-IK-0006- CL22 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=1 B=2 C=0 | 05 | EPS | 2026-04-24 00:00:00 | CPP-RFI-68-331-05-0225
1334 | PS5-61-IK-0006- CL23 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1335 | PS5-61-IK-0006- CL24 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1336 | PS5-61-IK-0006- CL25 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1337 | PS5-61-IK-0006- CL26 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-12 00:00:00 | CPP-RFI-68-331-05-0264
1338 | PS5-61-IK-0006- CL27 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-12 00:00:00 | CPP-RFI-68-331-05-0264
1339 | PS5-61-IK-0006- CL28 | 0.6/1KV | CU/XLPE/LSZH/ AWA/LSZH | 400V AC |  | 1C | 500 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M50 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 44.6 | A=2 B=2 C=0 | 05 | EPS | 2026-05-12 00:00:00 | CPP-RFI-68-331-05-0264
1340 | PS5-61-IK-0006- CL29 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 60 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IK-0006 | B02 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | PS5-61-IK-0006_BUS A - UPS A | 05 | EPS
1341 | PS5-61-IK-0006- CL30 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 60 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IK-0006 | B02 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | PS5-61-IK-0006_BUS B - UPS B | 05 | EPS
1342 | PS5-61-IK-0006- CL31 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 70 |  | PS5-61-IG-0016 | N/A | Generator Electrical Building Normal L&SP Distribution Board PS-5 |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | PS5-61-IK-0006_BUS A - Normal Aux | 05 | EPS
1343 | PS5-61-IK-0006- CL32 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 70 |  | PS5-61-IG-0016 | N/A | Generator Electrical Building Normal L&SP Distribution Board PS-5 |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | PS5-61-IK-0006_BUS B - Normal Aux | 05 | EPS
1344 | PS5-61-IK-0006- CL33 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 2C+E | 2.5 | 30 |  | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M20 | PS5-61-IK-0006 | A01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-05-0244
1345 | PS5-61-IK-0006- CL34 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | - |  | 2C+E | 2.5 | 35 |  | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M20 | PS5-61-IK-0006 | B01 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-05-0244
1346 | PS5-61-ISR- 0101-CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 110 |  | PS5-61-IJ-0001 | C07 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-ISR-0101 | N/A | 33kV Shunt Reactor - 3.63 MVAr |  | Transformer area |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | Phase A | 05 | EPS | 2026-03-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1347 | PS5-61-ISR- 0101-CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 110 |  | PS5-61-IJ-0001 | C07 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-ISR-0101 | N/A | 33kV Shunt Reactor - 3.63 MVAr |  | Transformer area |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | Phase B | 05 | EPS | 2026-03-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1348 | PS5-61-ISR- 0101-CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 110 |  | PS5-61-IJ-0001 | C07 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-ISR-0101 | N/A | 33kV Shunt Reactor - 3.63 MVAr |  | Transformer area |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | Phase C | 05 | EPS | 2026-03-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1349 | PS5-61-ISR- 0101-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 110 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-61-ISR-0101 | N/A | 33kV Shunt Reactor - 3.63 MVAr |  | Transformer area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0254
1350 | PS5-61-ISR- 0102-CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 240 | 120 |  | PS5-61-IJ-0001 | B12 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M63 | PS5-61-ISR-0102 | N/A | 33kV Shunt Reactor - 7.2 MVAR |  | Transformer area |  |  |  | TZ-MID-68-WPR2- 151112 | 52.4 | Phase A | 05 | EPS | 2026-03-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1351 | PS5-61-ISR- 0102-CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 240 | 120 |  | PS5-61-IJ-0001 | B12 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M63 | PS5-61-ISR-0102 | N/A | 33kV Shunt Reactor - 7.2 MVAR |  | Transformer area |  |  |  | TZ-MID-68-WPR2- 151112 | 52.4 | Phase B | 05 | EPS | 2026-03-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1352 | PS5-61-ISR- 0102-CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 240 | 120 |  | PS5-61-IJ-0001 | B12 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M63 | PS5-61-ISR-0102 | N/A | 33kV Shunt Reactor - 7.2 MVAR |  | Transformer area |  |  |  | TZ-MID-68-WPR2- 151112 | 52.4 | Phase C | 05 | EPS | 2026-03-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1353 | PS5-61-ISR- 0102-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 120 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-61-ISR-0102 | N/A | 33kV Shunt Reactor - 7.2 MVAR |  | Transformer area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0254
1354 | PS5-61-IU- 0001A-CH01 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 210 |  | PS5-60-GE- 8100A | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001A | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase A | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1355 | PS5-61-IU- 0001A-CH02 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 210 |  | PS5-60-GE- 8100A | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001A | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase B | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1356 | PS5-61-IU- 0001A-CH03 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 210 |  | PS5-60-GE- 8100A | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001A | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase C | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1357 | PS5-61-IU- 0001B-CH01 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 210 |  | PS5-60-GE- 8100B | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001B | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase A | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1358 | PS5-61-IU- 0001B-CH02 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 210 |  | PS5-60-GE- 8100B | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001B | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase B | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1359 | PS5-61-IU- 0001B-CH03 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 210 |  | PS5-60-GE- 8100B | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001B | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase C | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1360 | PS5-61-IU- 0001C-CH01 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 200 |  | PS5-60-GE- 8100C | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001C | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase A | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1361 | PS5-61-IU- 0001C-CH02 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 200 |  | PS5-60-GE- 8100C | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001C | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase B | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1362 | PS5-61-IU- 0001C-CH03 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 200 |  | PS5-60-GE- 8100C | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001C | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase C | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1363 | PS5-61-IU- 0001D-CH01 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 185 |  | PS5-60-GE- 8100D | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001D | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase A | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1364 | PS5-61-IU- 0001D-CH02 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 185 |  | PS5-60-GE- 8100D | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001D | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase B | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1365 | PS5-61-IU- 0001D-CH03 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 185 |  | PS5-60-GE- 8100D | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001D | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase C | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1366 | PS5-61-IU- 0001E-CH01 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 175 |  | PS5-60-GE- 8100E | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001E | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase A | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1367 | PS5-61-IU- 0001E-CH02 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 175 |  | PS5-60-GE- 8100E | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001E | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase B | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1368 | PS5-61-IU- 0001E-CH03 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 175 |  | PS5-60-GE- 8100E | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001E | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase C | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1369 | PS5-61-IU- 0001F-CH01 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 165 |  | PS5-60-GE- 8100F | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001F | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase A | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1370 | PS5-61-IU- 0001F-CH02 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 165 |  | PS5-60-GE- 8100F | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001F | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase B | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1371 | PS5-61-IU- 0001F-CH03 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 165 |  | PS5-60-GE- 8100F | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001F | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase C | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1372 | PS5-61-IU- 0001G-CH01 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 155 |  | PS5-60-GE- 8100G | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001G | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase A | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1373 | PS5-61-IU- 0001G-CH02 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 155 |  | PS5-60-GE- 8100G | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001G | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase B | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1374 | PS5-61-IU- 0001G-CH03 | 6/10 (12) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 11000V AC |  | 1C | 300 | 155 |  | PS5-60-GE- 8100G | N/A | Power Generator |  | Power generator building area | Ind - IP 55 | M50 | PS5-61-IU- 0001G | N/A | 11/33kV Transformer - 6.8 MVA |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116,151112 | 43.1 | HV - Phase C | 05 | EPS | 2026-02-20 00:00:00 | CPP-RFI-68-33/1-05-161
1375 | PS5-61-IU-0010 -CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 95 |  | PS5-61-IJ-0001 | C04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IU-0010 | N/A | LLHT Oil Transformer, EACOP North , 0.696 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 3.35-1.75 Kv |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase A | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1376 | PS5-61-IU-0010 -CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 95 |  | PS5-61-IJ-0001 | C04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IU-0010 | N/A | LLHT Oil Transformer, EACOP North , 0.696 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 3.35-1.75 Kv |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase B | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1377 | PS5-61-IU-0010 -CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 95 |  | PS5-61-IJ-0001 | C04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IU-0010 | N/A | LLHT Oil Transformer, EACOP North , 0.696 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 3.35-1.75 Kv |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase C | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1378 | PS5-61-IU-0010 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 100 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IU-0010 | N/A | LLHT Oil Transformer, EACOP North , 0.696 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 3.35-1.75 Kv |  | Outdoor | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0254
1379 | PS5-61-IU-0010 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 2.5 | 100 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IU-0010 | N/A | LLHT Oil Transformer, EACOP North , 0.696 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 3.35-1.75 Kv |  | Outdoor | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 19.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0256
1380 | PS5-61-IU-0011 -CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 105 |  | PS5-61-IJ-0001 | C05 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IU-0011 | N/A | LLHT Oil Transformer, EACOP South, 1.248 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 6-3.2 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase A | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1381 | PS5-61-IU-0011 -CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 105 |  | PS5-61-IJ-0001 | C05 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IU-0011 | N/A | LLHT Oil Transformer, EACOP South, 1.248 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 6-3.2 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase B | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1382 | PS5-61-IU-0011 -CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 105 |  | PS5-61-IJ-0001 | C05 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IU-0011 | N/A | LLHT Oil Transformer, EACOP South, 1.248 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 6-3.2 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase C | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1383 | PS5-61-IU-0011 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 110 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IU-0011 | N/A | LLHT Oil Transformer, EACOP South, 1.248 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 6-3.2 kV |  | Outdoor | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0254
1384 | PS5-61-IU-0011 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 2.5 | 110 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IU-0011 | N/A | LLHT Oil Transformer, EACOP South, 1.248 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 6-3.2 kV |  | Outdoor | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 19.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0254
1385 | PS5-61-IU- 3100A-CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 165 |  | PS5-61-IJ-0001 | A09 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111,151112 | 43.7 | HV - Phase A | 05 | EPS | 2026-03-18 00:00:00 | CPP-RFI-68-33/1-05-181
1386 | PS5-61-IU- 3100A-CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 165 |  | PS5-61-IJ-0001 | A09 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111,151112 | 43.7 | HV - Phase B | 05 | EPS | 2026-03-18 00:00:00 | CPP-RFI-68-33/1-05-181
1387 | PS5-61-IU- 3100A-CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 165 |  | PS5-61-IJ-0001 | A09 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111,151112 | 43.7 | HV - Phase C | 05 | EPS | 2026-03-18 00:00:00 | CPP-RFI-68-33/1-05-181
1388 | PS5-61-IU- 3100A-CH04 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/GSWA/FRL S PVC | 1650V AC |  | 3C | 50 | 35 |  | PS5-61-IV- 0006A | N/A | Pre-Magnetisation Transformer - VSD Package |  | VSD Package | Ind - IP 55 | M50 | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 49.8 | HV - Pre Mag Trafo cable | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1389 | PS5-61-IU- 3100A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 35 |  | PS5-61-IDH- 3100A | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 | PS5-61-IU- 3100A | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151111 | 17.2 | Space Heater - VFD Trafo Marshalling Box | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0217
1390 | PS5-61-IU- 3100B-CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 175 |  | PS5-61-IJ-0001 | B10 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111,151112 | 43.7 | HV - Phase A | 05 | EPS | 2026-03-18 00:00:00 | CPP-RFI-68-33/1-05-181
1391 | PS5-61-IU- 3100B-CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 175 |  | PS5-61-IJ-0001 | B10 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111,151112 | 43.7 | HV - Phase B | 05 | EPS | 2026-03-18 00:00:00 | CPP-RFI-68-33/1-05-181
1392 | PS5-61-IU- 3100B-CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 175 |  | PS5-61-IJ-0001 | B10 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111,151112 | 43.7 | HV - Phase C | 05 | EPS | 2026-03-18 00:00:00 | CPP-RFI-68-33/1-05-181
1393 | PS5-61-IU- 3100B-CH04 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/GSWA/FRL S PVC | 1650V AC |  | 3C | 50 | 35 |  | PS5-61-IV-0006B | N/A | Pre-Magnetisation Transformer - VSD Package |  | VSD Package | Ind - IP 55 | M50 | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 49.8 | HV - Pre Mag Trafo cable | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1394 | PS5-61-IU- 3100B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 35 |  | PS5-61-IDH- 3100B | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 | PS5-61-IU- 3100B | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151111 | 17.2 | Space Heater - VFD Trafo Marshalling Box | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0217
1395 | PS5-61-IU- 3100C-CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 185 |  | PS5-61-IJ-0001 | B11 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111,151112 | 43.7 | HV - Phase A | 05 | EPS | 2026-03-18 00:00:00 | CPP-RFI-68-33/1-05-181
1396 | PS5-61-IU- 3100C-CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 185 |  | PS5-61-IJ-0001 | B11 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111,151112 | 43.7 | HV - Phase B | 05 | EPS | 2026-03-18 00:00:00 | CPP-RFI-68-33/1-05-181
1397 | PS5-61-IU- 3100C-CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 185 |  | PS5-61-IJ-0001 | B11 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111,151112 | 43.7 | HV - Phase C | 05 | EPS | 2026-03-18 00:00:00 | CPP-RFI-68-33/1-05-181
1398 | PS5-61-IU- 3100C-CH04 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/GSWA/FRL S PVC | 1650V AC |  | 3C | 50 | 35 |  | PS5-61-IV-0006C | N/A | Pre-Magnetisation Transformer - VSD Package |  | VSD Package | Ind - IP 55 | M50 | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151111 | 49.8 | HV - Pre Mag Trafo cable | 05 | EPS | 2026-03-28 00:00:00 | CPP-RFI-68-33/1-05-0192
1399 | PS5-61-IU- 3100C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 35 |  | PS5-61-IDH- 3100C | N/A | Variable Speed Drive - Export Pump |  | VSD E-house | Ind - IP 55 | M20 | PS5-61-IU- 3100C | N/A | 33kV VSD Transformer |  | VSD Pre-Fabricated E house | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151111 | 17.2 | Space Heater - VFD Trafo Marshalling Box | 05 | EPS | 2026-04-15 00:00:00 | CPP-RFI-68-33/1-05-0217
1400 | PS5-61-IV- 0001A-CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 75 |  | PS5-61-IJ-0001 | A04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase A | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1401 | PS5-61-IV- 0001A-CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 75 |  | PS5-61-IJ-0001 | A04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase B | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1402 | PS5-61-IV- 0001A-CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 75 |  | PS5-61-IJ-0001 | A04 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase C | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1403 | PS5-61-IV- 0001A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 75 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IV- 0001A | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0265
1404 | PS5-61-IV- 0001B-CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 80 |  | PS5-61-IJ-0001 | B05 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase A | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1405 | PS5-61-IV- 0001B-CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 80 |  | PS5-61-IJ-0001 | B05 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase B | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1406 | PS5-61-IV- 0001B-CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 80 |  | PS5-61-IJ-0001 | B05 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | HV - Phase C | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1407 | PS5-61-IV- 0001B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 80 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-61-IV-0001B | N/A | Distribution Transformer, Main LV MCC 0.42kV, 2.5MVA, ONAN, Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0265
1408 | PS5-61-IV- 0002A-CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 175 |  | PS5-61-IJ-0001 | A05 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151116 | 43.7 | A=0 B=1 C=0 | 05 | EPS | 2026-03-22 00:00:00 | CPP-RFI-68-33/1-05-0184
1409 | PS5-61-IV- 0002A-CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 175 |  | PS5-61-IJ-0001 | A05 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151116 | 43.7 | A=1 B=0 C=0 | 05 | EPS | 2026-03-22 00:00:00 | CPP-RFI-68-33/1-05-0184
1410 | PS5-61-IV- 0002A-CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 175 |  | PS5-61-IJ-0001 | A05 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151116 | 43.7 | A=0 B=0 C=1 | 05 | EPS | 2026-03-22 00:00:00 | CPP-RFI-68-33/1-05-0184
1411 | PS5-61-IV- 0002A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 55 |  | PS5-61-IG-0016 | N/A | Generator Electrical Building Normal L&SP Distribution Board PS-5 |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IV- 0002A | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
1412 | PS5-61-IV- 0002B-CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 170 |  | PS5-61-IJ-0001 | B06 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151116 | 43.7 | A=0 B=1 C=0 | 05 | EPS | 2026-03-22 00:00:00 | CPP-RFI-68-33/1-05-0184
1413 | PS5-61-IV- 0002B-CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 170 |  | PS5-61-IJ-0001 | B06 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151116 | 43.7 | A=0 B=1 C=0 | 05 | EPS | 2026-03-22 00:00:00 | CPP-RFI-68-33/1-05-0184
1414 | PS5-61-IV- 0002B-CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 170 |  | PS5-61-IJ-0001 | B06 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151116 | 43.7 | A=0 B=1 C=0 | 05 | EPS | 2026-03-22 00:00:00 | CPP-RFI-68-33/1-05-0184
1415 | PS5-61-IV- 0002B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 60 |  | PS5-61-IG-0016 | N/A | Generator Electrical Building Normal L&SP Distribution Board PS-5 |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IV-0002B | N/A | Distribution Transformer, Power generator BLD 0.42kV, 2.5MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
1416 | PS5-61-IV- 0005A-CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 230 |  | PS5-61-IJ-0001 | A07 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV- 0005A | N/A | Distribution Transformer, Office BLD 0.42kV, 1MVA, ONAN , Dyn11, 33 / 0.42 Kv |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151120,151106 | 43.7 | HV - Phase A | 05 | EPS
1417 | PS5-61-IV- 0005A-CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 230 |  | PS5-61-IJ-0001 | A07 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV- 0005A | N/A | Distribution Transformer, Office BLD 0.42kV, 1MVA, ONAN , Dyn11, 33 / 0.42 Kv |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151120,151106 | 43.7 | HV - Phase B | 05 | EPS
1418 | PS5-61-IV- 0005A-CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 230 |  | PS5-61-IJ-0001 | A07 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV- 0005A | N/A | Distribution Transformer, Office BLD 0.42kV, 1MVA, ONAN , Dyn11, 33 / 0.42 Kv |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151120,151106 | 43.7 | HV - Phase C | 05 | EPS
1419 | PS5-61-IV- 0005B-CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 235 |  | PS5-61-IJ-0001 | B08 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV-0005B | N/A | Distribution Transformer, Office BLD 0.42kV, 1MVA, ONAN , Dyn11, 33 / 0.42 Kv |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151120,151106 | 43.7 | HV - Phase A | 05 | EPS
1420 | PS5-61-IV- 0005B-CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 235 |  | PS5-61-IJ-0001 | B08 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV-0005B | N/A | Distribution Transformer, Office BLD 0.42kV, 1MVA, ONAN , Dyn11, 33 / 0.42 Kv |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151120,151106 | 43.7 | HV - Phase B | 05 | EPS
1421 | PS5-61-IV- 0005B-CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 235 |  | PS5-61-IJ-0001 | B08 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV-0005B | N/A | Distribution Transformer, Office BLD 0.42kV, 1MVA, ONAN , Dyn11, 33 / 0.42 Kv |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151120,151106 | 43.7 | HV - Phase C | 05 | EPS
1422 | PS5-61-IV- 0006A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 35 | 170 |  | PS5-61-IK-0001 | A0613 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-61-IV- 0006A | N/A | Pre-Magnetisation Transformer - VSD Package |  | VSD Package | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112,151111 | 29.3 | A=0 B=2 C=0 | 05 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0292
1423 | PS5-61-IV- 0006B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 35 | 175 |  | PS5-61-IK-0001 | A0609 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-61-IV-0006B | N/A | Pre-Magnetisation Transformer - VSD Package |  | VSD Package | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112,151111 | 29.3 | A=0 B=2 C=0 | 05 | EPS | 2026-05-14 00:00:00 | CPP-RFI-68-33/1-07-0265
1424 | PS5-61-IV- 0006C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 35 | 180 |  | PS5-61-IK-0001 | B0217 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-61-IV-0006C | N/A | Pre-Magnetisation Transformer - VSD Package |  | VSD Package | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112,151111 | 29.3 | A=0 B=2 C=0 | 05 | EPS | 2026-05-19 00:00:00 | CPP-RFI-68-331-07-0292
1425 | PS5-61-IV- 0007A-CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 170 |  | PS5-61-IJ-0001 | A06 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151116 | 43.7 | A=0 B=1 C=0 | 05 | EPS | 2026-03-22 00:00:00 | CPP-RFI-68-33/1-05-0184
1426 | PS5-61-IV- 0007A-CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 170 |  | PS5-61-IJ-0001 | A06 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151116 | 43.7 | A=0 B=1 C=0 | 05 | EPS | 2026-03-22 00:00:00 | CPP-RFI-68-33/1-05-0184
1427 | PS5-61-IV- 0007A-CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 170 |  | PS5-61-IJ-0001 | A06 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151116 | 43.7 | A=0 B=1 C=0 | 05 | EPS | 2026-03-22 00:00:00 | CPP-RFI-68-33/1-05-0184
1428 | PS5-61-IV- 0007A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 65 |  | PS5-61-IG-0016 | N/A | Generator Electrical Building Normal L&SP Distribution Board PS-5 |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IV- 0007A | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1429 | PS5-61-IV- 0007B-CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 165 |  | PS5-61-IJ-0001 | B07 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151116 | 43.7 | A=0 B=1 C=0 | 05 | EPS | 2026-03-22 00:00:00 | CPP-RFI-68-33/1-05-0184
1430 | PS5-61-IV- 0007B-CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 165 |  | PS5-61-IJ-0001 | B07 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151116 | 43.7 | A=0 B=1 C=0 | 05 | EPS | 2026-03-22 00:00:00 | CPP-RFI-68-33/1-05-0184
1431 | PS5-61-IV- 0007B-CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 165 |  | PS5-61-IJ-0001 | B07 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112,151116 | 43.7 | A=0 B=1 C=0 | 05 | EPS | 2026-03-22 00:00:00 | CPP-RFI-68-33/1-05-0184
1432 | PS5-61-IV- 0007B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 70 |  | PS5-61-IG-0016 | N/A | Generator Electrical Building Normal L&SP Distribution Board PS-5 |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-61-IV-0007B | N/A | Distribution Transformer, New Power generator BLD 0.42kV, 2MVA, ONAN , Dyn11, 33 / 0.42 kV |  | Outdoor | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151116 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-01 00:00:00 | CPP-RFI-68-331-05-0228
1433 | PS5-61-NER- 0010-CH01 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 5550V AC |  | 1C | 95 | 20 |  | PS5-61-IU-0010 | N/A | LLHT Oil Transformer, EACOP North , 0.696 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 3.35-1.75 Kv |  | Outdoor |  |  | PS5-61-NER- 0010 | N/A | NER of LLHT Transformer 0.696MVA, Dyn11, 33/1.75-3.35kV |  | Outside EITS | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112 | 30.1 | A=2 B=1 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-05-0244
1434 | PS5-61-NER- 0010-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 85 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-61-NER- 0010 | N/A | NER of LLHT Transformer 0.696MVA, Dyn11, 33/1.75-3.35kV |  | Outside EITS | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-08 00:00:00 | CPP-RFI-68-331-07-0255
1435 | PS5-61-NER- 0011-CH01 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 5550V AC |  | 1C | 95 | 20 |  | PS5-61-IU-0011 | N/A | LLHT Oil Transformer, EACOP South, 1.248 MVA, ONAN, Motorised, DETC, CAPT, 9 steps, 33 / 6-3.2 kV |  | Outdoor |  |  | PS5-61-NER- 0011 | N/A | NER of LLHT Transformer 1.247MVA, Dyn11, 33/3.2-6kV |  | Outside EITS | Ind - IP 55 | M32 |  | TZ-MID-68-WPR2- 151112 | 30.1 | A=2 B=1 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-05-0244
1436 | PS5-61-NER- 0011-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 85 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-61-NER- 0011 | N/A | NER of LLHT Transformer 1.247MVA, Dyn11, 33/3.2-6kV |  | Outside EITS | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-08 00:00:00 | CPP-RFI-68-331-07-0255
1437 | PS5-62-IE-0001- CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 230V AC |  | 3C | 2.5 | 175 |  | PS5-62-IE-0002 | N/A | Lighting Control panel 2 - Pump Station 5 |  | Near EDG package | Ind - IP 55 | M20 | PS5-62-IE-0001 | N/A | Lighting Control panel 1 - Pump Station 5 |  | Near Export pump area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151111,151115,151117 | 17.6 | A=1 B=1 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-331-05-0226
1438 | PS5-62-IE-0001- CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 10 |  | PS5-05-IG-0006 | N/A | Outdoor Emergency Lighting DB - Field - (North Side) |  | Near EDG package | Ind - IP 55 | M20 | PS5-62-IE-0001 | N/A | Lighting Control panel 1 - Pump Station 5 |  | Near Export pump area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151111 | 17.2 | A=1 B=1 C=0 | 06 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-331-05-0226
1439 | PS5-62-IE-0002- CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 230V AC |  | 3C | 2.5 | 120 |  | PS5-08-15CB- 1001 | N/A | TELECOM SII SP3 SEC Cabinet |  | EITS Building | Ind - IP 55 | M20 | PS5-62-IE-0002 | N/A | Lighting Control panel 2 - Pump Station 5 |  | Near EDG package | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112,151111 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 30-May-2026 | CPP-RFI-68-33/1-07-0307
1440 | PS5-62-IE-0002- CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 10 |  | PS5-05-IG-0004 | N/A | Outdoor Emergency Lighting DB - Field - (South Side) |  | Near Export pump area | Ind - IP 55 | M20 | PS5-62-IE-0002 | N/A | Lighting Control panel 2 - Pump Station 5 |  | Near EDG package | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151117 | 17.2 | A=1 B=2 C=0 | 06 | EPS | 2026-05-13 00:00:00 | CPP-RFI-68-331-05-0266
1441 | PS5-63-IV-0010 -CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 60 |  | PS5-61-IJ-0001 | A08 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-63-IV-0010 | N/A | Earthing Transformer , 3368A, 33 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | Phase A | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1442 | PS5-63-IV-0010 -CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 60 |  | PS5-61-IJ-0001 | A08 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-63-IV-0010 | N/A | Earthing Transformer , 3368A, 33 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | Phase B | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1443 | PS5-63-IV-0010 -CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 60 |  | PS5-61-IJ-0001 | A08 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-63-IV-0010 | N/A | Earthing Transformer , 3368A, 33 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | Phase C | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1444 | PS5-63-IV-0010 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 65 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-63-IV-0010 | N/A | Earthing Transformer , 3368A, 33 kV |  | Outdoor | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-08 00:00:00 | CPP-RFI-68-331-07-0255
1445 | PS5-63-IV-0011 -CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 60 |  | PS5-61-IJ-0001 | C06 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-63-IV-0011 | N/A | Earthing Transformer , 3368A, 33 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | Phase A | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1446 | PS5-63-IV-0011 -CH02 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 60 |  | PS5-61-IJ-0001 | C06 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-63-IV-0011 | N/A | Earthing Transformer , 3368A, 33 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | Phase B | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1447 | PS5-63-IV-0011 -CH03 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 33000V AC |  | 1C | 95 | 60 |  | PS5-61-IJ-0001 | C06 | CBGS-0 33kV MV Switchgear, 1250A, IAC AFLR 25kA/3s |  | EITS Building | Ind - IP 55 | M50 | PS5-63-IV-0011 | N/A | Earthing Transformer , 3368A, 33 kV |  | Outdoor |  |  |  | TZ-MID-68-WPR2- 151112 | 43.7 | Phase C | 05 | EPS | 2026-04-02 00:00:00 | CPP-RFI-68-33/1-05-0197
1448 | PS5-63-IV-0011 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 65 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-63-IV-0011 | N/A | Earthing Transformer , 3368A, 33 kV |  | Outdoor | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-08 00:00:00 | CPP-RFI-68-331-07-0255
1449 | PS5-63-NER- 0010-CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | _ |  | 1C | 95 | 10 |  | PS5-63-IV-0010 | N/A | Earthing Transformer , 3368A, 33 kV |  | Outdoor |  |  | PS5-63-NER- 0010 | N/A | NER for Earthing Transformer (PS5-63-IV- 0010) |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | A=2 B=1 C=0 | 05 | EPS | 2026-04-11 00:00:00 | CPP-RFI-68-331-05-0210
1450 | PS5-63-NER- 0010-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 85 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-63-NER- 0010 | N/A | NER for Earthing Transformer (PS5-63-IV- 0010) |  | EITS Building (Outdoors) | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-08 00:00:00 | CPP-RFI-68-331-07-0255
1451 | PS5-63-NER- 0011-CH01 | 18/30 (36) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | _ |  | 1C | 95 | 10 |  | PS5-63-IV-0011 | N/A | Earthing Transformer , 3368A, 33 kV |  | Outdoor |  |  | PS5-63-NER- 0011 | N/A | NER for Earthing Transformer (PS5-63-IV- 0011) |  | EITS Building (Outdoors) | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 43.7 | A=2 B=1 C=0 | 05 | EPS | 2026-04-11 00:00:00 | CPP-RFI-68-331-05-0210
1452 | PS5-63-NER- 0011-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 85 |  | PS5-61-IG-0008 | N/A | Normal Auxiliary Distribution Panel - 3Ph 400 Inc, 1Ph 230VAC Outgoings, 160A, 50KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-63-NER- 0011 | N/A | NER for Earthing Transformer (PS5-63-IV- 0011) |  | EITS Building (Outdoors) | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151112 | 17.2 | A=2 B=2 C=0 | 05 | EPS | 2026-05-08 00:00:00 | CPP-RFI-68-331-07-0255
1453 | PS5-71-BE-0004 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 190 |  | PS5-71-IN-0002 | N/A | CRO-PRE PRESSURECONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-BE-0004 | N/A | CRO- prepressure module power junction box-JB3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151118, 151179 | 17.2 | LV Power_E03.1 - Trace heater PIPES | 07 | EPS | 2026-07-02 00:00:00 | CPP-RFI-68-331-05-0399
1454 | PS5-71-BE-0004 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 190 |  | PS5-71-IN-0002 | N/A | CRO-PRE PRESSURECONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-BE-0004 | N/A | CRO- prepressure module power junction box-JB3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151118, 151179 | 17.2 | LV Power_E03.2- Trace heater PIPES | 07 | EPS
1455 | PS5-71-BE-0004 -CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 190 |  | PS5-71-IN-0002 | N/A | CRO-PRE PRESSURECONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-BE-0004 | N/A | CRO- prepressure module power junction box-JB3 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151118, 151179 | 17.2 | LV Power_E03.3 - Trace heater PIPES | 07 | EPS | 2026-07-02 00:00:00 | CPP-RFI-68-331-05-0399
1456 | PS5-71-BI-0003 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 190 |  | PS5-71-IN-0002 | N/A | CRO-PRE PRESSURECONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-BI-0003 | N/A | CRO- prepressure module control junction box-JB1 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151118, 151179 | 17.2 | LV Power_E01-SPACE HEATER JB1 | 07 | EPS | 2026-07-02 00:00:00 | CPP-RFI-68-331-05-0399
1457 | PS5-71-BI-0003 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 190 |  | PS5-71-IN-0002 | N/A | CRO-PRE PRESSURECONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-BI-0003 | N/A | CRO- prepressure module control junction box-JB1 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151118, 151179 | 19.5 | LV Power_Crude Oil Pump 1 | 07 | EPS
1458 | PS5-71-BI-0003 -CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 190 |  | PS5-71-IN-0002 | N/A | CRO-PRE PRESSURECONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-BI-0003 | N/A | CRO- prepressure module control junction box-JB1 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151118, 151179 | 19.5 | LV Power_Crude Oil Pump 2 | 07 | EPS
1459 | PS5-71-BI-0003 -CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 2.5 | 190 |  | PS5-71-IN-0002 | N/A | CRO-PRE PRESSURECONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-BI-0003 | N/A | CRO- prepressure module control junction box-JB1 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151118, 151179 | 18.1 | LV Power_Autofilter | 07 | EPS
1460 | PS5-71-BI-0004 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 190 |  | PS5-71-IN-0002 | N/A | CRO-PRE PRESSURECONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-BI-0004 | N/A | CRO- prepressure module control junction box-JB2 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151118, 151179 | 17.2 | LV Power_E01-SPACE HEATER JB2 | 07 | EPS
1461 | PS5-71-BI-0005 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 200 |  | PS5-71-IN-0003 | N/A | DFO- PRE PRESSURE CONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-BI-0005 | N/A | DFO- prepressure module control junction box-JB1 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151118, 151179 | 17.2 | A=0 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
1462 | PS5-71-BI-0005 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 200 |  | PS5-71-IN-0003 | N/A | DFO- PRE PRESSURE CONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-BI-0005 | N/A | DFO- prepressure module control junction box-JB1 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151118, 151179 | 19.5 | A=0 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
1463 | PS5-71-BI-0005 -CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400VAC |  | 3C+E | 4 | 200 |  | PS5-71-IN-0003 | N/A | DFO- PRE PRESSURE CONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-BI-0005 | N/A | DFO- prepressure module control junction box-JB1 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151118, 151179 | 19.5 | A=1 B=2 C=0 | 07 | EPS | 2026-06-29 00:00:00 | CPP-RFI-68-33/1-05-0387
1464 | PS5-71-BI-0006 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230VAC |  | 2C+E | 2.5 | 200 |  | PS5-71-IN-0003 | N/A | DFO- PRE PRESSURE CONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-BI-0006 | N/A | DFO- prepressure module control junction box-JB2 |  | Generator Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167, 151118, 151179 | 17.2 | A=0 B=2 C=0 | 07 | EPS | 24-June-2026 | CPP-RFI-68-33/1-05-0377
1465 | PS5-71-DM- 3100A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 275 |  | PS5-61-IK-0001 | C0325 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-71-DM- 3100A | N/A | Diesel Fuel Supply Pump A |  | Diesel Fuel Pump Area | Ex'd - IP 66 | M25 / M32 |  | TZ-MID-68-WPR2- 151112,151111,151108, 151107 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1466 | PS5-71-DM- 3100B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 260 |  | PS5-61-IK-0001 | B0525 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-71-DM- 3100B | N/A | Diesel Fuel Supply Pump B |  | Diesel Fuel Pump Area | Ex'd - IP 66 | M25 / M32 |  | TZ-MID-68-WPR2- 151112,151111,151108, 151107 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1467 | PS5-71-DM- 3200-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 260 |  | PS5-61-IK-0001 | C0315 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-71-DM- 3200 | N/A | Diesel Fuel Make-Up Pump |  | Diesel Fuel Pump Area | Ex'd - IP 66 | M25 / M32 |  | TZ-MID-68-WPR2- 151112,151111,151108, 151107 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1468 | PS5-71-DM- 3300A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 10 | 250 |  | PS5-61-IK-0001 | A0315 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-71-DM- 3300A | N/A | Crude Fuel Oil Transfer Pump A |  | CFO Pump Area | Ex'd - IP 66 | M25 / M40 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 24.1 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1469 | PS5-71-DM- 3300B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 10 | 250 |  | PS5-61-IK-0001 | B0309 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-71-DM- 3300B | N/A | Crude Fuel Oil Transfer Pump B |  | CFO Pump Area | Ex'd - IP 66 | M25 / M40 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 24.1 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1470 | PS5-71-DM- 3400A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 10 | 240 |  | PS5-61-IK-0001 | A0214 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-71-DM- 3400A | N/A | Crude Fuel Oil Service Pump A |  | CFO Pump Area | Ex'd - IP 66 | M25 / M40 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 24.1 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1471 | PS5-71-DM- 3400B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 10 | 240 |  | PS5-61-IK-0001 | B0509 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-71-DM- 3400B | N/A | Crude Fuel Oil Service Pump B |  | CFO Pump Area | Ex'd - IP 66 | M25 / M40 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 24.1 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1472 | PS5-71-DM- 3500A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 290 |  | PS5-61-IK-0001 | C0323 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-71-DM- 3500A | N/A | Diesel Transfer Pump A |  | Diesel Day Fuel Day Drum Area | Ex'd - IP 66 | M25 / M32 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1473 | PS5-71-DM- 3500B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 6 | 290 |  | PS5-61-IK-0001 | B0621 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-71-DM- 3500B | N/A | Diesel Transfer Pump B |  | Diesel Day Fuel Day Drum Area | Ex'd - IP 66 | M25 / M32 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117 | 21.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1474 | PS5-71-FCV- 0018-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 150 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-FCV- 0018 | N/A | Flow Control Valve |  | CFO STORAGE TANK AREA | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151115 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1475 | PS5-71-FCV- 0019-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-FCV- 0019 | N/A | Flow Control Valve |  | DIESEL FUEL DAY DRUM | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1476 | PS5-71-FCV- 0020-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 195 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-FCV- 0020 | N/A | Flow Control Valve |  | CFO STORAGE TANK AREA | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151115 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-13 00:00:00 | CPP-RFI-68-331-05-0266
1477 | PS5-71-FIT- 0011A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 260 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-71-FIT- 0011A | N/A | Coriolis Flow Ind Transmitter |  | CFO STORAGE TANK AREA | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1478 | PS5-71-FIT- 0011B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 250 |  | PS5-06-IG-0002 | N/A | AC UPS Distribution Board (C) Single supply loads- 230VAC, 50Hz, 80A, 25KA/1s |  | EITS Building | Ind - IP 55 | M20 | PS5-71-FIT- 0011B | N/A | Coriolis Flow Ind Transmitter |  | CFO STORAGE TANK AREA | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1479 | PS5-71-HE- 2200-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 240 |  | PS5-61-IK-0001 | A0625 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-71-HE-2200 | N/A | Crude Fuel Oil Service Tank Heater |  | CFO Service tank area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 17.6 | A=1 B=2 C=0 | 07 | EPS | 2026-05-07 00:00:00 | CPP-RFI-68-331-07-0254
1480 | PS5-71-HE- 2200-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 35 | 240 |  | PS5-61-IK-0001 | A0625 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-71-HE-2200 | N/A | Crude Fuel Oil Service Tank Heater |  | CFO Service tank area | Ex'd - IP 66 | M32 / M40 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 29.3 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1481 | PS5-71-HE- 2200-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 130 |  | PS5-61-IG-0006 | N/A | Outdoor Normal L&SP DB - Field (South Side) |  | Export pump area | Ind - IP 55 | M20 | PS5-71-HE-2200 | N/A | Crude Fuel Oil Service Tank Heater |  | CFO Service tank area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151117,151114,151115 | 17.2 | A=1 B=2 C=0 | 06 | EPS | 2026-05-10 00:00:00 | CPP-RFI-68-331-05-0260
1482 | PS5-71-HE- 2300-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 250 |  | PS5-61-IK-0001 | B0319 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-71-HE-2300 | N/A | Crude Fuel Oil Storage Tank Heater |  | CFO Stroage tank area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 17.6 | A=0 B=2 C=0 | 07 | EPS | 2026-04-25 00:00:00 | CPP-RFI-68-33/1-05-0223
1483 | PS5-71-HE- 2300-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 35 | 250 |  | PS5-61-IK-0001 | B0319 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-71-HE-2300 | N/A | Crude Fuel Oil Storage Tank Heater |  | CFO Stroage tank area | Ex'd - IP 66 | M32 / M40 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 29.3 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1484 | PS5-71-HE- 2300-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 130 |  | PS5-61-IG-0006 | N/A | Outdoor Normal L&SP DB - Field (South Side) |  | Export pump area | Ind - IP 55 | M20 | PS5-71-HE-2300 | N/A | Crude Fuel Oil Storage Tank Heater |  | CFO Stroage tank area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151117,151114,151115 | 17.2 | A=0 B=2 C=0 | 06 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1485 | PS5-71-HE- 2400A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 35 | 260 |  | PS5-71-IE-0001 | N/A | Crude Fuel Oil Storage Tank Feed Heater Control Panel 1 |  | EITS Building | Ind - IP 55 | M32 | PS5-71-HE- 2400A | N/A | Crude Fuel Oil Storage Tank Feed Heater |  | CFO Stroage tank area | Ex'd - IP 66 | M32 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 29.3 | A=0 B=4 C=0 | 05 | EPS | 2026-04-24 00:00:00 | CPP-RFI-68-331-05-0225
1486 | PS5-71-HE- 2400A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 35 | 260 |  | PS5-71-IE-0001 | N/A | Crude Fuel Oil Storage Tank Feed Heater Control Panel 1 |  | EITS Building | Ind - IP 55 | M32 | PS5-71-HE- 2400A | N/A | Crude Fuel Oil Storage Tank Feed Heater |  | CFO Stroage tank area | Ex'd - IP 66 | M32 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 29.3 | LV Power (CFO Heater - Load 2 - 32kW) | 05 | EPS | 2026-04-24 00:00:00 | CPP-RFI-68-331-05-0225
1487 | PS5-71-HE- 2400A-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 260 |  | PS5-71-IE-0001 | N/A | Crude Fuel Oil Storage Tank Feed Heater Control Panel 1 |  | EITS Building | Ind - IP 55 | M32 | PS5-71-HE- 2400A | N/A | Crude Fuel Oil Storage Tank Feed Heater |  | CFO Stroage tank area | Ex'd - IP 66 | M32 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 27.5 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1488 | PS5-71-HE- 2400A-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 260 |  | PS5-71-IE-0001 | N/A | Crude Fuel Oil Storage Tank Feed Heater Control Panel 1 |  | EITS Building | Ind - IP 55 | M20 | PS5-71-HE- 2400A | N/A | Crude Fuel Oil Storage Tank Feed Heater |  | CFO Stroage tank area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1489 | PS5-71-HE- 2400B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 35 | 255 |  | PS5-71-IE-0002 | N/A | Crude Fuel Oil Storage Tank Feed Heater Control Panel 2 |  | EITS Building | Ind - IP 55 | M32 | PS5-71-HE- 2400B | N/A | Crude Fuel Oil Storage Tank Feed Heater |  | CFO Stroage tank area | Ex'd - IP 66 | M32 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 29.3 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1490 | PS5-71-HE- 2400B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 35 | 255 |  | PS5-71-IE-0002 | N/A | Crude Fuel Oil Storage Tank Feed Heater Control Panel 2 |  | EITS Building | Ind - IP 55 | M32 | PS5-71-HE- 2400B | N/A | Crude Fuel Oil Storage Tank Feed Heater |  | CFO Stroage tank area | Ex'd - IP 66 | M32 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 29.3 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1491 | PS5-71-HE- 2400B-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 25 | 255 |  | PS5-71-IE-0002 | N/A | Crude Fuel Oil Storage Tank Feed Heater Control Panel 2 |  | EITS Building | Ind - IP 55 | M32 | PS5-71-HE- 2400B | N/A | Crude Fuel Oil Storage Tank Feed Heater |  | CFO Stroage tank area | Ex'd - IP 66 | M32 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 27.5 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1492 | PS5-71-HE- 2400B-CL04 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 255 |  | PS5-71-IE-0002 | N/A | Crude Fuel Oil Storage Tank Feed Heater Control Panel 2 |  | EITS Building | Ind - IP 55 | M20 | PS5-71-HE- 2400B | N/A | Crude Fuel Oil Storage Tank Feed Heater |  | CFO Stroage tank area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 17.2 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1493 | PS5-71-IE-0001- CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 95 | 0 |  | PS5-61-IK-0001 | A0501 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 | PS5-71-IE-0001 | N/A | Crude Fuel Oil Storage Tank Feed Heater Control Panel 1 |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 49.5 | LV Power (CFO Storage tank Heater panel 1) ( Refer Note 06) | 04 | EITS
1494 | PS5-71-IE-0002- CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 95 | 0 |  | PS5-61-IK-0001 | B0301 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 | PS5-71-IE-0002 | N/A | Crude Fuel Oil Storage Tank Feed Heater Control Panel 2 |  | EITS Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112 | 49.5 | LV Power (CFO Storage Heater Panel - 2) ( Refer Note 06) | 05 | EITS
1495 | PS5-71-IES- 3100A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 270 |  | PS5-61-IK-0001 | C0325 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-71-IES- 3100A | N/A | Diesel Fuel Supply Pump A-LCS |  | Diesel Fuel Pump Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151108. 151107 | 17.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1496 | PS5-71-IES- 3100B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 265 |  | PS5-61-IK-0001 | B0525 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-71-IES- 3100B | N/A | Diesel Fuel Supply Pump B-LCS |  | Diesel Fuel Pump Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151108. 151107 | 17.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1497 | PS5-71-IES- 3200-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 260 |  | PS5-61-IK-0001 | C0315 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-71-IES-3200 | N/A | Diesel Fuel Make-Up Pump-LCS |  | Diesel Fuel Pump Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151108, 151107 | 17.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1498 | PS5-71-IES- 3300A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 250 |  | PS5-61-IK-0001 | A0315 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-71-IES- 3300A | N/A | Crude Fuel Oil Transfer Pump A-LCS |  | CFO Pump Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 17.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1499 | PS5-71-IES- 3300B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 250 |  | PS5-61-IK-0001 | B0309 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-71-IES- 3300B | N/A | Crude Fuel Oil Transfer Pump B-LCS |  | CFO Pump Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 17.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1500 | PS5-71-IES- 3400A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 240 |  | PS5-61-IK-0001 | A0214 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-71-IES- 3400A | N/A | Crude Fuel Oil Service Pump A-LCS |  | CFO Pump Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 17.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1501 | PS5-71-IES- 3400B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 240 |  | PS5-61-IK-0001 | B0509 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-71-IES- 3400B | N/A | Crude Fuel Oil Service Pump B-LCS |  | CFO Pump Area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 17.6 | A=0 B=2 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1502 | PS5-71-IES- 3500A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 290 |  | PS5-61-IK-0001 | C0323 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-71-IES- 3500A | N/A | Diesel Transfer Pump A- LCS |  | Diesel fuel day drum area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117 | 17.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1503 | PS5-71-IES- 3500B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 3C | 2.5 | 290 |  | PS5-61-IK-0001 | B0621 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-71-IES- 3500B | N/A | Diesel Transfer Pump B- LCS |  | Diesel fuel day drum area | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117 | 17.6 | A=0 B=3 C=0 | 05 | EPS | 2026-05-21 00:00:00 | CPP-RFI-68-33/1-07-0290
1504 | PS5-71-IN-0001 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-IN-0001 | N/A | DFO- SEPARATOR CONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
1505 | PS5-71-IN-0001 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-IN-0001 | N/A | DFO- SEPARATOR CONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 05 | EPS
1506 | PS5-71-IN-0001 -CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 10 | 50 |  | PS5-60-IH-0002 | C1F | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-71-IN-0001 | N/A | DFO- SEPARATOR CONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 25.6 | A=1 B=2 C=0 | 05 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
1507 | PS5-71-IN-0002 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-IN-0002 | N/A | CRO-PRE PRESSURECONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
1508 | PS5-71-IN-0002 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-IN-0002 | N/A | CRO-PRE PRESSURECONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 05 | EPS
1509 | PS5-71-IN-0002 -CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 6 | 40 |  | PS5-60-IH-0002 | C5G | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-71-IN-0002 | N/A | CRO-PRE PRESSURECONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 22.9 | CRO MCC AUX Cable (Common MCC) | 05 | EPS
1510 | PS5-71-IN-0003 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-IN-0003 | N/A | DFO- PRE PRESSURE CONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
1511 | PS5-71-IN-0003 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 45 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-IN-0003 | N/A | DFO- PRE PRESSURE CONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | A=0 B=1 C=0 | 05 | EPS | 12-June-2026 | CPP-RFI-68-33/1-07-0330
1512 | PS5-71-IN-0003 -CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 4 | 40 |  | PS5-60-IH-0002 | C5F | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-71-IN-0003 | N/A | DFO- PRE PRESSURE CONTROL PANEL |  | Generator Electrical Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 21.6 | A=1 B=2 C=0 | 05 | EPS | 2026-06-04 00:00:00 | CPP-RFI-68-33/1-05-0309
1513 | PS5-71-IN- 0004A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 50 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-IN- 0004A | N/A | CRO- SEPARATOR CONTROL PANEL-1 |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
1514 | PS5-71-IN- 0004A-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 50 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-IN- 0004A | N/A | CRO- SEPARATOR CONTROL PANEL-1 |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 05 | EPS
1515 | PS5-71-IN- 0004A-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 70 | 40 |  | PS5-60-IH-0002 | C5H | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M50 | PS5-71-IN- 0004A | N/A | CRO- SEPARATOR CONTROL PANEL-1 |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 43.4 | A=1 B=2 C=0 | 05 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
1516 | PS5-71-IN- 0004B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-IN- 0004B | N/A | CRO- SEPARATOR CONTROL PANEL-2 |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS A | 05 | EPS
1517 | PS5-71-IN- 0004B-CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 2.5 | 40 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M20 | PS5-71-IN- 0004B | N/A | CRO- SEPARATOR CONTROL PANEL-2 |  | Generator Electrical Building | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151167 | 17.2 | UPS B | 05 | EPS
1518 | PS5-71-IN- 0004B-CL03 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 70 | 30 |  | PS5-60-IH-0002 | C1H | GENERATOR COMMON MCC - Generator Elect. Building |  | Generator Electrical Building | Ind - IP 55 | M50 | PS5-71-IN- 0004B | N/A | CRO- SEPARATOR CONTROL PANEL-2 |  | Generator Electrical Building | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151116 | 43.4 | A=1 B=2 C=0 | 05 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
1519 | PS5-71-LCV- 4101-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 160 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-LCV- 4101 | N/A | LCV - CFO STORAGE TANK AREA |  | Field_CFO STORAGE TANK AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151114,151115 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-13 00:00:00 | CPP-RFI-68-331-05-0266
1520 | PS5-71-MOV- 0001-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 140 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-MOV- 0001 | N/A | Motor Operated Valve |  | Power generator building area | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151118 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1521 | PS5-71-MOV- 0002-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 150 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-MOV- 0002 | N/A | Motor Operated Valve |  | Power generator building area | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151118 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1522 | PS5-71-MOV- 0003-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 175 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-MOV- 0003 | N/A | Motor Operated Valve |  | Power generator building area | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151118 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1523 | PS5-71-MOV- 0004-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 185 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-MOV- 0004 | N/A | Motor Operated Valve |  | Power generator building area | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151118 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1524 | PS5-71-MOV- 0007-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 180 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-MOV- 0007 | N/A | Motor Operated Valve |  | Power generator building area | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151118 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-10 00:00:00 | CPP-RFI-68-331-05-0260
1525 | PS5-71-MOV- 0008-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 190 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-MOV- 0008 | N/A | Motor Operated Valve |  | Power generator building area | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151118 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-10 00:00:00 | CPP-RFI-68-331-05-0260
1526 | PS5-71-MOV- 0009-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 200 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-MOV- 0009 | N/A | Motor Operated Valve |  | Power generator building area | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151118 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1527 | PS5-71-MOV- 0010-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 210 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-MOV- 0010 | N/A | Motor Operated Valve |  | Power generator building area | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151118 | 18.1 | A=1 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1528 | PS5-71-SDV- 0001-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 125 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-SDV- 0001 | N/A | Shutdown Valve |  | DIESEL FUEL DAY DRUM | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1529 | PS5-71-SDV- 0022-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 145 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-SDV- 0022 | N/A | Shutdown Valve |  | CFO STORAGE TANK AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151115 | 18.1 | LV Power (Refer Note 13) | 05 | EPS
1530 | PS5-71-SDV- 0029-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 300 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-SDV- 0029 | N/A | Shutdown Valve |  | DIESEL FUEL STORAGE AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151115,151111, 151108,151107 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1531 | PS5-71-SDV- 0039-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-SDV- 0039 | N/A | Shutdown Valve |  | CFO STORAGE TANK AREA | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151115 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-13 00:00:00 | CPP-RFI-68-331-05-0266
1532 | PS5-71-UZ- 6200-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 16 | 160 |  | PS5-61-IG-0014 | N/A | Outdoor Power DB - Field(North) |  | Near EITS | Ind - IP 55 | M25 | PS5-71-UZ-6200 | N/A | Diesel Fuel Dispenser Station |  | Diesel Fuel Dispenser Station | Ex'd - IP 66 | M25 |  | TZ-MID-68-WPR2- 151112, 151111, 151108, 151107 | 24.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1533 | PS5-71-XV-0089 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 190 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-XV-0089 | N/A | On / Off Valve |  | CFO STORAGE TANKS AREA | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151115 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-13 00:00:00 | CPP-RFI-68-331-05-0266
1534 | PS5-71-XV-0090 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 195 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-XV-0090 | N/A | On / Off Valve |  | CFO STORAGE TANKS AREA | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151115 | 18.1 | A=2 B=2 C=0 | 05 | EPS | 2026-05-13 00:00:00 | CPP-RFI-68-331-05-0266
1535 | PS5-71-XV-0091 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 75 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-XV-0091 | N/A | On / Off Valve |  | Power generator building area | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151117,151115 | 18.1 | MOV DB outgoing to On/OFF Valve (Refer Note 13) | 05 | EPS
1536 | PS5-71-XV-0092 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 120 |  | PS5-61-IG-0042 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-71-XV-0092 | N/A | On / Off Valve |  | DIESEL FUEL DAY DRUM ARE | Ind - IP 55 | M20 / M25 |  | TZ-MID-68-WPR2- 151117 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1537 | PS5-74-IG-5101 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 185 | 170 |  | PS5-61-IK-0001 | A0707 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M63 | PS5-74-IG-5101 | N/A | Nitrogen Generation Skid Power Distribution Panel |  | Nitrogen Generation Skid | Ind - IP 55 | M63 / M50 |  | TZ-MID-68-WPR2- 151112,151111,151108 | 59.4 | A=0 B=2 C=0 | 05 | EPS | 27-May-2026 | CPP-RFI-68-33/1-07-0303
1538 | PS5-74-LB-5101 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 10 | 320 |  | PS5-06-IG- 0004A | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-74-LB-5101 | N/A | Nitrogen Generation Skid - Unit Control Panel |  | Nitrogen Generation Skid | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167,151116,151112, 151111,151108 | 22.6 | A=1 B=2 C=0 | 05 | EPS | 2026-05-10 00:00:00 | CPP-RFI-68-331-05-0260
1539 | PS5-74-LB-5101 -CL02 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 10 | 320 |  | PS5-06-IG- 0004B | N/A | AC UPS DB - Generator Electrical Bldng |  | Generator Electrical Building | Ind - IP 55 | M25 | PS5-74-LB-5101 | N/A | Nitrogen Generation Skid - Unit Control Panel |  | Nitrogen Generation Skid | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151167,151116,151112, 151111,151108 | 22.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1540 | PS5-75-DM- 3100A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 410 |  | PS5-61-IK-0001 | A0233 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-75-DM- 3100A | N/A | Corrosion inhbitor Pump A |  | Near DRA injection package | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1541 | PS5-75-DM- 3100B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 410 |  | PS5-61-IK-0001 | B0633 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-75-DM- 3100B | N/A | Corrosion inhibitor Pump B |  | Near DRA injection package | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 27-May-2026 | CPP-RFI-68-33/1-07-0303
1542 | PS5-75-DM- 3200A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 410 |  | PS5-61-IK-0001 | A0313 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-75-DM- 3200A | N/A | Biocide injection Pump A |  | Near DRA injection package | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1543 | PS5-75-DM- 3200B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 410 |  | PS5-61-IK-0001 | B0619 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-75-DM- 3200B | N/A | Biocide injection Pump B |  | Near DRA injection package | Ex'd - IP 66 | M20 / M25 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 18.1 | A=0 B=2 C=0 | 05 | EPS | 27-May-2026 | CPP-RFI-68-33/1-07-0303
1544 | PS5-75-IES- 3100A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 5C | 2.5 | 410 |  | PS5-61-IK-0001 | A0233 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-75-IES- 3100A | N/A | Corrosion inhbitor Pump A-LCS |  | Near DRA injection package | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 19.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1545 | PS5-75-IES- 3100B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 5C | 2.5 | 410 |  | PS5-61-IK-0001 | B0633 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-75-IES- 3100B | N/A | Corrosion inhibitor Pump B-LCS |  | Near DRA injection package | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 19.6 | A=0 B=2 C=0 | 05 | EPS | 27-May-2026 | CPP-RFI-68-33/1-07-0303
1546 | PS5-75-IES- 3200A-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 5C | 2.5 | 410 |  | PS5-61-IK-0001 | A0313 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-75-IES- 3200A | N/A | Biocide injection Pump A -LCS |  | Near DRA injection package | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 19.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1547 | PS5-75-IES- 3200B-CD01 | 0.6/1KV | CU/PVC/LSZH/G SWA/LSZH | 48V DC |  | 5C | 2.5 | 410 |  | PS5-61-IK-0001 | B0619 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M20 | PS5-75-IES- 3200B | N/A | Biocide injection Pump B -LCS |  | Near DRA injection package | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114,151113 | 19.6 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1548 | PS5-75-ISO- 0001-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 16 | 400 |  | PS5-61-IK-0001 | A0531 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M32 | PS5-75-ISO- 0001 | N/A | Power socket-DRA Injection package MCC |  | Field_DRA injection package | Ex'd - IP 66 | M32 |  | TZ-MID-68-WPR2- 151112, 151111, 151115, 151117, 151114,151113 | 28.2 | A=0 B=2 C=0 | 05 | EPS | 27-May-2026 | CPP-RFI-68-33/1-07-0303
1549 | PS5-75-ISO- 0002-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 10 | 400 |  | PS5-61-IK-0001 | B0601 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M25 | PS5-75-ISO- 0002 | N/A | Power socket-DRA Injection Pkg portable recirculation pump |  | Field_DRA injection package | Ex'd - IP 66 | M25 |  | TZ-MID-68-WPR2- 151112, 151111, 151115, 151117, 151114,151113 | 25.6 | A=0 B=2 C=0 | 05 | EPS | 27-May-2026 | CPP-RFI-68-33/1-07-0303
1550 | PS5-75-MOV- 0001-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 2.5 | 130 |  | PS5-61-IG-0043 | N/A | MOV DB - Field |  | Near Export pump area | Ind - IP 55 | M20 | PS5-75-MOV- 0001 | N/A | Motorized Operated Valve - DRA Injection Package |  | DRA Injection Package | Ex'd - IP 66 | M20 |  | TZ-MID-68-WPR2- 151117,151114,151113 | 18.1 | A=2 B=2 C=0 | 07 | EPS | 2026-06-03 00:00:00 | CPP-RFI-68-331-05-0312
1551 | PS5-78-JC- 9100A-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 10 | 210 |  | PS5-61-IK-0006 | A0301 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M25 | PS5-78-JC- 9100A | N/A | 10 OHT Crane - Generator Building |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 25.6 | LV Power | 05 | EPS
1552 | PS5-78-JC- 9100B-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 10 | 190 |  | PS5-61-IK-0006 | A0328 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M25 | PS5-78-JC- 9100B | N/A | 10 OHT Crane - Generator Building |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 25.6 | LV Power | 05 | EPS
1553 | PS5-78-JC- 9100C-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 10 | 160 |  | PS5-61-IK-0006 | B0332 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M25 | PS5-78-JC- 9100C | N/A | 10 OHT Crane - Generator Building |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 25.6 | LV Power | 05 | EPS
1554 | PS5-78-JC- 9100D-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 10 | 140 |  | PS5-61-IK-0006 | B0328 | 0.4kV Switchboard |  | Gen Electrical Building | Ind - IP 55 | M25 | PS5-78-JC- 9100D | N/A | 10 OHT Crane - Generator Building |  | Generator Building | Ind - IP 55 | M25 |  | TZ-MID-68-WPR2- 151116 | 25.6 | LV Power | 05 | EPS
1555 | PS5-79-BH- 0001-CH01 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 5550V AC |  | 1C | 95 | 375 |  | PS5-61-IJ-0010 | A02 | SM6 LLHT 7.2 kV MV Switchgear, 630A, 16kA/3s |  | EITS Building | Ind - IP 55 | M32 | PS5-79-BH-0001 | N/A | LLHT High Voltage Power Junction Box_North |  | Near export pump area | Ex'd - IP 66 | M32 / M40 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 30.1 | A=2 B=1 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-05-0244
1556 | PS5-79-BH- 0001-CH02 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 5550V AC |  | 1C | 95 | 375 |  | PS5-61-IJ-0010 | A02 | SM6 LLHT 7.2 kV MV Switchgear, 630A, 16kA/3s |  | EITS Building | Ind - IP 55 | M32 | PS5-79-BH-0001 | N/A | LLHT High Voltage Power Junction Box_North |  | Near export pump area | Ex'd - IP 66 | M32 / M40 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 30.1 | A=2 B=1 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-05-0244
1557 | PS5-79-BH- 0001-CH03 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 5550V AC |  | 1C | 95 | 375 |  | PS5-61-IJ-0010 | A02 | SM6 LLHT 7.2 kV MV Switchgear, 630A, 16kA/3s |  | EITS Building | Ind - IP 55 | M32 | PS5-79-BH-0001 | N/A | LLHT High Voltage Power Junction Box_North |  | Near export pump area | Ex'd - IP 66 | M32 / M40 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 30.1 | A=2 B=1 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-05-0244
1558 | PS5-79-BH- 0002-CH01 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 5550V AC |  | 1C | 95 | 380 |  | PS5-61-IJ-0011 | A02 | SM6 LLHT 7.2 kV MV Switchgear, 630A, 16kA/3s |  | EITS Building | Ind - IP 55 | M32 | PS5-79-BH-0002 | N/A | LLHT High Voltage Power Junction Box_South |  | Near export pump area | Ex'd - IP 66 | M32 / M40 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 30.1 | A=2 B=1 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-05-0244
1559 | PS5-79-BH- 0002-CH02 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 5550V AC |  | 1C | 95 | 380 |  | PS5-61-IJ-0011 | A02 | SM6 LLHT 7.2 kV MV Switchgear, 630A, 16kA/3s |  | EITS Building | Ind - IP 55 | M32 | PS5-79-BH-0002 | N/A | LLHT High Voltage Power Junction Box_South |  | Near export pump area | Ex'd - IP 66 | M32 / M40 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 30.1 | A=2 B=1 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-05-0244
1560 | PS5-79-BH- 0002-CH03 | 3.6/6 (7.2) KV | AL/XLPE/TCWB/ PVC/AWA/FRLS PVC | 5550V AC |  | 1C | 95 | 380 |  | PS5-61-IJ-0011 | A02 | SM6 LLHT 7.2 kV MV Switchgear, 630A, 16kA/3s |  | EITS Building | Ind - IP 55 | M32 | PS5-79-BH-0002 | N/A | LLHT High Voltage Power Junction Box_South |  | Near export pump area | Ex'd - IP 66 | M32 / M40 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151114 | 30.1 | A=2 B=1 C=0 | 05 | EPS | 2026-05-05 00:00:00 | CPP-RFI-68-331-05-0244
1561 | PS5-79-IV-0001 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 50 | 195 |  | PS5-61-IK-0001 | B0229 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 | PS5-79-IV-0001 | N/A | Electrical Heat Tracing Transformer 1 - 63KVA 400/400V |  | Near CFO Service Pump area | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 32.9 | A=0 B=2 C=0 | 05 | EPS | 27-May-2026 | CPP-RFI-68-33/1-07-0303
1562 | PS5-79-IV-0002 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 95 | 190 |  | PS5-61-IK-0001 | B0431 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 | PS5-79-IV-0002 | N/A | Electrical Heat Tracing Transformer 2 - 100KVA 400/400V |  | Near CFO Service Pump area | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112,151111,151115 | 42.1 | A=0 B=2 C=0 | 05 | EPS | 27-May-2026 | CPP-RFI-68-33/1-07-0303
1563 | PS5-79-IV-0003 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 70 | 280 |  | PS5-61-IK-0001 | B0213 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 | PS5-79-IV-0003 | N/A | Electrical Heat Tracing Transformer 3 - 63KVA 400/400V |  | Near Diesel Fuel Day Tank Area | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117 | 38 | A=0 B=2 C=0 | 05 | EPS | 27-May-2026 | CPP-RFI-68-33/1-07-0303
1564 | PS5-79-IV-0004 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 70 | 280 |  | PS5-61-IK-0001 | B0201 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 | PS5-79-IV-0004 | N/A | Electrical Heat Tracing Transformer 4 - 63KVA 400/400V |  | Near Diesel Fuel Day Tank Area | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117 | 38 | A=0 B=2 C=0 | 05 | EPS | 27-May-2026 | CPP-RFI-68-33/1-07-0303
1565 | PS5-79-IV-0005 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 120 | 280 |  | PS5-61-IK-0001 | B0315 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 | PS5-79-IV-0005 | N/A | Electrical Heat Tracing Transformer 5 - 100KVA 400/400V |  | Near Diesel Fuel Day Tank Area | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117 | 45.4 | A=0 B=2 C=0 | 05 | EPS | 27-May-2026 | CPP-RFI-68-33/1-07-0303
1566 | PS5-79-IV-0006 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 70 | 280 |  | PS5-61-IK-0001 | A0206 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 | PS5-79-IV-0006 | N/A | Electrical Heat Tracing Transformer 6 - 63KVA 400/400V |  | Near Export Pump Area | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117 | 38 | A=0 B=2 C=0 | 05 | EPS | 27-May-2026 | CPP-RFI-68-33/1-07-0303
1567 | PS5-79-IV-0007 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 120 | 285 |  | PS5-61-IK-0001 | A0601 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 | PS5-79-IV-0007 | N/A | Electrical Heat Tracing Transformer 7 - 100KVA 400/400V |  | Near Export Pump Area | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117 | 45.4 | A=0 B=2 C=0 | 05 | EPS | 27-May-2026 | CPP-RFI-68-33/1-07-0303
1568 | PS5-79-IV-0008 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 120 | 290 |  | PS5-61-IK-0001 | A0629 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 | PS5-79-IV-0008 | N/A | Electrical Heat Tracing Transformer 8 - 100KVA 400/400V |  | Near Export Pump Area | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117 | 45.4 | A=0 B=2 C=0 | 05 | EPS | 27-May-2026 | CPP-RFI-68-33/1-07-0303
1569 | PS5-79-IV-0009 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 120 | 295 |  | PS5-61-IK-0001 | A0727 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 | PS5-79-IV-0009 | N/A | Electrical Heat Tracing Transformer 9 - 100KVA 400/400V |  | Near Export Pump Area | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117 | 45.4 | A=0 B=2 C=0 | 05 | EPS | 27-May-2026 | CPP-RFI-68-33/1-07-0303
1570 | PS5-79-IV-0010 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 120 | 295 |  | PS5-61-IK-0001 | A0617 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M50 | PS5-79-IV-0010 | N/A | Electrical Heat Tracing Transformer 10 - 100KVA 400/400V |  | Near Export Pump Area | Ind - IP 55 | M50 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117 | 45.4 | A=0 B=2 C=0 | 05 | EPS | 27-May-2026 | CPP-RFI-68-33/1-07-0303
1571 | PS5-79-IV-0011 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 185 | 315 |  | PS5-61-IK-0001 | A0327 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M63 | PS5-79-IV-0011 | N/A | Electrical Heat Tracing Transformer 11 - 100KVA 400/400V |  | Power generator building area | Ind - IP 55 | M63 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151118 | 59.4 | A=1 B=2 C=0 | 05 | EPS | 2026-05-24 00:00:00 | CPP-RFI-68-331-05-0295
1572 | PS5-79-IV-0012 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 3C+E | 185 | 405 |  | PS5-61-IK-0001 | A0722 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M63 | PS5-79-IV-0012 | N/A | Electrical Heat Tracing Transformer 12 - 100KVA 400/400V |  | Power generator building area | Ind - IP 55 | M63 |  | TZ-MID-68-WPR2- 151112,151111,151115, 151117,151118 | 59.4 | A=1 B=2 C=0 | 05 | EPS | 2026-05-08 00:00:00 | CPP-RFI-68-331-07-0255
1573 | PS5-82-IN-0001 -CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 400V AC |  | 4C+E | 35 | 385 |  | PS5-61-IK-0001 | B0427 | 0.4kV Switchboard |  | EITS Building | Ind - IP 55 | M40 | PS5-82-IN-0001 | N/A | MCC for Sewage Treatment Package |  | Sewage Treatment Pkge -North w | Ind - IP 55 | M40 |  | TZ-MID-68-WPR2- 151112,151111,151108, 151107,151105 | 34.5 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1574 | PS5-87-IRF- 0001-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 135 |  | PS5-61-IG-0007 | N/A | Outdoor Normal Lighting DB - Field - (North Side) |  | Near EDG package | Ind - IP 55 | M20 | PS5-87-IRF-0001 | N/A | Transformer Rectifier Unit 1-for tank (PS5-53- TR-4100) |  | Fire water storage Tank area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151111,151108,151109 | 18.5 | A=1 B=2 C=0 | 05 | EPS | 2026-05-13 00:00:00 | CPP-RFI-68-331-05-0266
1575 | PS5-87-IRF- 0002-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 120 |  | PS5-61-IG-0006 | N/A | Outdoor Normal L&SP DB - Field (South Side) |  | Export pump area | Ind - IP 55 | M20 | PS5-87-IRF-0002 | N/A | Transformer rectifier unit 2-for tank (PS5-71-TR- 4100) |  | CFO Area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151117,151115 | 18.5 | A=1 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1576 | PS5-87-IRF- 0003-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 4 | 120 |  | PS5-61-IG-0006 | N/A | Outdoor Normal L&SP DB - Field (South Side) |  | Export pump area | Ind - IP 55 | M20 | PS5-87-IRF-0003 | N/A | Transformer rectifier unit 3-for tank (PS5-71-TR- 4200) |  | CFO Area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151117,151115 | 18.5 | A=1 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211
1577 | PS5-87-IRF- 0004-CL01 | 0.6/1KV | CU/XLPE/LSZH/ GSWA/LSZH | 230V AC |  | 2C+E | 6 | 180 |  | PS5-61-IG-0007 | N/A | Outdoor Normal Lighting DB - Field - (North Side) |  | Near EDG package | Ind - IP 55 | M20 | PS5-87-IRF-0004 | N/A | Transformer rectifier unit 4-for tank ( PS5-71-TR- 4400) |  | Diesel fuel tank Area | Ind - IP 55 | M20 |  | TZ-MID-68-WPR2- 151111,151108,151107 | 19.5 | A=0 B=2 C=0 | 05 | EPS | 2026-04-17 00:00:00 | CPP-RFI-68-33/1-05-0211

## Instrument Cable Schedule
PROJECT NO. : 415000-00095
Cable Details | [9 empty] | From Equipment | [6 empty] | To Equipment
Sr. No. | Cable Tag. | Voltage Grade | Type | System Voltage | Drum No | Cores | Size (mm²) | Actual length laying done (m) | planned Length (m) | Tag No. | Cub. Ref | Description | G&T completed | Location | Gland Type | Entry Thread | Tag No. | Cub. Ref | Description | G&T Completed | Location | Gland Type | Entry Thread | Cable routing plan | Cable Routing Drawing | Outer Diameter (mm) | Remarks | Rev | DPS | Cable pulling date | Cable laying RFI Num | Drum tested RFI | Coiled length
1 | PS5-74-LB-5101-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 205 |  | PS5-74-LB-5101 |  |  |  | Package Skid |  |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Nitrogen Generation Skid interface; A=0 B=2 C=0 | 06 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0063
2 | PS5-74-LB-5101-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 205 |  | PS5-74-LB-5101 |  |  |  | Package Skid |  |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Nitrogen Generation Skid interface; A=0 B=2 C=0 | 06
3 | PS5-74-LB-5101-CJ01 | [5 empty] | 1P X 1.0 OS FR | 205 |  | PS5-74-LB-5101 |  |  |  | Package Skid |  |  | PS5-03-SFMC-0006 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Nitrogen Generation Skid interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0063
4 | PS5-01-BI-0001-CC01 | [5 empty] | 12P X 0.75 OS FR | 330 |  | PS5-01-BI-0001 |  |  |  | Package Skid |  |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; Foam Package interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
5 | PS5-01-BI-0002-CC01 | [5 empty] | 12P X 0.75 OS FR | 305 |  | PS5-01-BI-0002 |  |  |  | Package Skid |  |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; Watermist Package interface; A=1 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
6 | PS5-01-BI-0003-CC01 | [5 empty] | 12P X 0.75 OS FR | 305 |  | PS5-01-BI-0003 |  |  |  | Package Skid |  |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; Watermist Package interface; A=1 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
7 | PS5-01-BI-0004-CC01 | [5 empty] | 6P X 0.75 OS FR | 305 |  | PS5-01-BI-0004 |  |  |  | Package Skid |  |  | PS5-03-SFMC-0012 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Watermist Package interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
8 | PS5-01-BI-0005-CC01 | [5 empty] | 6P X 0.75 OS FR | 330 |  | PS5-01-BI-0005 |  |  |  | Package Skid |  |  | PS5-03-SFMC-0012 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Foam Package interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
9 | PS5-01-BI-0006-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 330 |  | PS5-01-BI-0006 |  |  |  | Package Skid |  |  | PS5-03-SFMC-0007 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Foam Package interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
10 | PS5-01-BI-1117-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 205 |  | PS5-01-FIT-0003A |  | Instr:PS5-01-BI-1117, InstrLoc:Field, Branch:PS5-01-FIT-0003A-CJ01, Sz:1P X 1.0 OS FL RTD, L:65m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0002 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
11 | PS5-01-BI-1118-CC01 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 205 |  | PS5-01-FCV-0003A |  | Instr:PS5-01-BI-1118, InstrLoc:Field, Branch:PS5-01-FY-0003A-CJ01, Sz:1P X 1.0 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0001 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0045
12 | PS5-01-BI-1501-CC01 | [5 empty] | 2P X 1.0 IS/OS FR | 340 |  | PS5-01-PIT-0010 |  | Instr:PS5-01-BI-1501, InstrLoc:Field, Branch:PS5-01-PIT-0010-CJ01, Sz:1P X 1.0 OS FR, L:115m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0007 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=2 C=0 | 05 |  | 2026-06-26 00:00:00 | CPP-RFI-68-64-12-0074
13 | PS5-01-BI-1515-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 205 |  | PS5-01-PDIT-0011A |  | Instr:PS5-01-BI-1515, InstrLoc:Field, Branch:PS5-01-PDIT-0011A-CJ01, Sz:1P X 1.0 OS FR, L:50m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0008 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
14 | PS5-01-BI-1520-CC01 | [5 empty] | 12P X 0.75 IS/OS FR | 275 |  | PS5-01-PIT-8101A |  | Instr:PS5-01-BI-1520, InstrLoc:Field, Branch:PS5-01-PIT-8101A-CJ01, Sz:1P X 1.0 OS FR, L:55m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0008 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
15 | PS5-01-BI-1571-CC01 | [5 empty] | 12P X 0.75 IS/OS FR | 320 |  | PS5-01-BI-1571 |  |  |  | Package Skid |  |  | PS5-03-SFMC-0008 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
16 | PS5-01-BI-2110-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 205 |  | PS5-01-FCV-0003A |  | Instr:PS5-01-BI-2110, InstrLoc:Field, Branch:PS5-01-FXS-0003A-CJ01, Sz:1P X 1.0 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
17 | PS5-01-BI-2520-CC01 | [5 empty] | 12P X 2.5 OS FR | 275 |  | PS5-01-SY-8101A |  | Instr:PS5-01-BI-2520, InstrLoc:Field, Branch:PS5-01-SY-8101A-CJ01, Sz:1P X 2.5 OS FR, L:55m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0012 |  |  |  | 33kV EITS Building | M50 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M50; A=1 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
18 | PS5-01-BI-2571A-CC01 | [5 empty] | 12P X 0.75 OS FR | 320 |  | PS5-01-BI-2571A |  |  |  | Package Skid |  |  | PS5-03-SFMC-0012 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; Deluge Valve Skid interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
19 | PS5-01-BI-2571B-CC01 | [5 empty] | 6P X 2.5 OS FR | 320 |  | PS5-01-BI-2571B |  |  |  | Package Skid |  |  | PS5-03-SFMC-0012 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Deluge Valve Skid interface; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-12-0055
20 | PS5-01-IE-0002A-CC01 | [5 empty] | 6P X 0.75 OS FR | 245 |  | PS5-01-IE-0002A |  |  |  | Package Skid |  |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Jockey Pump package interface; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-12-0055
21 | PS5-01-IE-0002A-CC02 | [5 empty] | 6P X 0.75 OS FR | 245 |  | PS5-01-IE-0002A |  |  |  | Package Skid |  |  | PS5-03-SFMC-0013 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Jockey Pump package interface; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-12-0055
22 | PS5-01-IE-0002B-CC01 | [5 empty] | 6P X 0.75 OS FR | 245 |  | PS5-01-IE-0002B |  |  |  | Package Skid |  |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Jockey Pump package interface; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-12-0055
23 | PS5-01-IE-0002B-CC02 | [5 empty] | 6P X 0.75 OS FR | 245 |  | PS5-01-IE-0002B |  |  |  | Package Skid |  |  | PS5-03-SFMC-0013 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Jockey Pump package interface; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-12-0055
24 | PS5-01-IE-0009A-CC01 | [5 empty] | 6P X 0.75 OS FR | 230 |  | PS5-01-IE-0009A |  |  |  | Package Skid |  |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Fire Water Pump package interface; A=0 B=2 C=0 | 06 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-12-0055
25 | PS5-01-IE-0009A-CC02 | [5 empty] | 2P X 1.0 OS FR | 230 |  | PS5-01-IE-0009A |  |  |  | Package Skid |  |  | PS5-03-SFMC-0012 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Fire Water Pump package interface | 06
26 | PS5-01-IE-0009B-CC01 | [5 empty] | 6P X 0.75 OS FR | 250 |  | PS5-01-IE-0009B |  |  |  | Package Skid |  |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Fire Water Pump package interface; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-12-0055
27 | PS5-01-IE-0009B-CC02 | [5 empty] | 2P X 1.0 OS FR | 250 |  | PS5-01-IE-0009B |  |  |  | Package Skid |  |  | PS5-03-SFMC-0012 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Fire Water Pump package interface | 05
28 | PS5-01-LB-0004-CC01 | [5 empty] | 6P X 0.75 OS FR | 205 |  | PS5-01-LB-0004 |  |  |  | UCP |  |  | PS5-03-SFMC-0011 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Gaseous Supression package interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
29 | PS5-01-LB-0004-CC02 | [5 empty] | 6P X 0.75 OS FR | 205 |  | PS5-01-LB-0004 |  |  |  | UCP |  |  | PS5-03-SFMC-0012 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Gaseous Supression package interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
30 | PS5-01-LB-0004-CC03 | [5 empty] | 12P X 0.75 OS FR | 205 |  | PS5-01-LB-0004 |  |  |  | UCP |  |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; Gaseous Supression package interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
31 | PS5-01-LIT-4201-CJ01 | [5 empty] | 1P X 1.0 OS FR | 305 |  | PS5-01-LIT-4201 |  |  |  | Package Skid |  |  | PS5-03-SFMC-0007 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=1 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
32 | PS5-01-PIT-0014-CJ01 | [5 empty] | 1P X 1.0 OS FR | 305 |  | PS5-01-PIT-0014 |  |  |  | Field |  |  | PS5-03-SFMC-0007 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=1 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
33 | PS5-01-PIT-0015-CJ01 | [5 empty] | 1P X 1.0 OS FR | 275 |  | PS5-01-PIT-0015 |  |  |  | Field |  |  | PS5-03-SFMC-0007 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=1 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
34 | PS5-01-PIT-0016-CJ01 | [5 empty] | 1P X 1.0 OS FR | 350 |  | PS5-01-PIT-0016 |  |  |  | Field |  |  | PS5-03-SFMC-0008 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
35 | PS5-01-PIT-0017-CJ01 | [5 empty] | 1P X 1.0 OS FR | 115 |  | PS5-01-PIT-0017 |  |  |  | Field |  |  | PS5-03-SFMC-0008 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
36 | PS5-03-BI-1502-CC01 | [5 empty] | 6T X 2.5 IS/OS FR | 265 |  | PS5-03-RDIR-0405 |  | Instr:PS5-03-BI-1502, InstrLoc:Field, Branch:PS5-03-RDIR-0405-CJ01, Sz:1T X 1.5 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0007 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0063
37 | PS5-03-BI-1503-CC01 | [5 empty] | 12T X 2.5 IS/OS FR | 265 |  | PS5-03-RDIR-0403 |  | Instr:PS5-03-BI-1503, InstrLoc:Field, Branch:PS5-03-RDIR-0403-CJ01, Sz:1T X 1.5 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0008 |  |  |  | 33kV EITS Building | M50 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M50; A=0 B=2 C=1 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
38 | PS5-03-BI-1506-CC01 | [5 empty] | 24T X 2.5 IS/OS FR | 265 |  | PS5-03-RDIR-0122 |  | Instr:PS5-03-BI-1506, InstrLoc:Field, Branch:PS5-03-RDIR-0122-CJ01, Sz:1T X 1.5 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0008 |  |  |  | 33kV EITS Building | M63 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M63; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
39 | PS5-03-BI-1507-CC01 | [5 empty] | 12T X 2.5 IS/OS FR | 380 |  | PS5-03-RDIR-0104 |  | Instr:PS5-03-BI-1507, InstrLoc:Field, Branch:PS5-03-RDIR-0104-CJ01, Sz:1T X 1.5 OS FR, L:80m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0007 |  |  |  | 33kV EITS Building | M50 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M50; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-12-0045
40 | PS5-03-BI-1508-CC01 | [5 empty] | 12T X 2.5 IS/OS FR | 370 |  | PS5-03-RDIR-0108 |  | Instr:PS5-03-BI-1508, InstrLoc:Field, Branch:PS5-03-RDIR-0108-CJ01, Sz:1T X 1.5 OS FR, L:60m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0007 |  |  |  | 33kV EITS Building | M50 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M50; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
41 | PS5-03-BI-1509-CC01 | [5 empty] | 6T X 2.5 IS/OS FR | 330 |  | PS5-03-RDIR-0114 |  | Instr:PS5-03-BI-1509, InstrLoc:Field, Branch:PS5-03-RDIR-0114-CJ01, Sz:1T X 1.5 OS FR, L:80m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0007 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
42 | PS5-03-BI-1510-CC01 | [5 empty] | 6T X 2.5 IS/OS FR | 225 |  | PS5-03-RDIR-0819 |  | Instr:PS5-03-BI-1510, InstrLoc:Field, Branch:PS5-03-RDIR-0819-CJ01, Sz:1T X 1.5 OS FR, L:60m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0007 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0063
43 | PS5-03-BI-1511-CC01 | [5 empty] | 6T X 2.5 IS/OS FR | 305 |  | PS5-03-RDUIR-0701 |  | Instr:PS5-03-BI-1511, InstrLoc:Building, Branch:PS5-03-RDUIR-0701-CJ01, Sz:1T X 1.5 OS FR, L:55m, GlandS:M20, GlandD:M20 |  | Bldg | M20 |  | PS5-03-SFMC-0007 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=1 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
44 | PS5-03-BI-1512-CC01 | [5 empty] | 6T X 2.5 IS/OS FR | 305 |  | PS5-03-RDUIR-0907 |  | Instr:PS5-03-BI-1512, InstrLoc:Building, Branch:PS5-03-RDUIR-0907-CJ01, Sz:1T X 1.5 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Bldg | M20 |  | PS5-03-SFMC-0008 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=1 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
45 | PS5-03-BI-1513-CC01 | [5 empty] | 6T X 2.5 IS/OS FR | 305 |  | PS5-03-RDUIR-1007 |  | Instr:PS5-03-BI-1513, InstrLoc:Building, Branch:PS5-03-RDUIR-1007-CJ01, Sz:1T X 1.5 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Bldg | M20 |  | PS5-03-SFMC-0008 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-04-0054
46 | PS5-03-BI-1514-CC01 | [5 empty] | 6T X 2.5 IS/OS FR | 275 |  | PS5-03-RDUIR-1107 |  | Instr:PS5-03-BI-1514, InstrLoc:Building, Branch:PS5-03-RDUIR-1107-CJ01, Sz:1T X 1.5 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Bldg | M20 |  | PS5-03-SFMC-0008 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-04-0054
47 | PS5-03-BI-1516-CC01 | [5 empty] | 6T X 2.5 IS/OS FR | 225 |  | PS5-03-RDUIR-1208 |  | Instr:PS5-03-BI-1516, InstrLoc:Building, Branch:PS5-03-RDUIR-1208-CJ01, Sz:1T X 1.5 OS FR, L:60m, GlandS:M20, GlandD:M20 |  | Bldg | M20 |  | PS5-03-SFMC-0008 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=1 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0049
48 | PS5-03-BI-2501-CC01 | [5 empty] | 6P X 0.75 OS FR | 150 |  | PS5-03-RDH-0614 |  | Instr:PS5-03-BI-2501, InstrLoc:Field, Branch:PS5-03-RDH-0614-CJ01, Sz:1P X 1.0 OS FR, L:50m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0063
49 | PS5-03-BI-2502-CC01 | [5 empty] | 12P X 0.75 OS FR | 135 |  | PS5-03-RDH-0601 |  | Instr:PS5-03-BI-2502, InstrLoc:Field, Branch:PS5-03-RDH-0601-CJ01, Sz:1P X 1.0 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=1 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
50 | PS5-03-BI-2503-CC01 | [5 empty] | 12P X 0.75 OS FR | 115 |  | PS5-03-RDH-0607 |  | Instr:PS5-03-BI-2503, InstrLoc:Field, Branch:PS5-03-RDH-0607-CJ01, Sz:1P X 1.0 OS FR, L:55m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=1 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
51 | PS5-03-BI-2504-CC01 | [5 empty] | 6P X 0.75 OS FR | 370 |  | PS5-03-RMAC-0101 |  | Instr:PS5-03-BI-2504, InstrLoc:Field, Branch:PS5-03-RMAC-0101-CJ01, Sz:1P X 1.0 OS FR, L:80m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
52 | PS5-03-BI-2505-CC01 | [5 empty] | 6P X 0.75 OS FR | 275 |  | PS5-03-RDH-0828 |  | Instr:PS5-03-BI-2505, InstrLoc:Field, Branch:PS5-03-RDH-0828-CJ01, Sz:1P X 1.0 OS FR, L:150m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0063
53 | PS5-03-BI-2506-CC01 | [5 empty] | 12P X 0.75 OS FR | 305 |  | PS5-03-RDH-0901 |  | Instr:PS5-03-BI-2506, InstrLoc:Building, Branch:PS5-03-RDH-0901-CJ01, Sz:1P X 1.0 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Bldg | M20 |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
54 | PS5-03-BI-2507-CC01 | [5 empty] | 12P X 0.75 OS FR | 305 |  | PS5-03-RDH-1001 |  | Instr:PS5-03-BI-2507, InstrLoc:Building, Branch:PS5-03-RDH-1001-CJ01, Sz:1P X 1.0 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Bldg | M20 |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
55 | PS5-03-BI-2508-CC01 | [5 empty] | 12P X 0.75 OS FR | 275 |  | PS5-03-RDH-1101 |  | Instr:PS5-03-BI-2508, InstrLoc:Building, Branch:PS5-03-RDH-1101-CJ01, Sz:1P X 1.0 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Bldg | M20 |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0056
56 | PS5-03-BI-2509-CC01 | [5 empty] | 6P X 0.75 OS FR | 165 |  | PS5-03-RMAC-0401 |  | Instr:PS5-03-BI-2509, InstrLoc:Field, Branch:PS5-03-RMAC-0401-CJ01, Sz:1P X 1.0 OS FR, L:142m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
57 | PS5-03-BI-2510-CC01 | [5 empty] | 6P X 0.75 OS FR | 340 |  | PS5-03-RDH-0302 |  | Instr:PS5-03-BI-2510, InstrLoc:Field, Branch:PS5-03-RDH-0302-CJ01, Sz:1P X 1.0 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32 | 05
58 | PS5-03-BI-2511-CC01 | [5 empty] | 12P X 0.75 OS FR | 305 |  | PS5-03-GDLHP-0137 |  | Instr:PS5-03-BI-2511, InstrLoc:Field, Branch:PS5-03-GDLHP-0137-CJ01, Sz:1P X 1.0 OS FR, L:55m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
59 | PS5-03-BI-2512-CC01 | [5 empty] | 6P X 0.75 OS FR | 265 |  | PS5-03-GDLHP-0401 |  | Instr:PS5-03-BI-2512, InstrLoc:Field, Branch:PS5-03-GDLHP-0401-CJ01, Sz:1P X 1.0 OS FR, L:45m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=1 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
60 | PS5-03-BI-2514-CC01 | [5 empty] | 6P X 0.75 OS FR | 225 |  | PS5-03-RDH-1201 |  | Instr:PS5-03-BI-2514, InstrLoc:Building, Branch:PS5-03-RDH-1201-CJ01, Sz:1P X 1.0 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Bldg | M20 |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-04-0054
61 | PS5-03-BI-2515-CC01 | [5 empty] | 6P X 0.75 OS FR | 305 |  | PS5-03-RDH-1302 |  | Instr:PS5-03-BI-2515, InstrLoc:Building, Branch:PS5-03-RDH-1302-CJ01, Sz:1P X 1.0 OS FR, L:55m, GlandS:M20, GlandD:M20 |  | Bldg | M20 |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
62 | PS5-03-HS-7002-CJ01 | [5 empty] | 1P X 1.0 OS FR | 350 |  | PS5-03-HS-7002 |  |  |  | Field |  |  | PS5-03-SFMC-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=1 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
63 | PS5-03-NMR-0801-CJ01 | [5 empty] | 1P X 1.0 OS FR | 275 |  | PS5-03-NMR-0801 |  |  |  | Field |  |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=1 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
64 | PS5-03-NMR-0802-CJ01 | [5 empty] | 1P X 1.0 OS FR | 265 |  | PS5-03-NMR-0802 |  |  |  | Field |  |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-12-0056
65 | PS5-03-NMR-0803-CJ01 | [5 empty] | 1P X 1.0 OS FR | 245 |  | PS5-03-NMR-0803 |  |  |  | Field |  |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=1 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
66 | PS5-03-NMR-0804-CJ01 | [5 empty] | 1P X 1.0 OS FR | 225 |  | PS5-03-NMR-0804 |  |  |  | Field |  |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=1 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
67 | PS5-03-RMAC-0120-CJ01 | [5 empty] | 1P X 1.0 OS FR | 245 |  | PS5-03-RMAC-0120 |  |  |  | Field |  |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
68 | PS5-03-RMAC-0824-CJ01 | [5 empty] | 1P X 1.0 OS FR | 165 |  | PS5-03-RMAC-0824 |  |  |  | Field |  |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=1 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
69 | PS5-03-SEA-0002-CC01 | [5 empty] | 4P X 0.75 OS FR | 425 |  | PS5-03-SEA-0002 |  |  |  | Guard House Bldg FACP |  |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0055
70 | PS5-03-SEA-0002-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 425 |  | PS5-03-SEA-0002 |  |  |  | Guard House Bldg FACP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=1 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0037
71 | PS5-03-SEA-0003-CC01 | [5 empty] | 12P X 0.75 OS FR | 425 |  | PS5-03-SEA-0003 |  |  |  | Generator Control Bldg FACP |  |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=1 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
72 | PS5-03-SEA-0003-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 425 |  | PS5-03-SEA-0003 |  |  |  | Generator Control Bldg FACP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
73 | PS5-03-SEA-0005-CC01 | [5 empty] | 4P X 0.75 OS FR | 425 |  | PS5-03-SEA-0005 |  |  |  | Off Bldg FACP |  |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25 | 05
74 | PS5-03-SEA-0005-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 425 |  | PS5-03-SEA-0005 |  |  |  | Off Bldg FACP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20 | 05
75 | PS5-03-SEA-0006-CC01 | [5 empty] | 4P X 0.75 OS FR | 425 |  | PS5-03-SEA-0006 |  |  |  | Warehouse Bldg FACP |  |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
76 | PS5-03-SEA-0006-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 425 |  | PS5-03-SEA-0006 |  |  |  | Warehouse Bldg FACP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=1 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0037
77 | PS5-06-GU-0003A-CC01 | [5 empty] | 2P X 1.0 OS FR | 235 |  | PS5-06-GU-0003A |  |  |  | Generator Control Bldg |  |  | PS5-03-SFMC-0003 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen building UPS interface; A=0 B=2 C=0 | 06 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
78 | PS5-06-GU-0003B-CC01 | [5 empty] | 2P X 1.0 OS FR | 235 |  | PS5-06-GU-0003B |  |  |  | Generator Control Bldg |  |  | PS5-03-SFMC-0003 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen building UPS interface; A=0 B=2 C=0 | 06 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
79 | PS5-09-BI-2501-CC01 | [5 empty] | 12P X 0.75 OS FR | 425 |  | PS5-09-BI-2501 |  |  |  | Warehouse Bldg |  |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; Warehouse HVAC Damper Close Position Feedback; A=1 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0037
80 | PS5-09-BI-2502-CC01 | [5 empty] | 12P X 0.75 OS FR | 425 |  | PS5-09-BI-2502 |  |  |  | Off Bldg |  |  | PS5-03-SFMC-0011 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; Office HVAC Damper Close Position Feedback | 05
81 | PS5-09-BI-2504-CC01 | [5 empty] | 12P X 0.75 IS/OS FR | 425 |  | PS5-09-BI-2504 |  |  |  | Off Bldg |  |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; Office HVAC Damper Close Position Feedback | 06
82 | PS5-09-BI-2503-CC01 | [5 empty] | 24P X 0.75 OS FR | 425 |  | PS5-09-BI-2503 |  |  |  | Generator Control Bldg |  |  | PS5-03-SFMC-0011 |  |  |  | 33kV EITS Building | M50 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M50; Generator Bldg HVAC Damper Close Position Feedback; A=0 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
83 | PS5-09-LB-0006-CC01 | [5 empty] | 12P X 2.5 OS FR | 425 |  | PS5-09-LB-0006 |  |  |  | Off Bldg HCP |  |  | PS5-03-SFMC-0013 |  |  |  | 33kV EITS Building | M50 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M50; Office Bldg HVAC UCP interface | 05
84 | PS5-09-LB-0006-CC05 | [5 empty] | 12P X 0.75 IS/OS FR | 425 |  | PS5-09-LB-0006 |  |  |  | Off Bldg HCP |  |  | PS5-03-SFMC-0012 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; Office Bldg HVAC UCP interface | 06
85 | PS5-09-LB-0006-CC02 | [5 empty] | 4P X 0.75 OS FR | 425 |  | PS5-09-LB-0006 |  |  |  | Off Bldg HCP |  |  | PS5-03-SFMC-0011 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Office Bldg HVAC UCP interface | 05
86 | PS5-09-LB-0006-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 425 |  | PS5-09-LB-0006 |  |  |  | Off Bldg HCP |  |  | PS5-04-PMC-0003 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Office Bldg HVAC UCP interface | 05
87 | PS5-09-LB-0006-CC04 | [5 empty] | 2P X 1.0 OS FR | 410 |  | PS5-09-LB-0006 |  |  |  | Off Bldg HCP |  |  | PS5-03-SFMC-0011 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Office Bldg HVAC UCP interface | 06
88 | PS5-09-LB-0007-CC01 | [5 empty] | 12P X 2.5 OS FR | 425 |  | PS5-09-LB-0007 |  |  |  | Warehouse Bldg HCP |  |  | PS5-03-SFMC-0013 |  |  |  | 33kV EITS Building | M50 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M50; Warehouse Building HVAC UCP interface; A=1 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0037
89 | PS5-09-LB-0007-CC02 | [5 empty] | 4P X 0.75 OS FR | 425 |  | PS5-09-LB-0007 |  |  |  | Warehouse Bldg HCP |  |  | PS5-03-SFMC-0011 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Warehouse Building HVAC UCP interface; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
90 | PS5-09-LB-0007-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 425 |  | PS5-09-LB-0007 |  |  |  | Warehouse Bldg HCP |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Warehouse Building HVAC UCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0037
91 | PS5-09-LB-0007-CC04 | [5 empty] | 2P X 1.0 OS FR | 410 |  | PS5-09-LB-0007 |  |  |  | Warehouse Bldg HCP |  |  | PS5-03-SFMC-0011 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Warehouse Building HVAC UCP interface; A=1 B=2 C=0 | 06 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0037
92 | PS5-09-LB-0008-CC01 | [5 empty] | 24P X 2.5 OS FR | 425 |  | PS5-09-LB-0008 |  |  |  | Generator Control Bldg HCP |  |  | PS5-03-SFMC-0013 |  |  |  | 33kV EITS Building | M63 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M63; Powergen Building HVAC UCP interface; A=1 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
93 | PS5-09-LB-0008-CC02 | [5 empty] | 4P X 0.75 OS FR | 425 |  | PS5-09-LB-0008 |  |  |  | Generator Control Bldg HCP |  |  | PS5-03-SFMC-0011 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen Building HVAC UCP interface; A=1 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
94 | PS5-09-LB-0008-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 425 |  | PS5-09-LB-0008 |  |  |  | Generator Control Bldg HCP |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen Building HVAC UCP interface; A=0 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
95 | PS5-09-LB-0008-CC04 | [5 empty] | 2P X 1.0 OS FR | 410 |  | PS5-09-LB-0008 |  |  |  | Generator Control Bldg HCP |  |  | PS5-03-SFMC-0011 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen Building HVAC UCP interface; A=0 B=2 C=0 | 06 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
96 | PS5-09-LB-0008-CC05 | [5 empty] | 2P X 1.0 OS FR | 410 |  | PS5-09-LB-0008 |  |  |  | Generator Control Bldg HCP |  |  | PS5-03-SFMC-0012 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen Building HVAC UCP interface; A=0 B=2 C=0 | 06 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
97 | PS5-09-LB-0008-CC06 | [5 empty] | 2P X 1.0 OS FR | 410 |  | PS5-09-LB-0008 |  |  |  | Generator Control Bldg HCP |  |  | PS5-03-SFMC-0012 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen Building HVAC UCP interface; A=1 B=2 C=0 | 06 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
98 | PS5-09-LB-0008-CC07 | [5 empty] | 2P X 1.0 OS FR | 425 |  | PS5-09-LB-0008 |  |  |  | Generator Control Bldg HCP |  |  | PS5-03-SFMC-0012 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen Building HVAC UCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0056
99 | PS5-09-LB-0008-CC08 | [5 empty] | 2P X 1.0 OS FR | 425 |  | PS5-09-LB-0008 |  |  |  | Generator Control Bldg HCP |  |  | PS5-03-SFMC-0011 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen Building HVAC UCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0056
100 | PS5-25-BI-1101-CC01 | [5 empty] | 24P X 0.75 IS/OS FL RTD | 360 |  | PS5-25-FIT-0001 |  | Instr:PS5-25-BI-1101, InstrLoc:Field, Branch:PS5-25-FIT-0001-CJ01, Sz:1P X 1.0 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0001 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
101 | PS5-25-BI-1102-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 350 |  | PS5-25-ZIT-0001 |  | Instr:PS5-25-BI-1102, InstrLoc:Field, Branch:PS5-25-ZIT-0001-CC01, Sz:2P X 1.0 OS FL RTD, L:40m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-04-PMC-0002 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
102 | PS5-25-BI-1103-CC01 | [5 empty] | 24P X 0.75 IS/OS FL RTD | 330 |  | PS5-25-FIT-0003A |  | Instr:PS5-25-BI-1103, InstrLoc:Field, Branch:PS5-25-FIT-0003A-CJ01, Sz:1P X 1.0 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0001 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=3 C=1 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
103 | PS5-25-BI-1104-CC01 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 305 |  | PS5-25-FIT-0003C |  | Instr:PS5-25-BI-1104, InstrLoc:Field, Branch:PS5-25-FIT-0003C-CJ01, Sz:1P X 1.0 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0002 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
104 | PS5-25-BI-1115-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 350 |  | PS5-25-PIT-0013 |  | Instr:PS5-25-BI-1115, InstrLoc:Field, Branch:PS5-25-PIT-0013-CJ01, Sz:1P X 1.0 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0002 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
105 | PS5-25-BI-1201-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 360 |  | PS5-25-ESDV-0021 |  | Instr:PS5-25-BI-1201, InstrLoc:Field, Branch:PS5-25-ESDV-0021-CC01, Sz:2P X 1.0 OS FR, L:40m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-03-SFMC-0001 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
106 | PS5-25-BI-1301-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 370 |  | PS5-25-PIT-0008A |  | Instr:PS5-25-BI-1301, InstrLoc:Field, Branch:PS5-25-PIT-0008A-CJ01, Sz:1P X 1.0 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0002 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
107 | PS5-25-BI-1302-CC01 | [5 empty] | 24P X 0.75 IS/OS FR | 320 |  | PS5-25-TIT-0002A |  | Instr:PS5-25-BI-1302, InstrLoc:Field, Branch:PS5-25-TIT-0002A-CJ01, Sz:1P X 1.0 OS FR, L:65m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0002 |  |  |  | 33kV EITS Building | M50 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M50; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
108 | PS5-25-BI-1310-CC01 | [5 empty] | 24P X 0.75 IS/OS FR | 320 |  | PS5-25-TIT-0002C |  | Instr:PS5-25-BI-1310, InstrLoc:Field, Branch:PS5-25-TIT-0002C-CJ01, Sz:1P X 1.0 OS FR, L:50m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0002 |  |  |  | 33kV EITS Building | M50 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M50; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-04-0054/ CPP-RFI-68-64-11-0067
109 | PS5-25-BI-2101-CC01 | [5 empty] | 24P X 0.75 OS FL RTD | 360 |  | PS5-25-MOV-0001 |  | Instr:PS5-25-BI-2101, InstrLoc:Field, Branch:PS5-25-MXS-0001-CJ01, Sz:1P X 1.0 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0003 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
110 | PS5-25-BI-2102-CC01 | [5 empty] | 24P X 0.75 OS FL RTD | 395 |  | PS5-25-MOV-0008 |  | Instr:PS5-25-BI-2102, InstrLoc:Field, Branch:PS5-25-MXS-0008-CJ01, Sz:1P X 1.0 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0003 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
111 | PS5-25-BI-2103-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 395 |  | PS5-25-MOV-0026 |  | Instr:PS5-25-BI-2103, InstrLoc:Field, Branch:PS5-25-MOV-0026-CC01, Sz:6P X 0.75 OS FL RTD, L:40m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0046
112 | PS5-25-BI-2104-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 370 |  | PS5-25-XV-0053 |  | Instr:PS5-25-BI-2104, InstrLoc:Field, Branch:PS5-25-XV-0053-CC01, Sz:2P X 1.0 OS FL RTD, L:65m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-04-PMC-0003 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0046
113 | PS5-25-BI-2105-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 350 |  | PS5-25-XV-0053 |  | Instr:PS5-25-BI-2105, InstrLoc:Field, Branch:PS5-25-XXS-0053-CJ01, Sz:1P X 1.0 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0046
114 | PS5-25-BI-2106-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 330 |  | PS5-25-FCV-0003A |  | Instr:PS5-25-BI-2106, InstrLoc:Field, Branch:PS5-25-FXS-0003A-CJ01, Sz:1P X 1.0 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0046
115 | PS5-25-BI-2108-CC01 | [5 empty] | 12P X 2.5 OS FL RTD | 320 |  | PS5-25-SDV-0035C |  | Instr:PS5-25-BI-2108, InstrLoc:Field, Branch:PS5-25-SY-0035CB-CJ01, Sz:1P X 2.5 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0046
116 | PS5-25-BI-2109-CC01 | [5 empty] | 12P X 2.5 OS FL RTD | 320 |  | PS5-25-SDV-0035A |  | Instr:PS5-25-BI-2109, InstrLoc:Field, Branch:PS5-25-SY-0035AB-CJ01, Sz:1P X 2.5 OS FL RTD, L:70m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0046
117 | PS5-25-BI-2201-CC01 | [5 empty] | 6P X 0.75 OS FR | 360 |  | PS5-25-ESDV-0021 |  | Instr:PS5-25-BI-2201, InstrLoc:Field, Branch:PS5-25-ESDV-0021-CC02, Sz:2P X 1.0 OS FR, L:40m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-03-SFMC-0001 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0046
118 | PS5-25-BI-2203-CC01 | [5 empty] | 6P X 0.75 OS FR | 360 |  | PS5-25-ESDV-0021 |  | Instr:PS5-25-BI-2203, InstrLoc:Field, Branch:PS5-25-ESDV-0021-CC03, Sz:2P X 1.0 OS FR, L:40m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-03-SFMC-0001 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0046
119 | PS5-25-BI-2205-CC01 | [5 empty] | 6P X 2.5 OS FR | 360 |  | PS5-25-ESDV-0021 |  | Instr:PS5-25-BI-2205, InstrLoc:Field, Branch:PS5-25-ESY-0021A-CJ01, Sz:1P X 1.0 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0001 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
120 | PS5-25-BI-2301-CC01 | [5 empty] | 12P X 0.75 OS FR | 330 |  | PS5-25-SDV-0035A |  | Instr:PS5-25-BI-2301, InstrLoc:Field, Branch:PS5-25-SXS-0035A-CJ01, Sz:1P X 1.0 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0003 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0046
121 | PS5-25-BI-2302-CC01 | [5 empty] | 6P X 0.75 OS FR | 370 |  | PS5-25-SDV-0022 |  | Instr:PS5-25-BI-2302, InstrLoc:Field, Branch:PS5-25-SXS-0022-CJ01, Sz:1P X 1.0 OS FR, L:35m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0004 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0046
122 | PS5-25-BI-2305-CC01 | [5 empty] | 24P X 0.75 OS FR | 320 |  | PS5-25-SDV-0035A |  | Instr:PS5-25-BI-2305, InstrLoc:Field, Branch:PS5-25-SDV-0035A-CC01, Sz:2P X 1.0 OS FR, L:70m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-03-SFMC-0003 |  |  |  | 33kV EITS Building | M50 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M50; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0048
123 | PS5-25-BI-2308-CC01 | [5 empty] | 12P X 2.5 OS FR | 330 |  | PS5-25-SDV-0035A |  | Instr:PS5-25-BI-2308, InstrLoc:Field, Branch:PS5-25-SY-0035AA-CJ01, Sz:1P X 2.5 OS FR, L:50m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0005 |  |  |  | 33kV EITS Building | M50 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M50; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0048
124 | PS5-25-BI-2309-CC01 | [5 empty] | 6P X 2.5 OS FR | 360 |  | PS5-25-ESDV-0021 |  | Instr:PS5-25-BI-2309, InstrLoc:Field, Branch:PS5-25-ESY-0021B-CJ01, Sz:1P X 2.5 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0005 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0048
125 | PS5-25-BI-2312-CC01 | [5 empty] | 12P X 0.75 OS FR | 305 |  | PS5-25-SDV-0035C |  | Instr:PS5-25-BI-2312, InstrLoc:Field, Branch:PS5-25-SXS-0035C-CJ01, Sz:1P X 1.0 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0003 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0048
126 | PS5-25-BI-2315-CC01 | [5 empty] | 24P X 0.75 OS FR | 320 |  | PS5-25-SDV-0035C |  | Instr:PS5-25-BI-2315, InstrLoc:Field, Branch:PS5-25-SDV-0035C-CC01, Sz:2P X 1.0 OS FR, L:50m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-03-SFMC-0003 |  |  |  | 33kV EITS Building | M50 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M50; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0048
127 | PS5-25-BI-2316-CC01 | [5 empty] | 12P X 2.5 OS FR | 320 |  | PS5-25-SDV-0035C |  | Instr:PS5-25-BI-2316, InstrLoc:Field, Branch:PS5-25-SY-0035CA-CJ01, Sz:1P X 2.5 OS FR, L:50m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0006 |  |  |  | 33kV EITS Building | M50 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M50; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0048
128 | PS5-25-SHSR-0052-CJ01 | [5 empty] | 1P X 1.0 OS FR | 370 |  | PS5-25-SDV-0052 |  |  |  | Field |  |  | PS5-03-SFMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
129 | PS5-28-BI-1105-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 380 |  | PS5-28-PIT-0015 |  | Instr:PS5-28-BI-1105, InstrLoc:Field, Branch:PS5-28-PIT-0015-CJ01, Sz:1P X 1.0 OS FL RTD, L:50m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0001 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0048
130 | PS5-28-BI-1106-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 425 |  | PS5-28-LIT-1201 |  | Instr:PS5-28-BI-1106, InstrLoc:Field, Branch:PS5-28-LIT-1201-CJ01, Sz:1P X 1.0 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0001 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
131 | PS5-28-BI-1114-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 305 |  | PS5-28-TIT-1401 |  | Instr:PS5-28-BI-1114, InstrLoc:Field, Branch:PS5-28-TIT-1401-CJ01, Sz:1P X 1.0 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0001 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=1 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
132 | PS5-28-BI-1303-CC01 | [5 empty] | 12P X 0.75 IS/OS FR | 380 |  | PS5-28-LIT-1102 |  | Instr:PS5-28-BI-1303, InstrLoc:Field, Branch:PS5-28-LIT-1102-CJ01, Sz:1P X 1.0 OS FR, L:50m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0001 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0048
133 | PS5-28-BI-1307-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 225 |  | PS5-28-TIT-1402 |  | Instr:PS5-28-BI-1307, InstrLoc:Field, Branch:PS5-28-TIT-1402-CJ01, Sz:1P X 1.0 OS FR, L:65m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0001 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0048
134 | PS5-28-BI-2304-CC01 | [5 empty] | 6P X 0.75 OS FR | 350 |  | PS5-28-SDV-0045 |  | Instr:PS5-28-BI-2304, InstrLoc:Field, Branch:PS5-28-SDV-0045-CC01, Sz:2P X 1.0 OS FR, L:25m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-03-SFMC-0004 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
135 | PS5-28-HXA-1101-CJ01 | [5 empty] | 1P X 2.5 OS FL RTD | 395 |  | PS5-28-HXA-1101 |  |  |  | Field |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=1 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0037
136 | PS5-28-LB-8200-CC01 | [5 empty] | 2P X 1.0 OS FL RTD | 265 |  | PS5-28-LB-8200 |  |  |  | LP |  |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Open Drainage Interceptor panel interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
137 | PS5-28-LB-8200-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 265 |  | PS5-28-LB-8200 |  |  |  | LP |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Open Drainage Interceptor panel interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
138 | PS5-50-BI-1107-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 165 |  | PS5-28-LIT-0002 |  | Instr:PS5-50-BI-1107, InstrLoc:Field, Branch:PS5-28-LIT-0002-CJ01, Sz:1P X 1.0 OS FL RTD, L:90m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0002 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0048
139 | PS5-50-IE-0001-CC01 | [5 empty] | 2P X 1.0 OS FL RTD | 445 |  | PS5-50-IE-0001 |  |  |  | LP |  |  | PS5-04-PMC-0008 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Submersible Pump package interface; A=1 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
140 | PS5-50-IE-0001-CC02 | [5 empty] | 4P X 0.75 OS FL RTD | 445 |  | PS5-50-IE-0001 |  |  |  | LP |  |  | PS5-04-PMC-0007 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Submersible Pump package interface; A=1 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
141 | PS5-50-IE-0002-CC01 | [5 empty] | 2P X 1.0 OS FL RTD | 820 |  | PS5-50-IE-0002 |  |  |  | LP |  |  | PS5-04-PMC-0008 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Submersible Pump package interface; A=1 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0055
142 | PS5-50-IE-0002-CC02 | [5 empty] | 4P X 0.75 OS FL RTD | 820 |  | PS5-50-IE-0002 |  |  |  | LP |  |  | PS5-04-PMC-0007 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Submersible Pump package interface; A=2 B=1 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0055
143 | PS5-50-IE-0001-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 445 |  | PS5-50-LIT-0001 |  |  |  | LP |  |  | PS5-04-PMC-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Submersible Pump package interface; A=0 B=2 C=0 | 05
144 | PS5-50-IE-0002-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 820 |  | PS5-50-LIT-0002 |  |  |  | LP |  |  | PS5-04-PMC-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Submersible Pump package interface; A=2 B=1 C=0 | 05
145 | PS5-53-BI-1108-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 200 |  | PS5-53-LIT-4101 |  | Instr:PS5-53-BI-1108, InstrLoc:Field, Branch:PS5-53-LIT-4101-CJ01, Sz:1P X 1.0 OS FL RTD, L:90m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0002 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0048
146 | PS5-53-BI-1304-CC01 | [5 empty] | 2P X 1.0 IS/OS FR | 245 |  | PS5-53-LIT-4102 |  | Instr:PS5-53-BI-1304, InstrLoc:Field, Branch:PS5-53-LIT-4102-CJ01, Sz:1P X 1.0 OS FR, L:35m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0002 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=0 C=1 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
147 | PS5-53-LA-0001-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 225 |  | PS5-53-LA-0001 |  |  |  | UCP |  |  | PS5-04-PMC-0003 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Water Treatment package UCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0063
148 | PS5-53-LA-0001-CC02 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 225 |  | PS5-53-LA-0001 |  |  |  | UCP |  |  | PS5-04-PMC-0002 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Water Treatment package UCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0063
149 | PS5-60-IE-0003A-CC21 | [5 empty] | 1P X 1.0 OS FL RTD | 250 |  | PS5-60-IE-0003A |  |  |  | GCP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
150 | PS5-60-IE-0003A-CC22 | [5 empty] | 1P X 1.0 OS FL RTD | 250 |  | PS5-60-IE-0003A |  |  |  | GCP |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
151 | PS5-60-IE-0003A-CC23 | [5 empty] | 2P X 1.0 OS FR | 250 |  | PS5-60-IE-0003A |  |  |  | GCP |  |  | PS5-03-SFMC-0003 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
152 | PS5-60-IE-0003A-CC24 | [5 empty] | 2P X 1.0 OS FR | 250 |  | PS5-60-IE-0003A |  |  |  | GCP |  |  | PS5-03-SFMC-0005 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
153 | PS5-60-IE-0003B-CC21 | [5 empty] | 1P X 1.0 OS FL RTD | 250 |  | PS5-60-IE-0003B |  |  |  | GCP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
154 | PS5-60-IE-0003B-CC22 | [5 empty] | 1P X 1.0 OS FL RTD | 250 |  | PS5-60-IE-0003B |  |  |  | GCP |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
155 | PS5-60-IE-0003B-CC23 | [5 empty] | 2P X 1.0 OS FR | 250 |  | PS5-60-IE-0003B |  |  |  | GCP |  |  | PS5-03-SFMC-0003 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
156 | PS5-60-IE-0003B-CC24 | [5 empty] | 2P X 1.0 OS FR | 250 |  | PS5-60-IE-0003B |  |  |  | GCP |  |  | PS5-03-SFMC-0005 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
157 | PS5-60-IE-0003C-CC21 | [5 empty] | 1P X 1.0 OS FL RTD | 245 |  | PS5-60-IE-0003C |  |  |  | GCP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Powergen GCP interface; A=1 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
158 | PS5-60-IE-0003C-CC22 | [5 empty] | 1P X 1.0 OS FL RTD | 245 |  | PS5-60-IE-0003C |  |  |  | GCP |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Powergen GCP interface; A=1 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
159 | PS5-60-IE-0003C-CC23 | [5 empty] | 2P X 1.0 OS FR | 245 |  | PS5-60-IE-0003C |  |  |  | GCP |  |  | PS5-03-SFMC-0003 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0063
160 | PS5-60-IE-0003C-CC24 | [5 empty] | 2P X 1.0 OS FR | 245 |  | PS5-60-IE-0003C |  |  |  | GCP |  |  | PS5-03-SFMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
161 | PS5-60-IE-0003D-CC21 | [5 empty] | 1P X 1.0 OS FL RTD | 245 |  | PS5-60-IE-0003D |  |  |  | GCP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Powergen GCP interface; A=1 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
162 | PS5-60-IE-0003D-CC22 | [5 empty] | 1P X 1.0 OS FL RTD | 245 |  | PS5-60-IE-0003D |  |  |  | GCP |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Powergen GCP interface; A=1 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
163 | PS5-60-IE-0003D-CC23 | [5 empty] | 2P X 1.0 OS FR | 245 |  | PS5-60-IE-0003D |  |  |  | GCP |  |  | PS5-03-SFMC-0003 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
164 | PS5-60-IE-0003D-CC24 | [5 empty] | 2P X 1.0 OS FR | 245 |  | PS5-60-IE-0003D |  |  |  | GCP |  |  | PS5-03-SFMC-0005 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0056
165 | PS5-60-IE-0003E-CC21 | [5 empty] | 1P X 1.0 OS FL RTD | 245 |  | PS5-60-IE-0003E |  |  |  | GCP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Powergen GCP interface; A=1 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
166 | PS5-60-IE-0003E-CC22 | [5 empty] | 1P X 1.0 OS FL RTD | 245 |  | PS5-60-IE-0003E |  |  |  | GCP |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Powergen GCP interface; A=2 B=4 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0049
167 | PS5-60-IE-0003E-CC23 | [5 empty] | 2P X 1.0 OS FR | 245 |  | PS5-60-IE-0003E |  |  |  | GCP |  |  | PS5-03-SFMC-0003 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0063
168 | PS5-60-IE-0003E-CC24 | [5 empty] | 2P X 1.0 OS FR | 245 |  | PS5-60-IE-0003E |  |  |  | GCP |  |  | PS5-03-SFMC-0005 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0056
169 | PS5-60-IE-0003F-CC21 | [5 empty] | 1P X 1.0 OS FL RTD | 245 |  | PS5-60-IE-0003F |  |  |  | GCP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Powergen GCP interface; A=1 B=4 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
170 | PS5-60-IE-0003F-CC22 | [5 empty] | 1P X 1.0 OS FL RTD | 245 |  | PS5-60-IE-0003F |  |  |  | GCP |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0056
171 | PS5-60-IE-0003F-CC23 | [5 empty] | 2P X 1.0 OS FR | 245 |  | PS5-60-IE-0003F |  |  |  | GCP |  |  | PS5-03-SFMC-0004 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0063
172 | PS5-60-IE-0003F-CC24 | [5 empty] | 2P X 1.0 OS FR | 245 |  | PS5-60-IE-0003F |  |  |  | GCP |  |  | PS5-03-SFMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0056
173 | PS5-60-IE-0003G-CC21 | [5 empty] | 1P X 1.0 OS FL RTD | 245 |  | PS5-60-IE-0003G |  |  |  | GCP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0056
174 | PS5-60-IE-0003G-CC22 | [5 empty] | 1P X 1.0 OS FL RTD | 245 |  | PS5-60-IE-0003G |  |  |  | GCP |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0056
175 | PS5-60-IE-0003G-CC23 | [5 empty] | 2P X 1.0 OS FR | 245 |  | PS5-60-IE-0003G |  |  |  | GCP |  |  | PS5-03-SFMC-0004 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
176 | PS5-60-IE-0003G-CC24 | [5 empty] | 2P X 1.0 OS FR | 245 |  | PS5-60-IE-0003G |  |  |  | GCP |  |  | PS5-03-SFMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen GCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
177 | PS5-60-IE-0004-CC08 | [5 empty] | 24P X 0.75 OS FL RTD | 205 |  | PS5-60-IE-0004 |  |  |  | MCP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; Powergen MCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-04-0054
178 | PS5-60-IE-0004-CC11 | [5 empty] | 2P X 1.0 OS FR | 205 |  | PS5-60-IE-0004 |  |  |  | MCP |  |  | PS5-03-SFMC-0004 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen MCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
179 | PS5-60-IE-0004-CC12 | [5 empty] | 2P X 1.0 OS FR | 205 |  | PS5-60-IE-0004 |  |  |  | MCP |  |  | PS5-03-SFMC-0005 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Powergen MCP interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
180 | PS5-60-SEA-0001-CC18 | [5 empty] | 6P X 0.75 OS FR | 225 |  | PS5-60-SEA-0001 |  |  |  | UCP |  |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
181 | PS5-71-BI-1109-CC01 | [5 empty] | 24P X 0.75 IS/OS FL RTD | 265 |  | PS5-71-LIT-4101 |  | Instr:PS5-71-BI-1109, InstrLoc:Field, Branch:PS5-71-LIT-4101-CJ01, Sz:1P X 1.0 OS FL RTD, L:45m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0002 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=4 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0048
182 | PS5-71-BI-1110-CC01 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 245 |  | PS5-71-PDIT-0056B |  | Instr:PS5-71-BI-1110, InstrLoc:Field, Branch:PS5-71-PDIT-0056B-CJ01, Sz:1P X 1.0 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0001 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0048
183 | PS5-71-BI-1111-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 265 |  | PS5-71-FIT-0005 |  | Instr:PS5-71-BI-1111, InstrLoc:Field, Branch:PS5-71-FIT-0005-CJ01, Sz:1P X 1.0 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0002 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=3 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
184 | PS5-71-BI-1112-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 140 |  | PS5-71-FIT-0012 |  | Instr:PS5-71-BI-1112, InstrLoc:Field, Branch:PS5-71-FIT-0012-CJ01, Sz:1P X 1.0 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0002 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
185 | PS5-71-BI-1113-CC01 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 250 |  | PS5-71-FCV-0019 |  | Instr:PS5-71-BI-1113, InstrLoc:Field, Branch:PS5-71-FY-0019-CJ01, Sz:1P X 1.0 OS FL RTD, L:50m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0002 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
186 | PS5-71-BI-1116-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 245 |  | PS5-71-FCV-0018 |  | Instr:PS5-71-BI-1116, InstrLoc:Field, Branch:PS5-71-FY-0018-CJ01, Sz:1P X 1.0 OS FL RTD, L:25m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0002 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0048
187 | PS5-71-BI-1117-CC01 | [5 empty] | 2P X 1.0 OS FL RTD | 245 |  | PS5-71-XV-0089 |  | Instr:PS5-71-BI-1117, InstrLoc:Field, Branch:PS5-71-PIT-0089-CJ01, Sz:1P X 1.0 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0001 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=3 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
188 | PS5-71-BI-2101-CC01 | [5 empty] | 6P X 2.5 OS FL RTD | 245 |  | PS5-71-XV-0089 |  | Instr:PS5-71-BI-2101, InstrLoc:Field, Branch:PS5-71-XY-0089-CJ01, Sz:1P X 2.5 OS FL RTD, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=0 | 06
189 | PS5-71-BI-1305-CC01 | [5 empty] | 12P X 0.75 IS/OS FR | 265 |  | PS5-71-LIT-4102 |  | Instr:PS5-71-BI-1305, InstrLoc:Field, Branch:PS5-71-LIT-4102-CJ01, Sz:1P X 1.0 OS FR, L:45m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0002 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0048
190 | PS5-71-BI-1306-CC01 | [5 empty] | 12P X 0.75 IS/OS FR | 245 |  | PS5-71-LIT-4202 |  | Instr:PS5-71-BI-1306, InstrLoc:Field, Branch:PS5-71-LIT-4202-CJ01, Sz:1P X 1.0 OS FR, L:45m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0002 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0048
191 | PS5-71-BI-1308-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 265 |  | PS5-71-LIT-4402 |  | Instr:PS5-71-BI-1308, InstrLoc:Field, Branch:PS5-71-LIT-4402-CJ01, Sz:1P X 1.0 OS FR, L:60m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0001 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=1 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-12-0063
192 | PS5-71-BI-2107-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 245 |  | PS5-71-LCV-4101 |  | Instr:PS5-71-BI-2107, InstrLoc:Field, Branch:PS5-71-LXS-4101-CJ01, Sz:1P X 1.0 OS FL RTD, L:45m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0048
193 | PS5-71-BI-2113-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 250 |  | PS5-71-XV-0091 |  | Instr:PS5-71-BI-2113, InstrLoc:Field, Branch:PS5-71-XV-0091-CC01, Sz:2P X 1.0 OS FL RTD, L:50m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-04-PMC-0003 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
194 | PS5-71-BI-2114-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 250 |  | PS5-71-XV-0091 |  | Instr:PS5-71-BI-2114, InstrLoc:Field, Branch:PS5-71-XXS-0091-CJ01, Sz:1P X 1.0 OS FL RTD, L:50m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=3 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
195 | PS5-71-BI-2115-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 250 |  | PS5-71-XV-0091 |  | Instr:PS5-71-BI-2115, InstrLoc:Field, Branch:PS5-71-XY-0091-CJ01, Sz:1P X 1.0 OS FL RTD, L:50m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=3 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
196 | PS5-71-BI-2116-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 225 |  | PS5-71-XV-0089 |  | Instr:PS5-71-BI-2116, InstrLoc:Field, Branch:PS5-71-XV-0089-CC01, Sz:2P X 1.0 OS FL RTD, L:55m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-04-PMC-0003 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
197 | PS5-71-BI-2118-CC01 | [5 empty] | 24P X 0.75 OS FL RTD | 275 |  | PS5-71-MOV-0007 |  | Instr:PS5-71-BI-2118, InstrLoc:Field, Branch:PS5-71-MOV-0007-CC01, Sz:6P X 0.75 OS FL RTD, L:40m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=2 B=1 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0055
198 | PS5-71-BI-2119-CC01 | [5 empty] | 24P X 0.75 OS FL RTD | 225 |  | PS5-71-MOV-0009 |  | Instr:PS5-71-BI-2119, InstrLoc:Field, Branch:PS5-71-MOV-0009-CC01, Sz:6P X 0.75 OS FL RTD, L:40m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=2 B=1 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0055
199 | PS5-71-BI-2120-CC01 | [5 empty] | 24P X 0.75 OS FL RTD | 305 |  | PS5-71-MOV-0001 |  | Instr:PS5-71-BI-2120, InstrLoc:Field, Branch:PS5-71-MOV-0001-CC01, Sz:6P X 0.75 OS FL RTD, L:40m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=1 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0055
200 | PS5-71-BI-2121-CC01 | [5 empty] | 24P X 0.75 OS FL RTD | 305 |  | PS5-71-MOV-0003 |  | Instr:PS5-71-BI-2121, InstrLoc:Field, Branch:PS5-71-MOV-0003-CC01, Sz:6P X 0.75 OS FL RTD, L:40m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40; A=1 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-12-0055
201 | PS5-71-BI-2122-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 275 |  | PS5-71-MOV-0007 |  | Instr:PS5-71-BI-2122, InstrLoc:Field, Branch:PS5-71-MOV-0007-CC02, Sz:6P X 0.75 OS FL RTD, L:40m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
202 | PS5-71-BI-2123-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 225 |  | PS5-71-MOV-0009 |  | Instr:PS5-71-BI-2123, InstrLoc:Field, Branch:PS5-71-MOV-0009-CC02, Sz:6P X 0.75 OS FL RTD, L:40m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0035
203 | PS5-71-BI-2124-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 305 |  | PS5-71-MOV-0001 |  | Instr:PS5-71-BI-2124, InstrLoc:Field, Branch:PS5-71-MOV-0001-CC02, Sz:6P X 0.75 OS FL RTD, L:40m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
204 | PS5-71-BI-2125-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 305 |  | PS5-71-MOV-0003 |  | Instr:PS5-71-BI-2125, InstrLoc:Field, Branch:PS5-71-MOV-0003-CC02, Sz:6P X 0.75 OS FL RTD, L:40m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
205 | PS5-71-BI-2306-CC01 | [5 empty] | 6P X 0.75 OS FR | 245 |  | PS5-71-SDV-0022 |  | Instr:PS5-71-BI-2306, InstrLoc:Field, Branch:PS5-71-SDV-0022-CC01, Sz:2P X 1.0 OS FR, L:50m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-03-SFMC-0004 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=3 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
206 | PS5-71-BI-2307-CC01 | [5 empty] | 6P X 0.75 OS FR | 265 |  | PS5-71-SDV-0029 |  | Instr:PS5-71-BI-2307, InstrLoc:Field, Branch:PS5-71-SDV-0029-CC01, Sz:2P X 1.0 OS FR, L:25m, GlandS:M25, GlandD:M25 |  | Field | M25 |  | PS5-03-SFMC-0004 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=1 | 05 |  |  | CPP-RFI-68-64-12-0063
207 | PS5-71-BI-2310-CC01 | [5 empty] | 6P X 2.5 OS FR | 225 |  | PS5-71-SDV-0039 |  | Instr:PS5-71-BI-2310, InstrLoc:Field, Branch:PS5-71-SY-0039-CJ01, Sz:1P X 2.5 OS FR, L:45m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0006 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0045
208 | PS5-71-BI-2313-CC01 | [5 empty] | 6P X 0.75 OS FR | 265 |  | PS5-71-SDV-0029 |  | Instr:PS5-71-BI-2313, InstrLoc:Field, Branch:PS5-71-SXS-0029-CJ01, Sz:1P X 1.0 OS FR, L:25m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0004 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=1 | 05
209 | PS5-71-BI-2314-CC01 | [5 empty] | 6P X 0.75 OS FR | 245 |  | PS5-71-SDV-0022 |  | Instr:PS5-71-BI-2314, InstrLoc:Field, Branch:PS5-71-SXS-0022-CJ01, Sz:1P X 1.0 OS FR, L:40m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0004 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=1 B=4 C=1 | 05 |  | 2026-05-09 00:00:00 | CPP-RFI-68-64-12-0045
210 | PS5-71-BI-2317-CC01 | [5 empty] | 6P X 2.5 OS FR | 265 |  | PS5-71-SDV-0029 |  | Instr:PS5-71-BI-2317, InstrLoc:Field, Branch:PS5-71-SY-0029-CJ01, Sz:1P X 2.5 OS FR, L:25m, GlandS:M20, GlandD:M20 |  | Field | M20 |  | PS5-03-SFMC-0006 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=1 | 05 |  |  | CPP-RFI-68-64-12-0063
211 | PS5-71-IN-0001-CC08 | [5 empty] | 1P X 1.0 OS FL RTD | 205 |  | PS5-71-IN-0001 |  |  |  | UCP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; DFO Seperator panel interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
212 | PS5-71-IN-0001-CC09 | [5 empty] | 2P X 1.0 OS FR | 205 |  | PS5-71-IN-0001 |  |  |  | UCP |  |  | PS5-03-SFMC-0004 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; DFO Seperator panel interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
213 | PS5-71-IN-0001-CC10 | [5 empty] | 2P X 1.0 OS FR | 205 |  | PS5-71-IN-0001 |  |  |  | UCP |  |  | PS5-03-SFMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; DFO Seperator panel interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
214 | PS5-71-IN-0002-CC05 | [5 empty] | 1P X 1.0 OS FL RTD | 200 |  | PS5-71-IN-0002 |  |  |  | UCP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; CFO Pre-pressure panel interface; A=0 B=2 C=0 | 05 |  | 2026-04-17 00:00:00 | CPP-RFI-68-64-04-0038
215 | PS5-71-IN-0002-CC06 | [5 empty] | 2P X 1.0 OS FR | 200 |  | PS5-71-IN-0002 |  |  |  | UCP |  |  | PS5-03-SFMC-0004 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; CFO Pre-pressure panel interface; A=0 B=2 C=0 | 05 |  | 2026-04-17 00:00:00 | CPP-RFI-68-64-04-0038
216 | PS5-71-IN-0002-CC07 | [5 empty] | 2P X 1.0 OS FR | 200 |  | PS5-71-IN-0002 |  |  |  | UCP |  |  | PS5-03-SFMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; CFO Pre-pressure panel interface; A=0 B=2 C=0 | 05 |  | 2026-04-17 00:00:00 | CPP-RFI-68-64-04-0038
217 | PS5-71-IN-0003-CC05 | [5 empty] | 1P X 1.0 OS FL RTD | 200 |  | PS5-71-IN-0003 |  |  |  | UCP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; DFO Pre-pressure panel interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
218 | PS5-71-IN-0003-CC06 | [5 empty] | 2P X 1.0 OS FR | 200 |  | PS5-71-IN-0003 |  |  |  | UCP |  |  | PS5-03-SFMC-0004 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; DFO Pre-pressure panel interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
219 | PS5-71-IN-0003-CC07 | [5 empty] | 2P X 1.0 OS FR | 200 |  | PS5-71-IN-0003 |  |  |  | UCP |  |  | PS5-03-SFMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; DFO Pre-pressure panel interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
220 | PS5-71-IN-0004A-CC08 | [5 empty] | 1P X 1.0 OS FL RTD | 200 |  | PS5-71-IN-0004A |  |  |  | UCP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; CFO Separator Panel interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
221 | PS5-71-IN-0004A-CC09 | [5 empty] | 1P X 1.0 OS FR | 200 |  | PS5-71-IN-0004A |  |  |  | UCP |  |  | PS5-03-SFMC-0003 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; CFO Separator Panel interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
222 | PS5-71-IN-0004A-CC12 | [5 empty] | 1P X 1.0 OS FR | 200 |  | PS5-71-IN-0004A |  |  |  | UCP |  |  | PS5-03-SFMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; CFO Separator Panel interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
223 | PS5-71-IN-0004B-CC08 | [5 empty] | 1P X 1.0 OS FL RTD | 205 |  | PS5-71-IN-0004B |  |  |  | UCP |  |  | PS5-04-PMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; CFO Separator Panel interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
224 | PS5-71-IN-0004B-CC09 | [5 empty] | 1P X 1.0 OS FR | 205 |  | PS5-71-IN-0004B |  |  |  | UCP |  |  | PS5-03-SFMC-0003 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; CFO Separator Panel interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
225 | PS5-71-IN-0004B-CC12 | [5 empty] | 1P X 1.0 OS FR | 205 |  | PS5-71-IN-0004B |  |  |  | UCP |  |  | PS5-03-SFMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; CFO Separator Panel interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
226 | PS5-75-BI-1177-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 425 |  | PS5-75-BI-1177 |  |  |  | Package Skid |  |  | PS5-04-PMC-0002 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Biocide Injection package interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
227 | PS5-75-BI-1178-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 415 |  | PS5-75-BI-1178 |  |  |  | Package Skid |  |  | PS5-04-PMC-0002 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Corrosion Inhibitor package interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
228 | PS5-75-BI-1371-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 425 |  | PS5-75-BI-1371 |  |  |  | Package Skid |  |  | PS5-03-SFMC-0002 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Biocide Injection package interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
229 | PS5-75-BI-1372-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 415 |  | PS5-75-BI-1372 |  |  |  | Package Skid |  |  | PS5-03-SFMC-0002 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Corrosion Inhibitor package interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
230 | PS5-75-BI-0001-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 445 |  | PS5-75-BI-0001 |  |  |  | Skid |  |  | PS5-04-PMC-0001 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; DRA Injection package interface; A=0 B=1 C=0 | 07 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
231 | PS5-75-BI-0002-CC01 | [5 empty] | 4P X 0.75 OS FL RTD | 445 |  | PS5-75-BI-0002 |  |  |  | Skid |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; DRA Injection package interface; A=0 B=2 C=0 | 07 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
232 | PS5-75-BI-0002-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 445 |  | PS5-75-BI-0002 |  |  |  | Skid |  |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; DRA Injection package interface; A=0 B=1 C=0 | 07 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
233 | PS5-75-BI-0002-CC03 | [5 empty] | 4P X 0.75 OS FR | 445 |  | PS5-75-BI-0002 |  |  |  | Skid |  |  | PS5-03-SFMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; DRA Injection package interface; A=0 B=2 C=0 | 07 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-12-0056
234 | PS5-75-MOV-0001-CC01 | [5 empty] | 4P X 0.75 OS FL RTD | 415 |  | PS5-75-MOV-0001 |  |  |  | Field |  |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=1 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
235 | PS5-75-MOV-0001-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 415 |  | PS5-75-MOV-0001 |  |  |  | Field |  |  | PS5-04-PMC-0003 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=1 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
236 | PS5-79-IG-0001-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 200 |  | PS5-79-XA-0001 |  |  |  | Field |  |  | PS5-04-PMC-0003 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
237 | PS5-79-IG-0002-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 200 |  | PS5-79-XA-0002 |  |  |  | Field |  |  | PS5-04-PMC-0003 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
238 | PS5-79-IG-0003-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 275 |  | PS5-79-XA-0003 |  |  |  | Field |  |  | PS5-04-PMC-0003 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
239 | PS5-79-IG-0004-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 305 |  | PS5-79-XA-0004 |  |  |  | Field |  |  | PS5-04-PMC-0003 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
240 | PS5-79-IG-0005-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 305 |  | PS5-79-XA-0005 |  |  |  | Field |  |  | PS5-04-PMC-0003 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
241 | PS5-79-IG-0006-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 305 |  | PS5-79-XA-0006 |  |  |  | Field |  |  | PS5-04-PMC-0003 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
242 | PS5-79-IG-0007-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 305 |  | PS5-79-XA-0007 |  |  |  | Field |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
243 | PS5-79-IG-0008-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 320 |  | PS5-79-XA-0008 |  |  |  | Field |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
244 | PS5-79-IG-0009-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 320 |  | PS5-79-XA-0009 |  |  |  | Field |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
245 | PS5-79-IG-0010-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 320 |  | PS5-79-XA-0010 |  |  |  | Field |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
246 | PS5-79-IG-0011-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 40 |  | PS5-79-XA-0011 |  |  |  | Field |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
247 | PS5-79-IG-0012-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 445 |  | PS5-79-XA-0012 |  |  |  | Field |  |  | PS5-04-PMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
248 | PS5-71-TIT-2403A-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 275 |  | PS5-71-TIT-2403A |  |  |  | Field |  |  | PS5-71-IE-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-60-TUL1-150007 |  | GlandSrc:M20; Heater Temp Transmitter to Thyristor panel; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
249 | PS5-71-TIT-2403B-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 275 |  | PS5-71-TIT-2403B |  |  |  | Field |  |  | PS5-71-IE-0002 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-60-TUL1-150007 |  | GlandSrc:M20; Heater Temp Transmitter to Thyristor panel; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
250 | PS5-05-BI-0002-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M32 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M32; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
251 | PS5-05-BI-0002-CC02 | [5 empty] | 2P X 1.0 OS FR | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M25 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M25; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
252 | PS5-05-IE-8101-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M32 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M32; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
253 | PS5-05-BI-0002-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M20 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M20; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
254 | PS5-05-BI-0002-CJ02 | [5 empty] | 1P X 1.0 OS FL RTD | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M20 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M20; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
255 | PS5-05-BI-0002-CC05 | [5 empty] | RS485 MODBUS | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M25 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M25; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0050
256 | PS5-05-GC-8100-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M32 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M32; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
257 | PS5-05-LIT-4101-CJ01 | [5 empty] | 1P X 1.0 OS FR | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M20 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M20; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
258 | PS5-05-UH-8100-CC01 | [5 empty] | 2P X 1.0 OS FL RTD | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M25 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M25; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
259 | PS5-05-BI-0002-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M25 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M25; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0049
260 | PS5-05-UH-8100-CC02 | [5 empty] | 6P X 0.75 IS/OS FR | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M32 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M32; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0049
261 | PS5-05-BI-0002-CJ03 | [5 empty] | 1P X 2.5 OS FL RTD | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M20 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M20; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
262 | PS5-03-SEA-0001-CC01 | [5 empty] | 12P X 0.75 OS FR | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M40 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M40; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0049
263 | PS5-05-BI-0002-CC06 | [5 empty] | RS485 MODBUS | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M25 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M25; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0050
264 | PS5-05-BI-0002-CC04 | [5 empty] | 24P X 0.75 OS FL RTD | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M40 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M40; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
265 | PS5-05-IG-0009-CC01 | [5 empty] | 24P X 0.75 OS FL RTD | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M40 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M40; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
266 | PS5-05-IG-0009-CC02 | [5 empty] | 24P X 0.75 OS FL RTD | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M40 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M40; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
267 | PS5-05-IG-0009-CJ01 | [5 empty] | 1P X 1.0 OS FR | 330 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-05-IE-8100 |  |  |  | Generator Control Building | M20 |  |  | TZ-MID-60-UTR2-160007 |  | GlandSrc:M20; EDG Skid and GCP interface cable; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
268 | PS5-05-BI-0002-CC11 | [5 empty] | 6P X 0.75 OS FR | 175 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-03-SFMC-0009 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
269 | PS5-05-BI-0002-CC12 | [5 empty] | 2P X 1.0 OS FR | 175 |  | PS5-05-BI-0002 |  |  |  | Field |  |  | PS5-03-SFMC-0011 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
270 | PS5-05-IE-8100-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 205 |  | PS5-05-IE-8100 |  |  |  | Generator Control Bldg |  |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; A=0 B=2 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0049
271 | PS5-05-IE-8100-CC02 | [5 empty] | 2P X 1.0 OS FR | 205 |  | PS5-05-IE-8100 |  |  |  | Generator Control Bldg |  |  | PS5-03-SFMC-0003 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
272 | PS5-03-MTX-0001-CC01 | [5 empty] | 6P X 0.75 OS FR | 425 |  | PS5-03-MTX-0001 |  |  |  | Off Bldg |  |  | PS5-03-SFMC-0001 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32 | 05
273 | PS5-03-MTX-0001-CC02 | [5 empty] | 1P X 1.0 OS FR | 425 |  | PS5-03-MTX-0001 |  |  |  | Off Bldg |  |  | PS5-03-SFMC-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20 | 05
274 | PS5-03-MTX-0001-CC03 | [5 empty] | 1P X 1.0 OS FR | 425 |  | PS5-03-MTX-0001 |  |  |  | Off Bldg |  |  | PS5-03-SFMC-0004 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20 | 05
275 | PS5-03-MTX-0001-CC04 | [5 empty] | 2P X 1.0 OS FR | 425 |  | PS5-03-MTX-0001 |  |  |  | Off Bldg |  |  | PS5-03-SFMC-0005 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25 | 05
276 | PS5-03-MTX-0001-CC05 | [5 empty] | 12P X 0.75 OS FR | 425 |  | PS5-03-MTX-0001 |  |  |  | Off Bldg |  |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40 | 05
277 | PS5-03-MTX-0001-CC06 | [5 empty] | 12P X 0.75 OS FR | 425 |  | PS5-03-MTX-0001 |  |  |  | Off Bldg |  |  | PS5-03-SFMC-0011 |  |  |  | 33kV EITS Building | M40 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M40 | 05
278 | PS5-03-MTX-0001-CC07 | [5 empty] | 24P X 0.75 OS FR | 425 |  | PS5-03-MTX-0001 |  |  |  | Off Bldg |  |  | PS5-03-SFMC-0011 |  |  |  | 33kV EITS Building | M50 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M50 | 05
279 | PS5-03-MTX-0001-CC08 | [5 empty] | 24P X 0.75 OS FR | 425 |  | PS5-03-MTX-0001 |  |  |  | Off Bldg |  |  | PS5-03-SFMC-0012 |  |  |  | 33kV EITS Building | M50 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M50 | 05
280 | PS5-25-BI-1174A-CC01 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 370 |  | PS5-25-BI-1174A |  |  |  | Package Skid |  |  | PS5-04-PMC-0001 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Export Pump VFD Cabinet interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
281 | PS5-25-BI-1174B-CC01 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 360 |  | PS5-25-BI-1174B |  |  |  | Package Skid |  |  | PS5-04-PMC-0001 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Export Pump VFD Cabinet interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
282 | PS5-25-BI-1174C-CC01 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 350 |  | PS5-25-BI-1174C |  |  |  | Package Skid |  |  | PS5-04-PMC-0001 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Export Pump VFD Cabinet interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
283 | PS5-25-BI-1274A-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 370 |  | PS5-25-BI-1274A |  |  |  | Package Skid |  |  | PS5-03-SFMC-0002 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Export Pump VFD Cabinet interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
284 | PS5-25-BI-1274B-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 360 |  | PS5-25-BI-1274B |  |  |  | Package Skid |  |  | PS5-03-SFMC-0002 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Export Pump VFD Cabinet interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
285 | PS5-25-BI-1274C-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 350 |  | PS5-25-BI-1274C |  |  |  | Package Skid |  |  | PS5-03-SFMC-0001 |  |  |  | 33kV EITS Building | M32 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M32; Export Pump VFD Cabinet interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
286 | PS5-61-IDH-3100A-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 165 |  | PS5-61-IDH-3100A |  |  |  | E-House |  |  | PS5-04-PMC-0001 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Export Pump VFD Cabinet interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
287 | PS5-61-IDH-3100A-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 165 |  | PS5-61-IDH-3100A |  |  |  | E-House |  |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Export Pump VFD Cabinet interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
288 | PS5-61-IDH-3100A-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 165 |  | PS5-61-IDH-3100A |  |  |  | E-House |  |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Export Pump VFD Cabinet interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
289 | PS5-61-IDH-3100B-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 175 |  | PS5-61-IDH-3100B |  |  |  | E-House |  |  | PS5-04-PMC-0001 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Export Pump VFD Trip; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
290 | PS5-61-IDH-3100B-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 175 |  | PS5-61-IDH-3100B |  |  |  | E-House |  |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Export Pump VFD Trip; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-12-0056
291 | PS5-61-IDH-3100B-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 175 |  | PS5-61-IDH-3100B |  |  |  | E-House |  |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Export Pump VFD Trip; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-12-0056
292 | PS5-61-IDH-3100C-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 175 |  | PS5-61-IDH-3100C |  |  |  | E-House |  |  | PS5-04-PMC-0002 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Export Pump VFD E-House LFAP interface; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-12-0056
293 | PS5-61-IDH-3100C-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 175 |  | PS5-61-IDH-3100C |  |  |  | E-House |  |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Export Pump VFD E-House LFAP interface; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-12-0056
294 | PS5-61-IDH-3100C-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 175 |  | PS5-61-IDH-3100C |  |  |  | E-House |  |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Export Pump VFD E-House LFAP interface | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
295 | PS5-25-MXS-3101AA-CJ01 | [5 empty] | 1P X 1.0 OS FR | 165 |  | PS5-61-IDH-3100A |  |  |  | E-House |  |  | PS5-03-SFMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Export Pump VFD E-House HVAC interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
296 | PS5-25-MXS-3101BA-CJ01 | [5 empty] | 1P X 1.0 OS FR | 175 |  | PS5-61-IDH-3100B |  |  |  | E-House |  |  | PS5-03-SFMC-0005 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Export Pump VFD E-House HVAC interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
297 | PS5-25-MXS-3101CA-CJ01 | [5 empty] | 1P X 1.0 OS FR | 175 |  | PS5-61-IDH-3100C |  |  |  | E-House |  |  | PS5-03-SFMC-0006 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Export Pump VFD E-House HVAC interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
298 | PS5-83-EHO-0001A-CC01 | [5 empty] | 2P X 1.0 OS FR | 370 |  | PS5-83-EHO-0001A |  |  |  | E-House |  |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Export Pump to VTMS interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
299 | PS5-83-EHO-0001B-CC01 | [5 empty] | 2P X 1.0 OS FR | 360 |  | PS5-83-EHO-0001B |  |  |  | E-House |  |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Export Pump to VFD interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
300 | PS5-83-EHO-0001C-CC01 | [5 empty] | 2P X 1.0 OS FR | 350 |  | PS5-83-EHO-0001C |  |  |  | E-House |  |  | PS5-03-SFMC-0010 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M25; Export Pump to VTMS interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
301 | PS5-83-EHO-0001A-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 370 |  | PS5-83-EHO-0001A |  |  |  | E-House |  |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Export Pump to VTMS interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
302 | PS5-83-EHO-0001B-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 360 |  | PS5-83-EHO-0001B |  |  |  | E-House |  |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Export Pump to VTMS interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
303 | PS5-83-EHO-0001C-CJ01 | [5 empty] | 1P X 1.0 OS FL RTD | 350 |  | PS5-83-EHO-0001C |  |  |  | E-House |  |  | PS5-04-PMC-0006 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161503 |  | GlandSrc:M20; Export Pump to VTMS interface; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-12-0073
304 | PS5-25-BI-1801A-CC01 | [5 empty] | 12T X 0.75 IS/OS FR (IS) | 370 |  | PS5-25-BI-1801A |  |  |  | Package Skid |  |  | PS5-25-IE-0001 |  |  |  | 33kV EITS Building | M40 |  |  | UT-MID-63-SLZ1-160005 UT-MID-63-SLZ1-150024 |  | GlandSrc:M40; Export Pump to VFD interface; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-12-0046
305 | PS5-25-BI-1802A-CC01 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 370 |  | PS5-25-BI-1802A |  |  |  | Package Skid |  |  | PS5-61-IDH-3100A |  |  |  | E-House | M25 |  |  | UT-MID-63-SLZ1-160005 UT-MID-63-SLZ1-150025 |  | GlandSrc:M25; Export Pump to VTMS interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
306 | PS5-25-BI-1802A-CC02 | [5 empty] | 6T X 0.75 IS/OS FR | 370 |  | PS5-25-BI-1802A |  |  |  | Package Skid |  |  | PS5-25-IE-0001 |  |  |  | 33kV EITS Building | M32 |  |  | UT-MID-63-SLZ1-160005 UT-MID-63-SLZ1-150024 |  | GlandSrc:M32; Export Pump to VTMS interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0046
307 | PS5-25-BI-1803A-CC01 | [5 empty] | 6T X 0.75 IS/OS FR | 370 |  | PS5-25-BI-1803A |  |  |  | Package Skid |  |  | PS5-25-IE-0001 |  |  |  | 33kV EITS Building | M32 |  |  | UT-MID-63-SLZ1-160005 UT-MID-63-SLZ1-150024 |  | GlandSrc:M32; Export Pump to VTMS interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0046
308 | PS5-25-BI-1803A-CC02 | [5 empty] | 12T X 0.75 IS/OS FR | 370 |  | PS5-25-BI-1803A |  |  |  | Package Skid |  |  | PS5-25-IE-0001 |  |  |  | 33kV EITS Building | M40 |  |  | UT-MID-63-SLZ1-160005 UT-MID-63-SLZ1-150024 |  | GlandSrc:M40; Export Pump to VTMS interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0046
309 | PS5-25-BI-1801B-CC01 | [5 empty] | 12T X 0.75 IS/OS FR (IS) | 360 |  | PS5-25-BI-1801B |  |  |  | Package Skid |  |  | PS5-25-IE-0001 |  |  |  | 33kV EITS Building | M40 |  |  | UT-MID-63-SLZ1-160005 UT-MID-63-SLZ1-150024 |  | GlandSrc:M40; Export Pump to VFD interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0046
310 | PS5-25-BI-1802B-CC01 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 360 |  | PS5-25-BI-1802B |  |  |  | Package Skid |  |  | PS5-61-IDH-3100B |  |  |  | E-House | M25 |  |  | UT-MID-63-SLZ1-160005 UT-MID-63-SLZ1-150025 |  | GlandSrc:M25; Export Pump to VTMS interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
311 | PS5-25-BI-1802B-CC02 | [5 empty] | 6T X 0.75 IS/OS FR | 360 |  | PS5-25-BI-1802B |  |  |  | Package Skid |  |  | PS5-25-IE-0001 |  |  |  | 33kV EITS Building | M32 |  |  | UT-MID-63-SLZ1-160005 UT-MID-63-SLZ1-150024 |  | GlandSrc:M32; Export Pump to VTMS interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0046
312 | PS5-25-BI-1803B-CC01 | [5 empty] | 6T X 0.75 IS/OS FR | 360 |  | PS5-25-BI-1803B |  |  |  | Package Skid |  |  | PS5-25-IE-0001 |  |  |  | 33kV EITS Building | M32 |  |  | UT-MID-63-SLZ1-160005 UT-MID-63-SLZ1-150024 |  | GlandSrc:M32; Export Pump to VTMS interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0046
313 | PS5-25-BI-1803B-CC02 | [5 empty] | 12T X 0.75 IS/OS FR | 360 |  | PS5-25-BI-1803B |  |  |  | Package Skid |  |  | PS5-25-IE-0001 |  |  |  | 33kV EITS Building | M40 |  |  | UT-MID-63-SLZ1-160005 UT-MID-63-SLZ1-150024 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0046
314 | PS5-25-BI-1801C-CC01 | [5 empty] | 12T X 0.75 IS/OS FR (IS) | 350 |  | PS5-25-BI-1801C |  |  |  | Package Skid |  |  | PS5-25-IE-0001 |  |  |  | 33kV EITS Building | M40 |  |  | UT-MID-63-SLZ1-160005 UT-MID-63-SLZ1-150024 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0046
315 | PS5-25-BI-1802C-CC01 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 350 |  | PS5-25-BI-1802C |  |  |  | Package Skid |  |  | PS5-61-IDH-3100C |  |  |  | E-House | M25 |  |  | UT-MID-63-SLZ1-160005 UT-MID-63-SLZ1-150025 |  | GlandSrc:M25; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
316 | PS5-25-BI-1802C-CC02 | [5 empty] | 6T X 0.75 IS/OS FR | 350 |  | PS5-25-BI-1802C |  |  |  | Package Skid |  |  | PS5-25-IE-0001 |  |  |  | 33kV EITS Building | M32 |  |  | UT-MID-63-SLZ1-160005 UT-MID-63-SLZ1-150024 |  | GlandSrc:M32; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0046
317 | PS5-25-BI-1803C-CC01 | [5 empty] | 6T X 0.75 IS/OS FR | 350 |  | PS5-25-BI-1803C |  |  |  | Package Skid |  |  | PS5-25-IE-0001 |  |  |  | 33kV EITS Building | M32 |  |  | UT-MID-63-SLZ1-160005 UT-MID-63-SLZ1-150024 |  | GlandSrc:M32; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
318 | PS5-25-BI-1803C-CC02 | [5 empty] | 12T X 0.75 IS/OS FR | 350 |  | PS5-25-BI-1803C |  |  |  | Package Skid |  |  | PS5-25-IE-0001 |  |  |  | 33kV EITS Building | M40 |  |  | UT-MID-63-SLZ1-160005 UT-MID-63-SLZ1-150024 |  | GlandSrc:M40; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
319 | PS5-71-BI-0001-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 250 |  | PS5-71-BI-0001 |  |  |  | Package Skid |  |  | PS5-26-LA-0001 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-KBV1-160008 |  | GlandSrc:M25; CFO Allocation Metering Package; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
320 | PS5-71-BI-0021-CC01 | [5 empty] | 2P X 1.0 OS FL RTD | 250 |  | PS5-71-BI-0021 |  |  |  | Package Skid |  |  | PS5-26-LA-0001 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-KBV1-160008 |  | GlandSrc:M25; CFO Allocation Metering Package | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
321 | PS5-71-BI-0021-CC02 | [5 empty] | RS485 MODBUS | 250 |  | PS5-71-BI-0021 |  |  |  | Package Skid |  |  | PS5-26-LA-0001 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-KBV1-160008 |  | GlandSrc:M25; CFO Allocation Metering Package; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
322 | PS5-25-MXS-3101AB-CJ01 | [5 empty] | 1P X 1.0 OS FR | 165 |  | PS5-61-IDH-3100A |  |  |  | E-House |  |  | PS5-01-LA-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161000 |  | GlandSrc:M20; VFD Cabinet interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
323 | PS5-25-MXS-3101BB-CJ01 | [5 empty] | 1P X 1.0 OS FR | 175 |  | PS5-61-IDH-3100B |  |  |  | E-House |  |  | PS5-01-LA-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161000 |  | GlandSrc:M20; VFD Cabinet interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
324 | PS5-25-MXS-3101CB-CJ01 | [5 empty] | 1P X 1.0 OS FR | 175 |  | PS5-61-IDH-3100C |  |  |  | E-House |  |  | PS5-01-LA-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161000 |  | GlandSrc:M20; VFD Cabinet interface; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
325 | PS5-25-PIT-0052-CJ01 | [5 empty] | 1P X 1.0 OS FR | 370 |  | PS5-25-SDV-0052 |  |  |  | Field |  |  | PS5-01-LA-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161000 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
326 | PS5-25-PIT-0071A-CJ01 | [5 empty] | 1P X 1.0 OS FR | 395 |  | PS5-25-PIT-0071A |  |  |  | Field |  |  | PS5-01-LA-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161000 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
327 | PS5-25-PIT-0071B-CJ01 | [5 empty] | 1P X 1.0 OS FR | 395 |  | PS5-25-PIT-0071B |  |  |  | Field |  |  | PS5-01-LA-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161000 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
328 | PS5-25-PIT-0071C-CJ01 | [5 empty] | 1P X 1.0 OS FR | 395 |  | PS5-25-PIT-0071C |  |  |  | Field |  |  | PS5-01-LA-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161000 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
329 | PS5-25-SDV-0052-CC01 | [5 empty] | 2P X 1.0 OS FR | 370 |  | PS5-25-SDV-0052 |  |  |  | Field |  |  | PS5-01-LA-0001 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-WPR2-161000 |  | GlandSrc:M25; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-12-0055
330 | PS5-25-SXS-0052-CJ01 | [5 empty] | 1P X 1.0 OS FR | 370 |  | PS5-25-SDV-0052 |  |  |  | Field |  |  | PS5-01-LA-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161000 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
331 | PS5-25-SY-0052A-CJ01 | [5 empty] | 1P X 2.5 OS FR | 370 |  | PS5-25-SDV-0052 |  |  |  | Field |  |  | PS5-01-LA-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-WPR2-161000 |  | GlandSrc:M20; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
332 | PS5-25-SDV-0052-CJ01 | [5 empty] | RS485 MODBUS | 370 |  | PS5-25-SDV-0052IDC24 |  |  |  | Field |  |  | PS5-01-LA-0001 |  |  |  | 33kV EITS Building | M25 |  |  | TZ-MID-68-HPH1-160008 UT-MID-73-VLV1-160029 |  | GlandSrc:M25; A=0 B=2 C=0 | 05 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0038
333 | PS5-01-BI-0007-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 65 |  | PS5-01-BI-0007 |  |  |  | Package Skid |  |  | PS5-01-LB-0004 |  |  |  | Generator Control Building | M32 |  |  | TZ-MID-63-SAN1-160001 |  | GlandSrc:M32; Gaseous Suppression Package skid interface | 05
334 | PS5-01-BI-0008-CC01 | [5 empty] | 6P X 2.5 OS FR | 65 |  | PS5-01-BI-0008 |  |  |  | Package Skid |  |  | PS5-01-LB-0004 |  |  |  | Generator Control Building | M32 |  |  | TZ-MID-63-SAN1-160001 |  | GlandSrc:M32; Gaseous Suppression Package skid interface | 05
335 | PS5-01-BI-0009-CC01 | [5 empty] | 24P X 0.75 OS FR | 65 |  | PS5-01-BI-0009 |  |  |  | Package Skid |  |  | PS5-01-LB-0004 |  |  |  | Generator Control Building | M50 |  |  | TZ-MID-63-SAN1-160001 |  | GlandSrc:M50; Gaseous Suppression Package skid interface | 05
336 | PS5-09-LB-0008-CX01 | [5 empty] | 24C SM FIBER OPTIC FR | 225 |  | PS5-09-LB-0008 |  |  |  | Generator Control Bldg HCP |  |  | PS5-04-PNC-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-SSF1-161401 |  | GlandSrc:M20; HVAC UCP Interface. Cable supply by Telecoms; A=0 B=2 C=0 | 06 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-04-0054
337 | PS5-09-LB-0006-CX01 | [5 empty] | 24C SM FIBER OPTIC FR | 425 |  | PS5-09-LB-0006 |  |  |  | Off Bldg HCP |  |  | PS5-04-PNC-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-SSF1-161401 |  | GlandSrc:M20; HVAC UCP Interface. Cable supply by Telecoms | 06
338 | PS5-09-LB-0007-CX01 | [5 empty] | 24C SM FIBER OPTIC FR | 425 |  | PS5-09-LB-0007 |  |  |  | Warehouse Bldg HCP |  |  | PS5-04-PNC-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-SSF1-161401 |  | GlandSrc:M20; HVAC UCP Interface. Cable supply by Telecoms; A=1 B=2 C=0 | 06 |  | 2026-05-06 00:00:00 | CPP-RFI-68-64-04-0043
339 | PS5-60-IE-0004-CX03 | [5 empty] | 24C SM FIBER OPTIC FR | 205 |  | PS5-60-IE-0004 |  |  |  | Generator Control Bldg |  |  | PS5-04-PNC-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-SSF1-161401 |  | GlandSrc:M20; Powergen MCP and EDG Interface. Cable Supply by Telecoms; A=0 B=2 C=0 | 06 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-04-0054
340 | PS5-60-IE-0004-CX04 | [5 empty] | 24C SM FIBER OPTIC FR | 205 |  | PS5-60-IE-0004 |  |  |  | Generator Control Bldg |  |  | PS5-04-PNC-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-SSF1-161401 |  | GlandSrc:M20; Powergen MCP and EDG Interface. Cable Supply by Telecoms; A=0 B=2 C=0 | 06 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-04-0054
341 | PS5-60-LA-0003-CX01 | [5 empty] | 24C SM FIBER OPTIC FR | 205 |  | PS5-60-LA-0003 |  |  |  | Generator Control Bldg |  |  | PS5-04-PNC-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-SSF1-161401 |  | GlandSrc:M20; Powergen RAP and EDG Interface. Cable Supply by Telecoms | 06
342 | PS5-74-LB-5101-CX01 | [5 empty] | 24C SM FIBER OPTIC FR | 205 |  | PS5-74-LB-5101 |  |  |  | Package Skid |  |  | PS5-04-PNC-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-SSF1-161401 |  | GlandSrc:M20; Nitrogen Package Interface. Cable Supply by Telecoms; A=0 B=2 C=0 | 06 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
343 | PS5-82-LA-0001-CX01 | [5 empty] | 24C SM FIBER OPTIC FR | 395 |  | PS5-82-LA-0001 |  |  |  | Package Skid |  |  | PS5-04-PNC-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-SSF1-161401 |  | GlandSrc:M20; Sewage Treament Package interface. Cable Supply by Telecoms; A=0 B=2 C=0 | 06 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0037
344 | PS5-53-LA-0001-CX01 | [5 empty] | 24C SM FIBER OPTIC FR | 225 |  | PS5-53-LA-0001 |  |  |  | Package Skid |  |  | PS5-04-PNC-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-SSF1-161401 |  | GlandSrc:M20; Water Treatment package interface. Cable Supply by Telecoms; A=0 B=2 C=0 | 06 |  | 2026-04-16 00:00:00 | CPP-RFI-68-64-04-0036
345 | PS5-60-IN-0001A-CA01 | [5 empty] | CAT 6A OUTDOOR | 133 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001A |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
346 | PS5-60-IN-0001B-CA01 | [5 empty] | CAT 6A OUTDOOR | 129 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
347 | PS5-60-IN-0001C-CA01 | [5 empty] | CAT 6A OUTDOOR | 120 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001C |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
348 | PS5-60-IN-0001D-CA01 | [5 empty] | CAT 6A OUTDOOR | 115 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001D |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
349 | PS5-60-IN-0001E-CA01 | [5 empty] | CAT 6A OUTDOOR | 106 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001E |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
350 | PS5-60-IN-0001F-CA01 | [5 empty] | CAT 6A OUTDOOR | 97 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001F |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
351 | PS5-60-IN-0001G-CA01 | [5 empty] | CAT 6A OUTDOOR | 92 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001G |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
352 | PS5-60-IE-0003B-CA03 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
353 | PS5-60-IE-0003B-CA04 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
354 | PS5-60-IE-0003B-CA05 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
355 | PS5-60-IE-0003C-CA03 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003C |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
356 | PS5-60-IE-0003C-CA04 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003C |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
357 | PS5-60-IE-0003C-CA05 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003C |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
358 | PS5-60-IE-0003D-CA03 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003D |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
359 | PS5-60-IE-0003D-CA04 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003D |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
360 | PS5-60-IE-0003D-CA05 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003D |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
361 | PS5-60-IE-0003E-CA03 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003E |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
362 | PS5-60-IE-0003E-CA04 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003E |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
363 | PS5-60-IE-0003E-CA05 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003E |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
364 | PS5-60-IE-0003F-CA03 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003F |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
365 | PS5-60-IE-0003F-CA04 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003F |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
366 | PS5-60-IE-0003F-CA05 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003F |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
367 | PS5-60-IE-0003G-CA03 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003G |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
368 | PS5-60-IE-0003G-CA04 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003G |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
369 | PS5-60-IE-0003G-CA05 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003G |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
370 | PS5-60-IE-0004-CA01 | [5 empty] | CAT 6A INDOOR | 40 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
371 | PS5-60-IE-0004-CA07 | [5 empty] | CAT 6A INDOOR | 45 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
372 | PS5-60-IE-0004-CA08 | [5 empty] | CAT 6A INDOOR | 40 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
373 | PS5-60-IE-0004-CA14 | [5 empty] | CAT 6A INDOOR | 45 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
374 | PS5-60-IE-0004-CA15 | [5 empty] | CAT 6A INDOOR | 40 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
375 | PS5-60-IE-0004-CA21 | [5 empty] | CAT 6A INDOOR | 45 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
376 | PS5-60-IN-0002A-CA01 | [5 empty] | CAT 6A OUTDOOR | 120 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002A |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
377 | PS5-60-IN-0002B-CA01 | [5 empty] | CAT 6A OUTDOOR | 115 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
378 | PS5-60-IN-0002C-CA01 | [5 empty] | CAT 6A OUTDOOR | 106 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002C |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
379 | PS5-60-IN-0002D-CA01 | [5 empty] | CAT 6A OUTDOOR | 101 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002D |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
380 | PS5-60-IN-0002E-CA01 | [5 empty] | CAT 6A OUTDOOR | 92 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002E |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
381 | PS5-60-IN-0002F-CA01 | [5 empty] | CAT 6A OUTDOOR | 83 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002F |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
382 | PS5-60-IN-0002G-CA01 | [5 empty] | CAT 6A OUTDOOR | 83 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002G |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
383 | PS5-60-LA-0002B-CA01 | [5 empty] | CAT 6A INDOOR | 20 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
384 | PS5-60-LA-0002B-CA02 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-LA-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
385 | PS5-60-LA-0002B-CA03 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-LA-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
386 | PS5-60-LA-0002B-CA04 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-LA-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
387 | PS5-60-LA-0002B-CA05 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-LA-0002C |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
388 | PS5-60-LA-0002B-CA06 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-LA-0002C |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
389 | PS5-60-LA-0002C-CA01 | [5 empty] | CAT 6A INDOOR | 20 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002C |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
390 | PS5-60-LA-0002C-CA02 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-LA-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002C |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
391 | PS5-60-LA-0002C-CA03 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-LA-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002C |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
392 | PS5-60-LA-0002C-CA04 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-LA-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002C |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
393 | PS5-60-LA-0002C-CA05 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-LA-0002B |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002C |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
394 | PS5-60-LA-0002C-CA06 | [5 empty] | CAT 6A INDOOR | 15 |  | PS5-60-LA-0002B |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002C |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
395 | PS5-60-SEA-0001-CA01 | [5 empty] | CAT 6A INDOOR | 40 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
396 | PS5-71-IN-0001-CA01 | [5 empty] | CAT 6A INDOOR | 25 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
397 | PS5-71-IN-0002-CA01 | [5 empty] | CAT 6A INDOOR | 20 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0002 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
398 | PS5-71-IN-0003-CA01 | [5 empty] | CAT 6A INDOOR | 25 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0003 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
399 | PS5-71-IN-0004A-CA01 | [5 empty] | CAT 6A INDOOR | 25 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0004A |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
400 | PS5-71-IN-0004B-CA01 | [5 empty] | CAT 6A INDOOR | 25 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0004B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
401 | PS5-60-IN-0001A-CC02 | [5 empty] | 1P X 1.0 OS FL RTD | 155 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001A |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
402 | PS5-60-IN-0001B-CC02 | [5 empty] | 1P X 1.0 OS FL RTD | 155 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
403 | PS5-60-IN-0001C-CC02 | [5 empty] | 1P X 1.0 OS FL RTD | 135 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001C |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
404 | PS5-60-IN-0001D-CC02 | [5 empty] | 1P X 1.0 OS FL RTD | 130 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001D |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
405 | PS5-60-IN-0001E-CC02 | [5 empty] | 1P X 1.0 OS FL RTD | 120 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001E |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
406 | PS5-60-IN-0001F-CC02 | [5 empty] | 1P X 1.0 OS FL RTD | 110 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001F |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
407 | PS5-60-IN-0001G-CC02 | [5 empty] | 1P X 1.0 OS FL RTD | 105 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001G |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
408 | PS5-60-IN-0001A-CC04 | [5 empty] | 1P X 1.0 OS FL RTD | 155 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001A |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
409 | PS5-60-IN-0001B-CC04 | [5 empty] | 1P X 1.0 OS FL RTD | 145 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
410 | PS5-60-IN-0001C-CC04 | [5 empty] | 1P X 1.0 OS FL RTD | 135 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001C |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
411 | PS5-60-IN-0001D-CC04 | [5 empty] | 1P X 1.0 OS FL RTD | 130 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001D |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
412 | PS5-60-IN-0001E-CC04 | [5 empty] | 1P X 1.0 OS FL RTD | 120 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001E |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
413 | PS5-60-IN-0001F-CC04 | [5 empty] | 1P X 1.0 OS FL RTD | 115 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001F |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
414 | PS5-60-IN-0001G-CC04 | [5 empty] | 1P X 1.0 OS FL RTD | 105 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001G |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
415 | PS5-60-BI-0002-CC04 | [5 empty] | 1P X 1.0 OS FR | 190 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0002 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 06
416 | PS5-60-BI-0002-CC03 | [5 empty] | 1P X 1.0 OS FR | 175 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0002 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
417 | PS5-60-BI-0001A-CC03 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 140 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0001A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
418 | PS5-60-BI-0001B-CC03 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 130 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0001B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
419 | PS5-60-BI-0001C-CC03 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 120 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0001C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
420 | PS5-60-BI-0001D-CC03 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 110 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0001D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
421 | PS5-60-BI-0001E-CC03 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 105 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0001E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
422 | PS5-60-BI-0001F-CC03 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 100 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0001F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
423 | PS5-60-BI-0001G-CC03 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 90 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0001G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
424 | PS5-60-BI-0001A-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 135 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0001A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
425 | PS5-60-BI-0001B-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 130 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0001B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
426 | PS5-60-BI-0001C-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 120 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0001C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
427 | PS5-60-BI-0001D-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 110 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0001D |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
428 | PS5-60-BI-0001E-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 105 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0001E |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
429 | PS5-60-BI-0001F-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 100 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0001F |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
430 | PS5-60-BI-0001G-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 90 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0001G |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
431 | PS5-60-IE-0002B-CC05 | [5 empty] | 1T X 1.5 OS FR | 65 |  | PS5-60-IE-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0002B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
432 | PS5-60-IE-0002C-CC05 | [5 empty] | 1T X 1.5 OS FR | 65 |  | PS5-60-IE-0002B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0002C |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
433 | PS5-60-IE-0002D-CC05 | [5 empty] | 1T X 1.5 OS FR | 65 |  | PS5-60-IE-0002C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0002D |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
434 | PS5-60-IE-0002E-CC05 | [5 empty] | 1T X 1.5 OS FR | 65 |  | PS5-60-IE-0002D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0002E |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
435 | PS5-60-IE-0002F-CC05 | [5 empty] | 1T X 1.5 OS FR | 65 |  | PS5-60-IE-0002E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0002F |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
436 | PS5-60-IE-0002G-CC05 | [5 empty] | 1T X 1.5 OS FR | 65 |  | PS5-60-IE-0002F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0002G |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
437 | PS5-61-BI-0001-CC03 | [5 empty] | 1T X 1.5 OS FR | 220 |  | PS5-61-TE-0003A |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=1 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
438 | PS5-61-BI-0002-CC03 | [5 empty] | 1T X 1.5 OS FR | 210 |  | PS5-61-TE-0003B |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0002 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=1 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
439 | PS5-61-BI-0003-CC03 | [5 empty] | 1T X 1.5 OS FR | 205 |  | PS5-61-TE-0003C |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0003 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=1 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
440 | PS5-61-BI-0004-CC03 | [5 empty] | 1T X 1.5 OS FR | 200 |  | PS5-61-TE-0003D |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0004 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=1 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
441 | PS5-61-BI-0005-CC03 | [5 empty] | 1T X 1.5 OS FR | 180 |  | PS5-61-TE-0003E |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0005 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=1 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
442 | PS5-61-BI-0006-CC03 | [5 empty] | 1T X 1.5 OS FR | 175 |  | PS5-61-TE-0003F |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0006 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=1 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
443 | PS5-61-BI-0007-CC03 | [5 empty] | 1T X 1.5 OS FR | 170 |  | PS5-61-TE-0003G |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0007 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=1 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
444 | PS5-60-BE-0004A-CC01 | [5 empty] | 1T X 1.5 OS FR | 20 |  | PS5-60-IN-0001A |  |  |  | Powergen Bldg |  |  | PS5-60-BE-0004A |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
445 | PS5-60-BE-0004B-CC01 | [5 empty] | 1T X 1.5 OS FR | 20 |  | PS5-60-IN-0001B |  |  |  | Powergen Bldg |  |  | PS5-60-BE-0004B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
446 | PS5-60-BE-0004C-CC01 | [5 empty] | 1T X 1.5 OS FR | 20 |  | PS5-60-IN-0001C |  |  |  | Powergen Bldg |  |  | PS5-60-BE-0004C |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
447 | PS5-60-BE-0004D-CC01 | [5 empty] | 1T X 1.5 OS FR | 20 |  | PS5-60-IN-0001D |  |  |  | Powergen Bldg |  |  | PS5-60-BE-0004D |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
448 | PS5-60-BE-0004E-CC01 | [5 empty] | 1T X 1.5 OS FR | 20 |  | PS5-60-IN-0001E |  |  |  | Powergen Bldg |  |  | PS5-60-BE-0004E |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
449 | PS5-60-BE-0004F-CC01 | [5 empty] | 1T X 1.5 OS FR | 20 |  | PS5-60-IN-0001F |  |  |  | Powergen Bldg |  |  | PS5-60-BE-0004F |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
450 | PS5-60-BE-0004G-CC01 | [5 empty] | 1T X 1.5 OS FR | 20 |  | PS5-60-IN-0001G |  |  |  | Powergen Bldg |  |  | PS5-60-BE-0004G |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
451 | PS5-60-BI-0016A-CC03 | [5 empty] | 1P X 2.5 OS FL RTD | 155 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016A |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
452 | PS5-60-BI-0016B-CC03 | [5 empty] | 1P X 2.5 OS FL RTD | 145 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
453 | PS5-60-BI-0016C-CC03 | [5 empty] | 1P X 2.5 OS FL RTD | 135 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016C |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
454 | PS5-60-BI-0016D-CC03 | [5 empty] | 1P X 2.5 OS FL RTD | 130 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016D |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
455 | PS5-60-BI-0016E-CC03 | [5 empty] | 1P X 2.5 OS FL RTD | 120 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016E |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
456 | PS5-60-BI-0016F-CC03 | [5 empty] | 1P X 2.5 OS FL RTD | 115 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016F |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
457 | PS5-60-BI-0016G-CC03 | [5 empty] | 1P X 2.5 OS FL RTD | 105 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016G |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-06-23 00:00:00 | CPP-RFI-68-64-04-0071
458 | PS5-60-BE-0001-CC01 | [5 empty] | 1P X 2.5 OS FL RTD | 170 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-BE-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
459 | PS5-60-BE-0002-CC01 | [5 empty] | 1P X 2.5 OS FL RTD | 170 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-BE-0002 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
460 | PS5-60-SY-0007-CC01 | [5 empty] | 1P X 2.5 OS FL RTD | 140 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-SY-0007 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
461 | PS5-60-SY-0008-CC01 | [5 empty] | 1P X 2.5 OS FL RTD | 135 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-SY-0008 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
462 | PS5-60-SY-0009-CC01 | [5 empty] | 1P X 2.5 OS FL RTD | 125 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-SY-0009 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
463 | PS5-60-SY-0010-CC01 | [5 empty] | 1P X 2.5 OS FL RTD | 115 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-SY-0010 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
464 | PS5-60-SY-0011-CC01 | [5 empty] | 1P X 2.5 OS FL RTD | 110 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-SY-0011 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
465 | PS5-60-SY-0012-CC01 | [5 empty] | 1P X 2.5 OS FL RTD | 105 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-SY-0012 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
466 | PS5-60-SY-0013-CC01 | [5 empty] | 1P X 2.5 OS FL RTD | 100 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-SY-0013 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
467 | PS5-71-IN-0001-CC04 | [5 empty] | 1P X 1.0 OS FL RTD | 185 |  | PS5-71-IN-0001 |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0011A |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
468 | PS5-71-IN-0001-CC05 | [5 empty] | 1P X 1.0 OS FL RTD | 185 |  | PS5-71-IN-0001 |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0011B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
469 | PS5-71-IN-0004A-CC04 | [5 empty] | 1P X 1.0 OS FL RTD | 180 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0011A |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
470 | PS5-71-IN-0004A-CC05 | [5 empty] | 1P X 1.0 OS FL RTD | 180 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0011A |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
471 | PS5-71-IN-0004B-CC04 | [5 empty] | 1P X 1.0 OS FL RTD | 180 |  | PS5-71-IN-0004B |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0011B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
472 | PS5-71-IN-0004B-CC05 | [5 empty] | 1P X 1.0 OS FL RTD | 180 |  | PS5-71-IN-0004B |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0011B |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
473 | PS5-60-IE-0003A-CC25 | [5 empty] | 2P X 1.0 OS FL RTD | 135 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-TX-41100A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
474 | PS5-60-IE-0003A-CC26 | [5 empty] | 2P X 1.0 OS FL RTD | 135 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-TX-41100B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
475 | PS5-60-IE-0003B-CC25 | [5 empty] | 2P X 1.0 OS FL RTD | 125 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-TX-41200A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
476 | PS5-60-IE-0003B-CC26 | [5 empty] | 2P X 1.0 OS FL RTD | 125 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-TX-41200B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
477 | PS5-60-IE-0003C-CC25 | [5 empty] | 2P X 1.0 OS FL RTD | 115 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-TX-41300A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
478 | PS5-60-IE-0003C-CC26 | [5 empty] | 2P X 1.0 OS FL RTD | 115 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-TX-41300B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
479 | PS5-60-IE-0003D-CC25 | [5 empty] | 2P X 1.0 OS FL RTD | 105 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-TX-41400A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
480 | PS5-60-IE-0003D-CC26 | [5 empty] | 2P X 1.0 OS FL RTD | 105 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-TX-41400B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
481 | PS5-60-IE-0003E-CC25 | [5 empty] | 2P X 1.0 OS FL RTD | 100 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-TX-41500A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
482 | PS5-60-IE-0003E-CC26 | [5 empty] | 2P X 1.0 OS FL RTD | 100 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-TX-41500B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
483 | PS5-60-IE-0003F-CC25 | [5 empty] | 2P X 1.0 OS FL RTD | 100 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-TX-41600A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
484 | PS5-60-IE-0003F-CC26 | [5 empty] | 2P X 1.0 OS FL RTD | 100 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-TX-41600B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
485 | PS5-60-IE-0003G-CC25 | [5 empty] | 2P X 1.0 OS FL RTD | 85 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-TX-41700A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
486 | PS5-60-IE-0003G-CC26 | [5 empty] | 2P X 1.0 OS FL RTD | 85 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-TX-41700B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
487 | PS5-60-IN-0001A-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 155 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
488 | PS5-60-IN-0001B-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 140 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
489 | PS5-60-IN-0001C-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 135 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
490 | PS5-60-IN-0001D-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 125 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
491 | PS5-60-IN-0001E-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 120 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
492 | PS5-60-IN-0001F-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 115 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
493 | PS5-60-IN-0001G-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 105 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
494 | PS5-60-IN-0001A-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 150 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
495 | PS5-60-IN-0001B-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 140 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
496 | PS5-60-IN-0001C-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 135 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
497 | PS5-60-IN-0001D-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 125 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
498 | PS5-60-IN-0001E-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 120 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
499 | PS5-60-IN-0001F-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 110 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
500 | PS5-60-IN-0001G-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 105 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0001G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
501 | PS5-60-BI-0006A-CC05 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IN-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
502 | PS5-60-BI-0006B-CC05 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IN-0002B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
503 | PS5-60-BI-0006C-CC05 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IN-0002C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
504 | PS5-60-BI-0006D-CC05 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IN-0002D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
505 | PS5-60-BI-0006E-CC05 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IN-0002E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
506 | PS5-60-BI-0006F-CC05 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IN-0002F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
507 | PS5-60-BI-0006G-CC05 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IN-0002G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
508 | PS5-60-IE-0003A-CC15 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 135 |  | PS5-60-IE-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
509 | PS5-60-IE-0003B-CC15 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 135 |  | PS5-60-IE-0002B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
510 | PS5-60-LA-0003-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 35 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0003 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
511 | PS5-71-BI-0009-CC02 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 20 |  | PS5-71-IN-0001 |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0009 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
512 | PS5-71-BI-0009-CC03 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 20 |  | PS5-71-IN-0001 |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0009 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
513 | PS5-71-BI-0011B-CC03 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 20 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0011B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
514 | PS5-60-BI-0003-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 170 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0003 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
515 | PS5-60-IN-0002A-CC06 | [5 empty] | 6P X 0.75 IS/OS FR | 135 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
516 | PS5-60-IN-0002B-CC06 | [5 empty] | 6P X 0.75 IS/OS FR | 125 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
517 | PS5-60-IN-0002C-CC06 | [5 empty] | 6P X 0.75 IS/OS FR | 120 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
518 | PS5-60-IN-0002D-CC06 | [5 empty] | 6P X 0.75 IS/OS FR | 110 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002D |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
519 | PS5-60-IN-0002E-CC06 | [5 empty] | 6P X 0.75 IS/OS FR | 105 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002E |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
520 | PS5-60-IN-0002F-CC06 | [5 empty] | 6P X 0.75 IS/OS FR | 100 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002F |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
521 | PS5-60-IN-0002G-CC06 | [5 empty] | 6P X 0.75 IS/OS FR | 90 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002G |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
522 | PS5-71-BI-0003-CC01 | [5 empty] | 6P X 0.75 IS/OS FR | 160 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0003 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
523 | PS5-71-BI-0005-CC02 | [5 empty] | 6P X 0.75 IS/OS FR | 180 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0005 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
524 | PS5-71-IN-0001-CC03 | [5 empty] | 6P X 0.75 IS/OS FR | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
525 | PS5-71-IN-0004A-CC03 | [5 empty] | 6P X 0.75 IS/OS FR | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0004A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
526 | PS5-71-IN-0004B-CC03 | [5 empty] | 6P X 0.75 IS/OS FR | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0004B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
527 | PS5-60-BI-0003-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 175 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0003 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
528 | PS5-60-BI-0006A-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 30 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
529 | PS5-60-BI-0006B-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 30 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
530 | PS5-60-BI-0006C-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 30 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
531 | PS5-60-BI-0006D-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 30 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
532 | PS5-60-BI-0006E-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 30 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
533 | PS5-60-BI-0006F-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 30 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
534 | PS5-60-BI-0006G-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 30 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
535 | PS5-60-BI-0016A-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 155 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
536 | PS5-60-BI-0016B-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 145 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
537 | PS5-60-BI-0016C-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 135 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
538 | PS5-60-BI-0016D-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 125 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
539 | PS5-60-BI-0016E-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 120 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
540 | PS5-60-BI-0016F-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 110 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
541 | PS5-60-BI-0016G-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 105 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
542 | PS5-60-BI-0002-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 170 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0002 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
543 | PS5-60-BI-0005A-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 170 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0005A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
544 | PS5-60-BI-0005A-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 170 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0005A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
545 | PS5-60-BI-0005B-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 165 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0005B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
546 | PS5-60-BI-0005B-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 165 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0005B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
547 | PS5-60-BI-0005C-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 155 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0005C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
548 | PS5-60-BI-0005C-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 155 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0005C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
549 | PS5-60-BI-0005D-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 150 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0005D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
550 | PS5-60-BI-0005D-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 150 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0005D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
551 | PS5-60-BI-0005E-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 140 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0005E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
552 | PS5-60-BI-0005E-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 140 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0005E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
553 | PS5-60-BI-0005F-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 130 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0005F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
554 | PS5-60-BI-0005F-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 130 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0005F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
555 | PS5-60-BI-0005G-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 125 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0005G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
556 | PS5-60-BI-0005G-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 125 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0005G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
557 | PS5-60-BI-0006A-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IN-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
558 | PS5-60-BI-0006A-CC06 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IN-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
559 | PS5-60-BI-0006B-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IN-0002B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
560 | PS5-60-BI-0006B-CC06 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IN-0002B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
561 | PS5-60-BI-0006C-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IN-0002C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
562 | PS5-60-BI-0006C-CC06 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IN-0002C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
563 | PS5-60-BI-0006D-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IN-0002D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
564 | PS5-60-BI-0006D-CC06 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IN-0002D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
565 | PS5-60-BI-0006E-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IN-0002E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
566 | PS5-60-BI-0006E-CC06 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IN-0002E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
567 | PS5-60-BI-0006F-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IN-0002F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
568 | PS5-60-BI-0006F-CC06 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IN-0002F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
569 | PS5-60-BI-0006G-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IN-0002G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
570 | PS5-60-BI-0006G-CC06 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IN-0002G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
571 | PS5-60-IE-0003A-CC07 | [5 empty] | 6P X 0.75 OS FL RTD | 130 |  | PS5-60-IE-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
572 | PS5-60-IE-0003B-CC06 | [5 empty] | 6P X 0.75 OS FL RTD | 125 |  | PS5-60-IE-0002B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
573 | PS5-60-IE-0003B-CC07 | [5 empty] | 6P X 0.75 OS FL RTD | 125 |  | PS5-60-IE-0002B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
574 | PS5-60-IE-0003C-CC06 | [5 empty] | 6P X 0.75 OS FL RTD | 115 |  | PS5-60-IE-0002C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
575 | PS5-60-IE-0003C-CC07 | [5 empty] | 6P X 0.75 OS FL RTD | 115 |  | PS5-60-IE-0002C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
576 | PS5-60-IE-0003D-CC06 | [5 empty] | 6P X 0.75 OS FL RTD | 105 |  | PS5-60-IE-0002D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
577 | PS5-60-IE-0003D-CC07 | [5 empty] | 6P X 0.75 OS FL RTD | 105 |  | PS5-60-IE-0002D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
578 | PS5-60-IE-0003E-CC06 | [5 empty] | 6P X 0.75 OS FL RTD | 100 |  | PS5-60-IE-0002E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
579 | PS5-60-IE-0003E-CC07 | [5 empty] | 6P X 0.75 OS FL RTD | 100 |  | PS5-60-IE-0002E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
580 | PS5-60-IE-0003F-CC06 | [5 empty] | 6P X 0.75 OS FL RTD | 95 |  | PS5-60-IE-0002F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
581 | PS5-60-IE-0003F-CC07 | [5 empty] | 6P X 0.75 OS FL RTD | 95 |  | PS5-60-IE-0002F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
582 | PS5-60-IE-0003G-CC06 | [5 empty] | 6P X 0.75 OS FL RTD | 85 |  | PS5-60-IE-0002G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
583 | PS5-60-IE-0003G-CC07 | [5 empty] | 6P X 0.75 OS FL RTD | 85 |  | PS5-60-IE-0002G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
584 | PS5-60-IN-0002A-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 140 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
585 | PS5-60-IN-0002A-CC04 | [5 empty] | 6P X 0.75 OS FL RTD | 140 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
586 | PS5-60-IN-0002B-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 130 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
587 | PS5-60-IN-0002B-CC04 | [5 empty] | 6P X 0.75 OS FL RTD | 130 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
588 | PS5-60-IN-0002C-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 120 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
589 | PS5-60-IN-0002C-CC04 | [5 empty] | 6P X 0.75 OS FL RTD | 120 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
590 | PS5-60-IN-0002D-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 110 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
591 | PS5-60-IN-0002D-CC04 | [5 empty] | 6P X 0.75 OS FL RTD | 110 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
592 | PS5-60-IN-0002E-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 105 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
593 | PS5-60-IN-0002E-CC04 | [5 empty] | 6P X 0.75 OS FL RTD | 105 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
594 | PS5-60-IN-0002F-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 100 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
595 | PS5-60-IN-0002F-CC04 | [5 empty] | 6P X 0.75 OS FL RTD | 100 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
596 | PS5-60-IN-0002G-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 95 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
597 | PS5-60-IN-0002G-CC04 | [5 empty] | 6P X 0.75 OS FL RTD | 95 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
598 | PS5-60-SEA-0001-CC10 | [5 empty] | 6P X 0.75 OS FL RTD | 150 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
599 | PS5-60-VS-9101A-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 140 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-VS-9101A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
600 | PS5-60-VS-9101B-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 130 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-VS-9101B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
601 | PS5-60-VS-9101C-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 120 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-VS-9101C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
602 | PS5-60-VS-9101D-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 110 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-VS-9101D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
603 | PS5-60-VS-9101E-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 105 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-VS-9101E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
604 | PS5-60-VS-9101F-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 100 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-VS-9101F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
605 | PS5-60-VS-9101G-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 90 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-VS-9101G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
606 | PS5-71-BI-0003-CC04 | [5 empty] | 6P X 0.75 OS FL RTD | 20 |  | PS5-71-IN-0002 |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0003 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
607 | PS5-71-BI-0006-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 20 |  | PS5-71-IN-0003 |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0006 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
608 | PS5-71-BI-0009-CC04 | [5 empty] | 6P X 0.75 OS FL RTD | 20 |  | PS5-71-IN-0001 |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0009 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
609 | PS5-71-BI-0010-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 20 |  | PS5-71-IN-0001 |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0010 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
610 | PS5-71-BI-0011A-CC03 | [5 empty] | 6P X 0.75 OS FL RTD | 20 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0011A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
611 | PS5-71-IN-0001-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0001 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
612 | PS5-71-IN-0001-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 40 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0001 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
613 | PS5-71-IN-0002-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0002 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
614 | PS5-71-IN-0003-CC01 | [5 empty] | 6P X 0.75 OS FL RTD | 35 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0003 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
615 | PS5-71-IN-0003-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 35 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0003 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
616 | PS5-60-BI-0006A-CC02 | [5 empty] | 6P X 0.75 OS FR | 40 |  | PS5-60-IN-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
617 | PS5-60-BI-0006B-CC02 | [5 empty] | 6P X 0.75 OS FR | 40 |  | PS5-60-IN-0002B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
618 | PS5-60-BI-0006C-CC02 | [5 empty] | 6P X 0.75 OS FR | 40 |  | PS5-60-IN-0002C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
619 | PS5-60-BI-0006D-CC02 | [5 empty] | 6P X 0.75 OS FR | 40 |  | PS5-60-IN-0002D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006D |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
620 | PS5-60-BI-0006E-CC02 | [5 empty] | 6P X 0.75 OS FR | 40 |  | PS5-60-IN-0002E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006E |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
621 | PS5-60-BI-0006F-CC02 | [5 empty] | 6P X 0.75 OS FR | 40 |  | PS5-60-IN-0002F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006F |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
622 | PS5-60-BI-0006G-CC02 | [5 empty] | 6P X 0.75 OS FR | 40 |  | PS5-60-IN-0002G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006G |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
623 | PS5-60-IE-0003A-CC03 | [5 empty] | 6P X 0.75 OS FR | 130 |  | PS5-60-IE-0001A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
624 | PS5-60-IE-0003B-CC03 | [5 empty] | 6P X 0.75 OS FR | 125 |  | PS5-60-IE-0001B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
625 | PS5-60-IE-0003C-CC03 | [5 empty] | 6P X 0.75 OS FR | 115 |  | PS5-60-IE-0001C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
626 | PS5-60-IE-0003D-CC03 | [5 empty] | 6P X 0.75 OS FR | 105 |  | PS5-60-IE-0001D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003D |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
627 | PS5-60-IE-0003E-CC03 | [5 empty] | 6P X 0.75 OS FR | 100 |  | PS5-60-IE-0001E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003E |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
628 | PS5-60-IE-0003F-CC03 | [5 empty] | 6P X 0.75 OS FR | 100 |  | PS5-60-IE-0001F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003F |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
629 | PS5-60-IN-0002A-CC03 | [5 empty] | 6P X 0.75 OS FR | 140 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
630 | PS5-60-IN-0002A-CC05 | [5 empty] | 6P X 0.75 OS FR | 140 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
631 | PS5-60-IN-0002B-CC03 | [5 empty] | 6P X 0.75 OS FR | 130 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
632 | PS5-60-IN-0002B-CC05 | [5 empty] | 6P X 0.75 OS FR | 130 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
633 | PS5-60-IN-0002C-CC03 | [5 empty] | 6P X 0.75 OS FR | 120 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
634 | PS5-60-IN-0002C-CC05 | [5 empty] | 6P X 0.75 OS FR | 120 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
635 | PS5-60-IN-0002D-CC03 | [5 empty] | 6P X 0.75 OS FR | 110 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002D |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
636 | PS5-60-IN-0002D-CC05 | [5 empty] | 6P X 0.75 OS FR | 110 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002D |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
637 | PS5-60-IN-0002E-CC03 | [5 empty] | 6P X 0.75 OS FR | 105 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002E |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
638 | PS5-60-IN-0002E-CC05 | [5 empty] | 6P X 0.75 OS FR | 105 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002E |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
639 | PS5-60-IN-0002F-CC03 | [5 empty] | 6P X 0.75 OS FR | 100 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002F |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
640 | PS5-60-IN-0002F-CC05 | [5 empty] | 6P X 0.75 OS FR | 100 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002F |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
641 | PS5-60-IN-0002G-CC03 | [5 empty] | 6P X 0.75 OS FR | 90 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002G |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
642 | PS5-60-IN-0002G-CC05 | [5 empty] | 6P X 0.75 OS FR | 90 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002G |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
643 | PS5-60-LA-0002A-CC01 | [5 empty] | 6P X 0.75 OS FR | 35 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
644 | PS5-60-LA-0002A-CC02 | [5 empty] | 6P X 0.75 OS FR | 35 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
645 | PS5-60-LA-0002A-CC03 | [5 empty] | 6P X 0.75 OS FR | 35 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
646 | PS5-60-LA-0002A-CC04 | [5 empty] | 6P X 0.75 OS FR | 35 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
647 | PS5-60-LA-0002A-CC05 | [5 empty] | 6P X 0.75 OS FR | 35 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
648 | PS5-60-LA-0002A-CC06 | [5 empty] | 6P X 0.75 OS FR | 35 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
649 | PS5-60-LA-0002A-CC07 | [5 empty] | 6P X 0.75 OS FR | 35 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
650 | PS5-60-LA-0002A-CC08 | [5 empty] | 6P X 0.75 OS FR | 35 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
651 | PS5-60-LA-0002A-CC09 | [5 empty] | 6P X 0.75 OS FR | 35 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
652 | PS5-60-LA-0002B-CC01 | [5 empty] | 6P X 0.75 OS FR | 35 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
653 | PS5-60-LA-0002B-CC02 | [5 empty] | 6P X 0.75 OS FR | 35 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
654 | PS5-60-LA-0002B-CC03 | [5 empty] | 6P X 0.75 OS FR | 35 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
655 | PS5-60-LA-0002B-CC04 | [5 empty] | 6P X 0.75 OS FR | 35 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
656 | PS5-60-LA-0002B-CC05 | [5 empty] | 6P X 0.75 OS FR | 35 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
657 | PS5-60-LA-0002B-CC06 | [5 empty] | 6P X 0.75 OS FR | 35 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
658 | PS5-60-LA-0002C-CC01 | [5 empty] | 6P X 0.75 OS FR | 40 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
659 | PS5-60-LA-0002C-CC02 | [5 empty] | 6P X 0.75 OS FR | 40 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
660 | PS5-60-LA-0002C-CC03 | [5 empty] | 6P X 0.75 OS FR | 40 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
661 | PS5-60-LA-0002C-CC04 | [5 empty] | 6P X 0.75 OS FR | 40 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
662 | PS5-60-LA-0002C-CC05 | [5 empty] | 6P X 0.75 OS FR | 40 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
663 | PS5-60-LA-0002C-CC06 | [5 empty] | 6P X 0.75 OS FR | 40 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0002C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
664 | PS5-60-SEA-0001-CC01 | [5 empty] | 6P X 0.75 OS FR | 190 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
665 | PS5-60-SEA-0001-CC02 | [5 empty] | 6P X 0.75 OS FR | 190 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
666 | PS5-60-SEA-0001-CC03 | [5 empty] | 6P X 0.75 OS FR | 170 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
667 | PS5-60-SEA-0001-CC04 | [5 empty] | 6P X 0.75 OS FR | 170 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
668 | PS5-60-SEA-0001-CC05 | [5 empty] | 6P X 0.75 OS FR | 155 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
669 | PS5-60-SEA-0001-CC06 | [5 empty] | 6P X 0.75 OS FR | 155 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
670 | PS5-60-SEA-0001-CC07 | [5 empty] | 6P X 0.75 OS FR | 145 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
671 | PS5-60-SEA-0001-CC11 | [5 empty] | 6P X 0.75 OS FR | 190 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
672 | PS5-60-SEA-0001-CC12 | [5 empty] | 6P X 0.75 OS FR | 190 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
673 | PS5-60-SEA-0001-CC13 | [5 empty] | 6P X 0.75 OS FR | 170 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
674 | PS5-60-SEA-0001-CC14 | [5 empty] | 6P X 0.75 OS FR | 170 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
675 | PS5-60-SEA-0001-CC15 | [5 empty] | 6P X 0.75 OS FR | 155 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
676 | PS5-60-SEA-0001-CC16 | [5 empty] | 6P X 0.75 OS FR | 155 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
677 | PS5-60-SEA-0001-CC17 | [5 empty] | 6P X 0.75 OS FR | 145 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
678 | PS5-61-BI-0001-CC02 | [5 empty] | 6P X 0.75 OS FR | 215 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=3 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0050
679 | PS5-61-BI-0002-CC02 | [5 empty] | 6P X 0.75 OS FR | 210 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0002 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=1 B=5 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0050
680 | PS5-61-BI-0003-CC02 | [5 empty] | 6P X 0.75 OS FR | 205 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0003 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=3 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0050
681 | PS5-61-BI-0004-CC02 | [5 empty] | 6P X 0.75 OS FR | 200 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0004 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=3 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0050
682 | PS5-61-BI-0005-CC02 | [5 empty] | 6P X 0.75 OS FR | 280 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0005 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=3 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0050
683 | PS5-61-BI-0006-CC02 | [5 empty] | 6P X 0.75 OS FR | 175 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0006 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=3 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0050
684 | PS5-61-BI-0007-CC02 | [5 empty] | 6P X 0.75 OS FR | 170 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0007 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=3 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0050
685 | PS5-71-IN-0001-CC06 | [5 empty] | 6P X 0.75 OS FR | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
686 | PS5-71-IN-0001-CC07 | [5 empty] | 6P X 0.75 OS FR | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0001 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
687 | PS5-71-IN-0002-CC03 | [5 empty] | 6P X 0.75 OS FR | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0002 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
688 | PS5-71-IN-0002-CC04 | [5 empty] | 6P X 0.75 OS FR | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0002 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
689 | PS5-71-IN-0003-CC03 | [5 empty] | 6P X 0.75 OS FR | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0003 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
690 | PS5-71-IN-0003-CC04 | [5 empty] | 6P X 0.75 OS FR | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0003 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
691 | PS5-71-IN-0004A-CC06 | [5 empty] | 6P X 0.75 OS FR | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0004A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
692 | PS5-71-IN-0004A-CC07 | [5 empty] | 6P X 0.75 OS FR | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0004A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
693 | PS5-71-IN-0004B-CC06 | [5 empty] | 6P X 0.75 OS FR | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0004B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
694 | PS5-71-IN-0004B-CC07 | [5 empty] | 6P X 0.75 OS FR | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0004B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
695 | PS5-60-BI-0019A-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 155 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0019A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
696 | PS5-60-BI-0019B-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 145 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0019B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
697 | PS5-60-BI-0019C-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 130 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0019C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
698 | PS5-60-BI-0019D-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 125 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0019D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
699 | PS5-60-BI-0019E-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 120 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0019E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
700 | PS5-60-BI-0019F-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 110 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0019F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
701 | PS5-60-BI-0019G-CC01 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 100 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0019G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
702 | PS5-60-IE-0003C-CC15 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 115 |  | PS5-60-IE-0002C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
703 | PS5-60-IE-0003D-CC15 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 105 |  | PS5-60-IE-0002D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
704 | PS5-60-IE-0003E-CC15 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 100 |  | PS5-60-IE-0002E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
705 | PS5-60-IE-0003F-CC15 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 100 |  | PS5-60-IE-0002F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
706 | PS5-60-IE-0003G-CC15 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 85 |  | PS5-60-IE-0002G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
707 | PS5-60-BI-0019A-CC02 | [5 empty] | 6P X 0.75 IS/OS FR | 150 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0019A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
708 | PS5-60-BI-0019B-CC02 | [5 empty] | 6P X 0.75 IS/OS FR | 145 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0019B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
709 | PS5-60-BI-0019C-CC02 | [5 empty] | 6P X 0.75 IS/OS FR | 135 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0019C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
710 | PS5-60-BI-0019D-CC02 | [5 empty] | 6P X 0.75 IS/OS FR | 125 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0019D |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
711 | PS5-60-BI-0019E-CC02 | [5 empty] | 6P X 0.75 IS/OS FR | 125 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0019E |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
712 | PS5-60-BI-0019F-CC02 | [5 empty] | 6P X 0.75 IS/OS FR | 115 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0019F |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
713 | PS5-60-BI-0019G-CC02 | [5 empty] | 6P X 0.75 IS/OS FR | 105 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0019G |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
714 | PS5-60-IE-0003A-CC06 | [5 empty] | 6P X 0.75 OS FL RTD | 130 |  | PS5-60-IE-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
715 | PS5-60-IE-0003A-CC16 | [5 empty] | 6P X 0.75 OS FR | 130 |  | PS5-60-IE-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
716 | PS5-60-IE-0003A-CC17 | [5 empty] | 6P X 0.75 OS FR | 130 |  | PS5-60-IE-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
717 | PS5-60-IE-0003B-CC16 | [5 empty] | 6P X 0.75 OS FR | 125 |  | PS5-60-IE-0002B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
718 | PS5-60-IE-0003B-CC17 | [5 empty] | 6P X 0.75 OS FR | 125 |  | PS5-60-IE-0002B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
719 | PS5-60-IE-0003C-CC16 | [5 empty] | 6P X 0.75 OS FR | 115 |  | PS5-60-IE-0002C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
720 | PS5-60-IE-0003C-CC17 | [5 empty] | 6P X 0.75 OS FR | 115 |  | PS5-60-IE-0002C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
721 | PS5-60-IE-0003D-CC16 | [5 empty] | 6P X 0.75 OS FR | 105 |  | PS5-60-IE-0002D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003D |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
722 | PS5-60-IE-0003D-CC17 | [5 empty] | 6P X 0.75 OS FR | 105 |  | PS5-60-IE-0002D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003D |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
723 | PS5-60-IE-0003E-CC16 | [5 empty] | 6P X 0.75 OS FR | 100 |  | PS5-60-IE-0002E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003E |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
724 | PS5-60-IE-0003E-CC17 | [5 empty] | 6P X 0.75 OS FR | 100 |  | PS5-60-IE-0002E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003E |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
725 | PS5-60-IE-0003F-CC16 | [5 empty] | 6P X 0.75 OS FR | 90 |  | PS5-60-IE-0002F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003F |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
726 | PS5-60-IE-0003F-CC17 | [5 empty] | 6P X 0.75 OS FR | 90 |  | PS5-60-IE-0002F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003F |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
727 | PS5-60-IE-0003G-CC03 | [5 empty] | 6P X 0.75 OS FR | 85 |  | PS5-60-IE-0001G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003G |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
728 | PS5-60-IE-0003G-CC16 | [5 empty] | 6P X 0.75 OS FR | 85 |  | PS5-60-IE-0002G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003G |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
729 | PS5-60-IE-0003G-CC17 | [5 empty] | 6P X 0.75 OS FR | 85 |  | PS5-60-IE-0002G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003G |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
730 | PS5-60-BI-0017A-CC02 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 45 |  | PS5-60-IN-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0017A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
731 | PS5-60-BI-0017B-CC02 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 45 |  | PS5-60-IN-0002B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0017B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
732 | PS5-60-BI-0017C-CC02 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 45 |  | PS5-60-IN-0002C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0017C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
733 | PS5-60-BI-0017D-CC02 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 45 |  | PS5-60-IN-0002D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0017D |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
734 | PS5-60-BI-0017E-CC02 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 45 |  | PS5-60-IN-0002E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0017E |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
735 | PS5-60-BI-0017F-CC02 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 45 |  | PS5-60-IN-0002F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0017F |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
736 | PS5-60-BI-0017G-CC02 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 45 |  | PS5-60-IN-0002G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0017G |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
737 | PS5-71-BI-0008A-CC01 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 20 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0008A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
738 | PS5-71-BI-0008A-CC02 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 20 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0008A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
739 | PS5-71-BI-0008B-CC01 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 20 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0008B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
740 | PS5-71-BI-0008B-CC02 | [5 empty] | 12P X 0.75 IS/OS FL RTD | 20 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0008B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
741 | PS5-60-BI-0002-CC01 | [5 empty] | 12P X 0.75 IS/OS FR | 180 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0002 |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
742 | PS5-60-IE-0003A-CC08 | [5 empty] | 12P X 0.75 OS FL RTD | 140 |  | PS5-60-IE-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
743 | PS5-60-IE-0003A-CC09 | [5 empty] | 12P X 0.75 OS FL RTD | 140 |  | PS5-60-IE-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
744 | PS5-60-IE-0003A-CC10 | [5 empty] | 12P X 0.75 OS FL RTD | 50 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
745 | PS5-60-IE-0003A-CC11 | [5 empty] | 12P X 0.75 OS FL RTD | 50 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
746 | PS5-60-IE-0003B-CC08 | [5 empty] | 12P X 0.75 OS FL RTD | 125 |  | PS5-60-IE-0002B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
747 | PS5-60-IE-0003B-CC09 | [5 empty] | 12P X 0.75 OS FL RTD | 125 |  | PS5-60-IE-0002B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
748 | PS5-60-IE-0003B-CC10 | [5 empty] | 12P X 0.75 OS FL RTD | 50 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
749 | PS5-60-IE-0003B-CC11 | [5 empty] | 12P X 0.75 OS FL RTD | 50 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
750 | PS5-60-IE-0003C-CC08 | [5 empty] | 12P X 0.75 OS FL RTD | 115 |  | PS5-60-IE-0002C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
751 | PS5-60-IE-0003C-CC09 | [5 empty] | 12P X 0.75 OS FL RTD | 115 |  | PS5-60-IE-0002C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
752 | PS5-60-IE-0003C-CC10 | [5 empty] | 12P X 0.75 OS FL RTD | 50 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
753 | PS5-60-IE-0003C-CC11 | [5 empty] | 12P X 0.75 OS FL RTD | 50 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
754 | PS5-60-IE-0003D-CC08 | [5 empty] | 12P X 0.75 OS FL RTD | 110 |  | PS5-60-IE-0002D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003D |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
755 | PS5-60-IE-0003D-CC09 | [5 empty] | 12P X 0.75 OS FL RTD | 110 |  | PS5-60-IE-0002D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003D |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
756 | PS5-60-IE-0003D-CC10 | [5 empty] | 12P X 0.75 OS FL RTD | 50 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
757 | PS5-60-IE-0003D-CC11 | [5 empty] | 12P X 0.75 OS FL RTD | 50 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
758 | PS5-60-IE-0003E-CC08 | [5 empty] | 12P X 0.75 OS FL RTD | 100 |  | PS5-60-IE-0002E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003E |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
759 | PS5-60-IE-0003E-CC09 | [5 empty] | 12P X 0.75 OS FL RTD | 100 |  | PS5-60-IE-0002E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003E |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
760 | PS5-60-IE-0003E-CC10 | [5 empty] | 12P X 0.75 OS FL RTD | 50 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
761 | PS5-60-IE-0003E-CC11 | [5 empty] | 12P X 0.75 OS FL RTD | 50 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
762 | PS5-60-IE-0003F-CC08 | [5 empty] | 12P X 0.75 OS FL RTD | 100 |  | PS5-60-IE-0002F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003F |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
763 | PS5-60-IE-0003F-CC09 | [5 empty] | 12P X 0.75 OS FL RTD | 100 |  | PS5-60-IE-0002F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003F |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
764 | PS5-60-IE-0003F-CC10 | [5 empty] | 12P X 0.75 OS FL RTD | 55 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
765 | PS5-60-IE-0003F-CC11 | [5 empty] | 12P X 0.75 OS FL RTD | 55 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
766 | PS5-60-IE-0003G-CC08 | [5 empty] | 12P X 0.75 OS FL RTD | 85 |  | PS5-60-IE-0002G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003G |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
767 | PS5-60-IE-0003G-CC09 | [5 empty] | 12P X 0.75 OS FL RTD | 85 |  | PS5-60-IE-0002G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003G |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
768 | PS5-60-IE-0003G-CC10 | [5 empty] | 12P X 0.75 OS FL RTD | 55 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
769 | PS5-60-IE-0003G-CC11 | [5 empty] | 12P X 0.75 OS FL RTD | 55 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
770 | PS5-60-IN-0002A-CC02 | [5 empty] | 12P X 0.75 OS FL RTD | 140 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
771 | PS5-60-IN-0002B-CC02 | [5 empty] | 12P X 0.75 OS FL RTD | 130 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
772 | PS5-60-IN-0002C-CC02 | [5 empty] | 12P X 0.75 OS FL RTD | 120 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002C |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
773 | PS5-60-IN-0002D-CC02 | [5 empty] | 12P X 0.75 OS FL RTD | 115 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002D |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
774 | PS5-60-IN-0002E-CC02 | [5 empty] | 12P X 0.75 OS FL RTD | 105 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002E |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
775 | PS5-60-IN-0002F-CC02 | [5 empty] | 12P X 0.75 OS FL RTD | 100 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002F |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
776 | PS5-60-IN-0002G-CC02 | [5 empty] | 12P X 0.75 OS FL RTD | 90 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IN-0002G |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
777 | PS5-71-BI-0001A-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 20 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0001A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
778 | PS5-71-BI-0001B-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 20 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0001B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
779 | PS5-71-BI-0002-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 20 |  | PS5-71-IN-0001 |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0002 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
780 | PS5-71-BI-0004-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 20 |  | PS5-71-IN-0002 |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0004 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
781 | PS5-71-BI-0005-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 20 |  | PS5-71-IN-0003 |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0005 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
782 | PS5-71-IN-0002-CC02 | [5 empty] | 12P X 0.75 OS FL RTD | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0002 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
783 | PS5-71-IN-0004A-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0004A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
784 | PS5-71-IN-0004A-CC02 | [5 empty] | 12P X 0.75 OS FL RTD | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0004A |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
785 | PS5-71-IN-0004B-CC01 | [5 empty] | 12P X 0.75 OS FL RTD | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0004B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
786 | PS5-71-IN-0004B-CC02 | [5 empty] | 12P X 0.75 OS FL RTD | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0004B |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
787 | PS5-60-IE-0003A-CC01 | [5 empty] | 12P X 0.75 OS FR | 135 |  | PS5-60-IE-0001A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003A |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
788 | PS5-60-IE-0003A-CC02 | [5 empty] | 12P X 0.75 OS FR | 135 |  | PS5-60-IE-0001A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003A |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
789 | PS5-60-IE-0003B-CC01 | [5 empty] | 12P X 0.75 OS FR | 125 |  | PS5-60-IE-0001B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003B |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
790 | PS5-60-IE-0003B-CC02 | [5 empty] | 12P X 0.75 OS FR | 125 |  | PS5-60-IE-0001B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003B |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
791 | PS5-60-IE-0003C-CC01 | [5 empty] | 12P X 0.75 OS FR | 115 |  | PS5-60-IE-0001C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003C |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
792 | PS5-60-IE-0003C-CC02 | [5 empty] | 12P X 0.75 OS FR | 115 |  | PS5-60-IE-0001C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003C |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
793 | PS5-60-IE-0003D-CC01 | [5 empty] | 12P X 0.75 OS FR | 110 |  | PS5-60-IE-0001D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003D |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
794 | PS5-60-IE-0003D-CC02 | [5 empty] | 12P X 0.75 OS FR | 110 |  | PS5-60-IE-0001D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003D |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
795 | PS5-60-IE-0003E-CC01 | [5 empty] | 12P X 0.75 OS FR | 100 |  | PS5-60-IE-0001E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003E |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
796 | PS5-60-IE-0003E-CC02 | [5 empty] | 12P X 0.75 OS FR | 100 |  | PS5-60-IE-0001E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003E |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
797 | PS5-60-IE-0003F-CC01 | [5 empty] | 12P X 0.75 OS FR | 100 |  | PS5-60-IE-0001F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003F |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 07
798 | PS5-60-IE-0003F-CC02 | [5 empty] | 12P X 0.75 OS FR | 100 |  | PS5-60-IE-0001F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003F |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 07
799 | PS5-60-IE-0003G-CC01 | [5 empty] | 12P X 0.75 OS FR | 90 |  | PS5-60-IE-0001G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003G |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 07
800 | PS5-60-IE-0003G-CC02 | [5 empty] | 12P X 0.75 OS FR | 90 |  | PS5-60-IE-0001G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003G |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 07
801 | PS5-60-IE-0003A-CC04 | [5 empty] | 12P X 0.75 OS FR | 135 |  | PS5-60-IE-0001A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003A |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
802 | PS5-60-IE-0003B-CC04 | [5 empty] | 12P X 0.75 OS FR | 125 |  | PS5-60-IE-0001B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003B |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
803 | PS5-60-IE-0003C-CC04 | [5 empty] | 12P X 0.75 OS FR | 115 |  | PS5-60-IE-0001C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003C |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
804 | PS5-60-IE-0003D-CC04 | [5 empty] | 12P X 0.75 OS FR | 110 |  | PS5-60-IE-0001D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003D |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
805 | PS5-60-IE-0003E-CC04 | [5 empty] | 12P X 0.75 OS FR | 100 |  | PS5-60-IE-0001E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003E |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
806 | PS5-60-IE-0003F-CC04 | [5 empty] | 12P X 0.75 OS FR | 100 |  | PS5-60-IE-0001F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003F |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 07
807 | PS5-60-IE-0003G-CC04 | [5 empty] | 12P X 0.75 OS FR | 90 |  | PS5-60-IE-0001G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003G |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 07
808 | PS5-60-IE-0003B-CC05 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 125 |  | PS5-60-IE-0001B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
809 | PS5-60-IE-0003C-CC05 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 115 |  | PS5-60-IE-0001C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
810 | PS5-60-IE-0003D-CC05 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 105 |  | PS5-60-IE-0001D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
811 | PS5-60-IE-0003E-CC05 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 100 |  | PS5-60-IE-0001E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
812 | PS5-60-IE-0003F-CC05 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 100 |  | PS5-60-IE-0001F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
813 | PS5-60-IE-0003G-CC05 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 85 |  | PS5-60-IE-0001G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003H |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
814 | PS5-60-IE-0003A-CC05 | [5 empty] | 6P X 0.75 IS/OS FL RTD | 130 |  | PS5-60-IE-0001A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
815 | PS5-71-BI-0011A-CC04 | [5 empty] | 24P X 0.75 IS/OS FL RTD | 20 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0011A |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
816 | PS5-71-BI-0011B-CC04 | [5 empty] | 24P X 0.75 IS/OS FL RTD | 20 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0011B |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
817 | PS5-71-BI-0003-CC02 | [5 empty] | 6P X 2.5 OS FL RTD | 20 |  | PS5-71-IN-0002 |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0003 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
818 | PS5-71-BI-0003-CC03 | [5 empty] | 6P X 2.5 OS FL RTD | 20 |  | PS5-71-IN-0002 |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0003 |  |  |  | Powergen Building | M32 |  |  | Note 9 |  | GlandSrc:M32; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
819 | PS5-60-BI-0006A-CC04 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IN-0002A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
820 | PS5-60-BI-0006B-CC04 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IN-0002B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
821 | PS5-60-BI-0006C-CC04 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IN-0002C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
822 | PS5-60-BI-0006D-CC04 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IN-0002D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
823 | PS5-60-BI-0006E-CC04 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IN-0002E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
824 | PS5-60-BI-0006F-CC04 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IN-0002F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
825 | PS5-60-BI-0006G-CC04 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IN-0002G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0006G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
826 | PS5-60-BI-0016A-CCO4 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IE-0001A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
827 | PS5-60-BI-0016B-CCO4 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IE-0001B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
828 | PS5-60-BI-0016C-CCO4 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IE-0001C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
829 | PS5-60-BI-0016D-CCO4 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IE-0001D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
830 | PS5-60-BI-0016E-CCO4 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IE-0001E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
831 | PS5-60-BI-0016F-CCO4 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IE-0001F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
832 | PS5-60-BI-0016G-CCO4 | [5 empty] | 6T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IE-0001G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
833 | PS5-60-BI-0008A-CC01 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 105 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0008A |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
834 | PS5-60-BI-0008B-CC01 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 105 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0008B |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
835 | PS5-60-BI-0009A-CC01 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 100 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0009A |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
836 | PS5-60-BI-0009B-CC01 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 100 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0009B |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
837 | PS5-60-BI-0010A-CC01 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 100 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0010A |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
838 | PS5-60-BI-0010B-CC01 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 100 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0010B |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
839 | PS5-60-BI-0011A-CC01 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 95 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0011A |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
840 | PS5-60-BI-0011B-CC01 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 95 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0011B |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
841 | PS5-60-BI-0012A-CC01 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 90 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0012A |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
842 | PS5-60-BI-0012B-CC01 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 90 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0012B |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
843 | PS5-60-BI-0013A-CC01 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 85 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0013A |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
844 | PS5-60-BI-0013B-CC01 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 85 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0013B |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
845 | PS5-60-BI-0014A-CC01 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 80 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0014A |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
846 | PS5-60-BI-0014B-CC01 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 80 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0014B |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
847 | PS5-60-BI-0016A-CC02 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 155 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016A |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
848 | PS5-60-BI-0016B-CC02 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 145 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016B |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
849 | PS5-60-BI-0016C-CC02 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 135 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016C |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
850 | PS5-60-BI-0016D-CC02 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 130 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016D |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
851 | PS5-60-BI-0016E-CC02 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 120 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016E |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
852 | PS5-60-BI-0016F-CC02 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 115 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016F |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
853 | PS5-60-BI-0016G-CC02 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 105 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0016G |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
854 | PS5-60-BI-0004A-CCO1 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IE-0001A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0004A |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
855 | PS5-60-BI-0004B-CCO1 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IE-0001B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0004B |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
856 | PS5-60-BI-0004C-CCO1 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IE-0001C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0004C |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
857 | PS5-60-BI-0004D-CCO1 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IE-0001D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0004D |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
858 | PS5-60-BI-0004E-CCO1 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IE-0001E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0004E |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
859 | PS5-60-BI-0004F-CCO1 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IE-0001F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0004F |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
860 | PS5-60-BI-0004G-CCO1 | [5 empty] | 12T X 0.75 IS/OS FL RTD | 40 |  | PS5-60-IE-0001G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0004G |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
861 | PS5-71-BI-0009-CC01 | [5 empty] | 6T X 2.5 OS FL RTD | 20 |  | PS5-71-IN-0001 |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0009 |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
862 | PS5-71-BI-0011A-CC01 | [5 empty] | 6T X 2.5 OS FL RTD | 20 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0011A |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
863 | PS5-71-BI-0011A-CC02 | [5 empty] | 6T X 2.5 OS FL RTD | 20 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0011A |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
864 | PS5-71-BI-0011A-CC05 | [5 empty] | 6T X 2.5 OS FL RTD | 20 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0011A |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
865 | PS5-71-BI-0011B-CC01 | [5 empty] | 6T X 2.5 OS FL RTD | 20 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0011B |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
866 | PS5-71-BI-0011B-CC02 | [5 empty] | 6T X 2.5 OS FL RTD | 20 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0011B |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
867 | PS5-71-BI-0011B-CC05 | [5 empty] | 6T X 2.5 OS FL RTD | 20 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-BI-0011B |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
868 | PS5-03-GDIR-0901-CC01 | [5 empty] | 1T X 1.5 OS FR | 190 |  | PS5-03-GDIR-0901 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
869 | PS5-03-GDIR-0902-CC01 | [5 empty] | 1T X 1.5 OS FR | 190 |  | PS5-03-GDIR-0902 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
870 | PS5-03-GDIR-0903-CC01 | [5 empty] | 1T X 1.5 OS FR | 190 |  | PS5-03-GDIR-0903 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
871 | PS5-03-GDIR-0904-CC01 | [5 empty] | 1T X 1.5 OS FR | 190 |  | PS5-03-GDIR-0904 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
872 | PS5-03-GDIR-0906-CC01 | [5 empty] | 1T X 1.5 OS FR | 190 |  | PS5-03-GDIR-0906 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
873 | PS5-03-GDIR-0907-CC01 | [5 empty] | 1T X 1.5 OS FR | 190 |  | PS5-03-GDIR-0907 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
874 | PS5-03-GDIR-0908-CC01 | [5 empty] | 1T X 1.5 OS FR | 190 |  | PS5-03-GDIR-0908 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
875 | PS5-03-GDIR-0909-CC01 | [5 empty] | 1T X 1.5 OS FR | 190 |  | PS5-03-GDIR-0909 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 06
876 | PS5-03-GDIR-1001-CC01 | [5 empty] | 1T X 1.5 OS FR | 170 |  | PS5-03-GDIR-1001 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
877 | PS5-03-GDIR-1002-CC01 | [5 empty] | 1T X 1.5 OS FR | 170 |  | PS5-03-GDIR-1002 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
878 | PS5-03-GDIR-1003-CC01 | [5 empty] | 1T X 1.5 OS FR | 170 |  | PS5-03-GDIR-1003 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
879 | PS5-03-GDIR-1004-CC01 | [5 empty] | 1T X 1.5 OS FR | 170 |  | PS5-03-GDIR-1004 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
880 | PS5-03-GDIR-1006-CC01 | [5 empty] | 1T X 1.5 OS FR | 170 |  | PS5-03-GDIR-1006 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
881 | PS5-03-GDIR-1007-CC01 | [5 empty] | 1T X 1.5 OS FR | 170 |  | PS5-03-GDIR-1007 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
882 | PS5-03-GDIR-1008-CC01 | [5 empty] | 1T X 1.5 OS FR | 170 |  | PS5-03-GDIR-1008 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
883 | PS5-03-GDIR-1009-CC01 | [5 empty] | 1T X 1.5 OS FR | 170 |  | PS5-03-GDIR-1009 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
884 | PS5-03-GDIR-1101-CC01 | [5 empty] | 1T X 1.5 OS FR | 155 |  | PS5-03-GDIR-1101 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
885 | PS5-03-GDIR-1102-CC01 | [5 empty] | 1T X 1.5 OS FR | 155 |  | PS5-03-GDIR-1102 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
886 | PS5-03-GDIR-1103-CC01 | [5 empty] | 1T X 1.5 OS FR | 155 |  | PS5-03-GDIR-1103 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
887 | PS5-03-GDIR-1104-CC01 | [5 empty] | 1T X 1.5 OS FR | 155 |  | PS5-03-GDIR-1104 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
888 | PS5-03-GDIR-1106-CC01 | [5 empty] | 1T X 1.5 OS FR | 155 |  | PS5-03-GDIR-1106 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
889 | PS5-03-GDIR-1107-CC01 | [5 empty] | 1T X 1.5 OS FR | 155 |  | PS5-03-GDIR-1107 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
890 | PS5-03-GDIR-1108-CC01 | [5 empty] | 1T X 1.5 OS FR | 155 |  | PS5-03-GDIR-1108 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
891 | PS5-03-GDIR-1109-CC01 | [5 empty] | 1T X 1.5 OS FR | 155 |  | PS5-03-GDIR-1109 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
892 | PS5-03-GDIR-1201-CC01 | [5 empty] | 1T X 1.5 OS FR | 150 |  | PS5-03-GDIR-1201 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
893 | PS5-03-GDIR-1202-CC01 | [5 empty] | 1T X 1.5 OS FR | 150 |  | PS5-03-GDIR-1202 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
894 | PS5-03-GDIR-1203-CC01 | [5 empty] | 1T X 1.5 OS FR | 150 |  | PS5-03-GDIR-1203 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
895 | PS5-03-GDIR-1204-CC01 | [5 empty] | 1T X 1.5 OS FR | 150 |  | PS5-03-GDIR-1204 |  |  |  | Powergen Bldg |  |  | PS5-60-SEA-0001 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
896 | PS5-60-IE-0003B-CA02 | [5 empty] | RS485 MODBUS | 20 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
897 | PS5-60-IE-0003C-CA02 | [5 empty] | RS485 MODBUS | 20 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
898 | PS5-60-IE-0003D-CA02 | [5 empty] | RS485 MODBUS | 20 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
899 | PS5-60-IE-0003E-CA02 | [5 empty] | RS485 MODBUS | 20 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
900 | PS5-60-IE-0003F-CA02 | [5 empty] | RS485 MODBUS | 20 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
901 | PS5-60-IE-0004-CC01 | [5 empty] | RS485 MODBUS | 45 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
902 | PS5-60-IE-0004-CC02 | [5 empty] | RS485 MODBUS | 45 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
903 | PS5-60-IE-0004-CC03 | [5 empty] | RS485 MODBUS | 45 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
904 | PS5-60-IE-0004-CC04 | [5 empty] | RS485 MODBUS | 45 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
905 | PS5-60-IE-0004-CC05 | [5 empty] | RS485 MODBUS | 50 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
906 | PS5-60-IE-0004-CC06 | [5 empty] | RS485 MODBUS | 50 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
907 | PS5-71-IN-0001-CA11 | [5 empty] | RS485 MODBUS | 45 |  | PS5-71-IN-0001 |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0003A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
908 | PS5-71-IN-0004A-CC11 | [5 empty] | RS485 MODBUS | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0004A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
909 | PS5-71-IN-0004A-CC13 | [5 empty] | RS485 MODBUS | 35 |  | PS5-71-IN-0004A |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0004B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
910 | PS5-71-IN-0004B-CC11 | [5 empty] | RS485 MODBUS | 35 |  | PS5-71-IN-0004B |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0001 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
911 | PS5-60-IE-0004-CC07 | [5 empty] | RS485 MODBUS | 50 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IE-0004 |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
912 | PS5-71-IN-0004A-CC10 | [5 empty] | RS485 MODBUS | 30 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-71-IN-0004A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 06
913 | PS5-60-BI-0008A-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 115 |  | PS5-60-IH-0001A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0008A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
914 | PS5-60-BI-0008B-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 115 |  | PS5-60-IH-0001A |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0008B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
915 | PS5-60-BI-0009A-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 110 |  | PS5-60-IH-0001B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0009A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
916 | PS5-60-BI-0009B-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 110 |  | PS5-60-IH-0001B |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0009B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
917 | PS5-60-BI-0010A-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 105 |  | PS5-60-IH-0001C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0010A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
918 | PS5-60-BI-0010B-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 105 |  | PS5-60-IH-0001C |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0010B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
919 | PS5-60-BI-0011A-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 100 |  | PS5-60-IH-0001D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0011A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
920 | PS5-60-BI-0011B-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 100 |  | PS5-60-IH-0001D |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0011B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
921 | PS5-60-BI-0012A-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 95 |  | PS5-60-IH-0001E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0012A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
922 | PS5-60-BI-0012B-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 95 |  | PS5-60-IH-0001E |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0012B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
923 | PS5-60-BI-0013A-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 90 |  | PS5-60-IH-0001F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0013A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
924 | PS5-60-BI-0013B-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 90 |  | PS5-60-IH-0001F |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0013B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
925 | PS5-60-BI-0014A-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 85 |  | PS5-60-IH-0001G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0014A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
926 | PS5-60-BI-0014B-CC02 | [5 empty] | 6P X 0.75 OS FL RTD | 85 |  | PS5-60-IH-0001G |  |  |  | Powergen Bldg |  |  | PS5-60-BI-0014B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
927 | PS5-61-BI-0001-CC01 | [5 empty] | 12P X 2.5 OS FL RTD | 210 |  | PS5-60-IE-0003A |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0001 |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=3 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0050
928 | PS5-61-BI-0002-CC01 | [5 empty] | 12P X 2.5 OS FL RTD | 210 |  | PS5-60-IE-0003B |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0002 |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=2 C=0 | 05 |  | 2026-04-24 00:00:00 | CPP-RFI-68-64-04-0054
929 | PS5-61-BI-0003-CC01 | [5 empty] | 12P X 2.5 OS FL RTD | 200 |  | PS5-60-IE-0003C |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0003 |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=3 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0050
930 | PS5-61-BI-0004-CC01 | [5 empty] | 12P X 2.5 OS FL RTD | 200 |  | PS5-60-IE-0003D |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0004 |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=3 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0050
931 | PS5-61-BI-0005-CC01 | [5 empty] | 12P X 2.5 OS FL RTD | 175 |  | PS5-60-IE-0003E |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0005 |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=3 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0050
932 | PS5-61-BI-0006-CC01 | [5 empty] | 12P X 2.5 OS FL RTD | 170 |  | PS5-60-IE-0003F |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0006 |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=3 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0050
933 | PS5-61-BI-0007-CC01 | [5 empty] | 12P X 2.5 OS FL RTD | 170 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-61-BI-0007 |  |  |  | Powergen Building | M40 |  |  | Note 9 |  | GlandSrc:M40; Powergen building internal cable connections. Cable supply by CONTRACTOR; A=0 B=3 C=0 | 05 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0050
934 | PS5-60-IH-0001A-CA01 | [5 empty] | RS485 MODBUS | 140 |  | PS5-60-IE-0003G |  |  |  | Powergen Bldg |  |  | PS5-60-IH-0001A |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
935 | PS5-60-IH-0001B-CA01 | [5 empty] | RS485 MODBUS | 135 |  | PS5-60-IE-0001B |  |  |  | Powergen Bldg |  |  | PS5-60-IH-0001B |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
936 | PS5-60-IH-0001C-CA01 | [5 empty] | RS485 MODBUS | 125 |  | PS5-60-IE-0001C |  |  |  | Powergen Bldg |  |  | PS5-60-IH-0001C |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
937 | PS5-60-IH-0001D-CA01 | [5 empty] | RS485 MODBUS | 115 |  | PS5-60-IE-0001D |  |  |  | Powergen Bldg |  |  | PS5-60-IH-0001D |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
938 | PS5-60-IH-0001E-CA01 | [5 empty] | RS485 MODBUS | 105 |  | PS5-60-IE-0001E |  |  |  | Powergen Bldg |  |  | PS5-60-IH-0001E |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
939 | PS5-60-IH-0001F-CA01 | [5 empty] | RS485 MODBUS | 100 |  | PS5-60-IE-0001F |  |  |  | Powergen Bldg |  |  | PS5-60-IH-0001F |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
940 | PS5-60-IH-0001G-CA01 | [5 empty] | RS485 MODBUS | 90 |  | PS5-60-IE-0001G |  |  |  | Powergen Bldg |  |  | PS5-60-IH-0001G |  |  |  | Powergen Building | M25 |  |  | Note 9 |  | GlandSrc:M25; Powergen building internal cable connections. Cable supply by CONTRACTOR | 05
941 | PS5-60-LA-0003-CC02 | [5 empty] | CAT 6A INDOOR | 35 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0003 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
942 | PS5-60-LA-0003-CC03 | [5 empty] | CAT 6A INDOOR | 35 |  | PS5-60-IE-0004 |  |  |  | Powergen Bldg |  |  | PS5-60-LA-0003 |  |  |  | Powergen Building | M20 |  |  | Note 9 |  | GlandSrc:M20; Powergen building internal cable connections. Cable supply by Telecoms | 06
943 | PS5-75-LA-6200-CX01 | [5 empty] | 24C SM FIBER OPTIC FR | 445 |  | PS5-75-LA-6200 |  |  |  | Skid |  |  | PS5-04-PNC-0001 |  |  |  | 33kV EITS Building | M20 |  |  | TZ-MID-68-SSF1-161401 |  | GlandSrc:M20; DRA Package interface. Cable Supply by Telecoms; A=0 B=1 C=0 | 07 |  | 2026-05-20 00:00:00 | CPP-RFI-68-64-04-0049

## Telecom Cable Schedule
PROJECT NO. : 415000-00095
Cable Details | [9 empty] | From Equipment | [6 empty] | To Equipment
Sr. No. | Cable Tag. | Voltage Grade | Type | System Voltage | Drum No | Cores | Size (mm²) | Actual length laying done (m) | planned Length (m) | Tag No. | Cub. Ref | Description | G&T completed | Location | Gland Type | Entry Thread | Tag No. | Cub. Ref | Description | G&T Completed | Location | Gland Type | Entry Thread | Cable routing plan | Cable Routing Drawing | Outer Diameter (mm) | Remarks | Rev | DPS | Cable pulling date | Cable laying RFI Num | Drum tested RFI | Coiled length
1 | PS5-08-01MP-0001-CC01 |  | G3 |  |  |  | 10P X 2.5 OS GSWB FR | 50 |  | PS5-08-13CB-1001 |  | SII SP3 SAF CABINET |  | EITS BLDG | - |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M50S 50S-E1FX
2 | PS5-08-01MP-0001-CC02 |  | G3 |  |  |  | 10P X 2.5 OS GSWB FR | 50 |  | PS5-08-13CB-1001 |  | SII SP3 SAF CABINET |  | EITS BLDG | - |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M50S 50S-E1FX
3 | PS5-08-01MP-0001-CC03 |  | G3 |  |  |  | 10P X 2.5 OS GSWB FR | 50 |  | PS5-08-13CB-1001 |  | SII SP3 SAF CABINET |  | EITS BLDG | - |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M50S 50S-E1FX
4 | PS5-08-01MP-0001-CC04 |  | G3 |  |  |  | 10P X 2.5 OS GSWB FR | 50 |  | PS5-08-13CB-1001 |  | SII SP3 SAF CABINET |  | EITS BLDG | - |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M50S 50S-E1FX
5 | PS5-08-01LS-0101-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 30 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | EITS BLDG | M20 20-E1FX |  | PS5-08-01LS-0101 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
6 | PS5-08-01LS-0102-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 80 |  | PS5-08-01LS-0101 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0102 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
7 | PS5-08-01BT-0003-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 245 |  | PS5-08-01LS-0102 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-0003 |  | PAGA JUNCTION BOX |  | SECONDARY MUSTER AREA | M20 20-E1FX
8 | PS5-08-01BT-0003-CR02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 5 |  | PS5-08-01OC-0002 |  | OVERRIDE CONTROL UNIT |  | SECONDARY MUSTER AREA | M20 20-E1FX |  | PS5-08-01BT-0003 |  | PAGA JUNCTION BOX |  | SECONDARY MUSTER AREA | M20 20-E1FX
9 | PS5-08-01LS-0103-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 5 |  | PS5-08-01OC-0002 |  | OVERRIDE CONTROL UNIT |  | SECONDARY MUSTER AREA | M20 20-E1FX |  | PS5-08-01LS-0103 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX
10 | PS5-08-01LS-0104-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 165 |  | PS5-08-01BT-0003 |  | PAGA JUNCTION BOX |  | SECONDARY MUSTER AREA | M20 20-E1FX |  | PS5-08-01LS-0104 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX
11 | PS5-08-01LS-0105-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 40 |  | PS5-08-01LS-0104 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0105 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
12 | PS5-08-01LS-0106-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 50 |  | PS5-08-01LS-0105 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0106 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
13 | PS5-08-01LS-0107-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 55 |  | PS5-08-01LS-0106 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0107 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
14 | PS5-08-01LS-0108-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 80 |  | PS5-08-01LS-0107 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0108 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
15 | PS5-08-01LS-0109-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 115 |  | PS5-08-01LS-0108 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0109 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
16 | PS5-08-01LS-0110-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 105 |  | PS5-08-01LS-0109 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0110 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=2 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
17 | PS5-08-01LS-0110-CR02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 110 |  | PS5-08-01LS-0110 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
18 | PS5-08-01LS-0201-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 115 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0201 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
19 | PS5-08-01BT-0004-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 280 |  | PS5-08-01LS-0201 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-0004 |  | PAGA JUNCTION BOX |  | SECONDARY MUSTER AREA | M20 20-E1FX
20 | PS5-08-01BT-0004-CR02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 5 |  | PS5-08-01OC-0002 |  | OVERRIDE CONTROL UNIT |  | SECONDARY MUSTER AREA | M20 20-E1FX |  | PS5-08-01BT-0004 |  | PAGA JUNCTION BOX |  | SECONDARY MUSTER AREA | M20 20-E1FX
21 | PS5-08-01LS-0202-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 5 |  | PS5-08-01OC-0002 |  | OVERRIDE CONTROL UNIT |  | SECONDARY MUSTER AREA | M20 20-E1FX |  | PS5-08-01LS-0202 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX
22 | PS5-08-01LS-0203-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 170 |  | PS5-08-01BT-0004 |  | PAGA JUNCTION BOX |  | SECONDARY MUSTER AREA | M20 20-E1FX |  | PS5-08-01LS-0203 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX
23 | PS5-08-01LS-0204-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 50 |  | PS5-08-01LS-0203 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0204 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
24 | PS5-08-01LS-0205-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 75 |  | PS5-08-01LS-0204 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0205 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
25 | PS5-08-01LS-0206-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 55 |  | PS5-08-01LS-0205 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0206 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
26 | PS5-08-01LS-0207-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 80 |  | PS5-08-01LS-0206 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0207 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
27 | PS5-08-01LS-0208-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 60 |  | PS5-08-01LS-0207 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0208 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
28 | PS5-08-01LS-0209-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 50 |  | PS5-08-01LS-0208 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0209 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
29 | PS5-08-01LS-0210-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 75 |  | PS5-08-01LS-0209 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0210 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
30 | PS5-08-01LS-0211-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 60 |  | PS5-08-01LS-0210 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0211 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
31 | PS5-08-01LS-0211-CR02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 50 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0211 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
32 | PS5-08-01LS-0301-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 350 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0301 |  | PAGA LOUDSPEAKER (EX) |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
33 | PS5-08-01LS-0302-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 140 |  | PS5-08-01LS-0301 |  | PAGA LOUDSPEAKER (EX) |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0302 |  | PAGA LOUDSPEAKER (EX) |  | FIELD | M20 20-E1FX |  |  |  |  | A=2 B=1 C=0 | 06 |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
34 | PS5-08-01LS-0303-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 165 |  | PS5-08-01LS-0302 |  | PAGA LOUDSPEAKER (EX) |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0303 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 | 06 |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
35 | PS5-08-01LS-0304-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 75 |  | PS5-08-01LS-0303 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0304 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX
36 | PS5-08-01LS-0305-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 170 |  | PS5-08-01LS-0304 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0305 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX
37 | PS5-08-01LS-0306-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 25 |  | PS5-08-01LS-0305 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0306 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
38 | PS5-08-01LS-0307-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 55 |  | PS5-08-01LS-0306 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0307 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=0 B=1 C=0 |  |  | 2026-07-01 00:00:00 | CPP-RFI-68-65-05-0034
39 | PS5-08-01BT-1501-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 110 |  | PS5-08-01LS-0307 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-1501 |  | PAGA JUNCTION BOX |  | GUARD HOUSE | M20 20-E1FX
40 | PS5-08-01LS-0308-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 5 |  | PS5-08-01BT-1501 |  | PAGA JUNCTION BOX |  | GUARD HOUSE | M20 20A2 |  | PS5-08-01LS-0308 |  | PAGA LOUDSPEAKER |  | GUARD HOUSE | M20 20DTSP2TN
41 | PS5-08-01LS-0309-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0308 |  | PAGA LOUDSPEAKER |  | GUARD HOUSE | M20 20DTSP2TN |  | PS5-08-01LS-0309 |  | PAGA LOUDSPEAKER |  | GUARD HOUSE | M20 20DTSP2TN
42 | PS5-08-01LS-0309-CR02 |  | G1 |  |  |  | 1P X 2.5 OS FR |  |  | PS5-08-01BT-1501 |  | PAGA JUNCTION BOX |  | GUARD HOUSE |  |  | PS5-08-01LS-0309 |  | PAGA LOUDSPEAKER |  | GUARD HOUSE
43 | PS5-08-01LS-0310-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 250 |  | PS5-08-01BT-1501 |  | PAGA JUNCTION BOX |  | GUARD HOUSE | M20 20-E1FX |  | PS5-08-01LS-0310 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX
44 | PS5-08-01LS-0310-CR02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 70 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0310 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX
45 | PS5-08-01LS-0401-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 280 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0401 |  | PAGA LOUDSPEAKER (EX) |  | FIELD | M20 20-E1FX |  |  |  |  | A=0 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
46 | PS5-08-01LS-0402-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 105 |  | PS5-08-01LS-0401 |  | PAGA LOUDSPEAKER (EX) |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0402 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=0 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
47 | PS5-08-01LS-0403-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 170 |  | PS5-08-01LS-0402 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0403 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
48 | PS5-08-01LS-0404-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 45 |  | PS5-08-01LS-0403 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0404 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=0 B=1 C=0 |  |  | 2026-07-01 00:00:00 | CPP-RFI-68-65-05-0034
49 | PS5-08-01LS-0405-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 20 |  | PS5-08-01LS-0404 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0405 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=0 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
50 | PS5-08-01BT-1502-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 185 |  | PS5-08-01LS-0405 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-1502 |  | PAGA JUNCTION BOX |  | GUARD HOUSE | M20 20-E1FX
51 | PS5-08-01LS-0406-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01BT-1502 |  | PAGA JUNCTION BOX |  | GUARD HOUSE | M20 20A2 |  | PS5-08-01LS-0406 |  | PAGA LOUDSPEAKER |  | GUARD HOUSE | M20 20DTSP2TN
52 | PS5-08-01LS-0407-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0406 |  | PAGA LOUDSPEAKER |  | GUARD HOUSE | M20 20DTSP2TN |  | PS5-08-01LS-0407 |  | PAGA LOUDSPEAKER |  | GUARD HOUSE | M20 20DTSP2TN
53 | PS5-08-01LS-0408-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0407 |  | PAGA LOUDSPEAKER |  | GUARD HOUSE | M20 20DTSP2TN |  | PS5-08-01LS-0408 |  | PAGA LOUDSPEAKER |  | GUARD HOUSE | M20 20DTSP2TN
54 | PS5-08-01LS-0408-CR02 |  | G1 |  |  |  | 1P X 2.5 OS FR |  |  | PS5-08-01BT-1502 |  | PAGA JUNCTION BOX |  | GUARD HOUSE |  |  | PS5-08-01LS-0408 |  | PAGA LOUDSPEAKER |  | GUARD HOUSE
55 | PS5-08-01LS-0409-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 30 |  | PS5-08-01BT-1502 |  | PAGA JUNCTION BOX |  | GUARD HOUSE | M20 20-E1FX |  | PS5-08-01LS-0409 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX
56 | PS5-08-01LS-0410-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 190 |  | PS5-08-01LS-0409 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0410 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX
57 | PS5-08-01LS-0411-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 165 |  | PS5-08-01LS-0410 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0411 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX
58 | PS5-08-01LS-0411-CR02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 35 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01LS-0411 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-04-12 00:00:00 | CPP-RFI-68-65-05-0024
59 | PS5-08-01BT-1903-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 100 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-1903 |  | PAGA JUNCTION BOX |  | POWER GEN BLDG | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
60 | PS5-08-01LS-0501-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01BT-1903 |  | PAGA JUNCTION BOX |  | POWER GEN BLDG | M20 20A2 |  | PS5-08-01LS-0501 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
61 | PS5-08-01LS-0502-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 50 |  | PS5-08-01LS-0501 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0502 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
62 | PS5-08-01LS-0503-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 25 |  | PS5-08-01LS-0502 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0503 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
63 | PS5-08-01LS-0504-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 45 |  | PS5-08-01LS-0503 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0504 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
64 | PS5-08-01LS-0505-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 20 |  | PS5-08-01LS-0504 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0505 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
65 | PS5-08-01LS-0506-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 45 |  | PS5-08-01LS-0505 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0506 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
66 | PS5-08-01LS-0507-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 50 |  | PS5-08-01LS-0506 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0507 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
67 | PS5-08-01LS-0508-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 25 |  | PS5-08-01LS-0507 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0508 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
68 | PS5-08-01LS-0509-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 30 |  | PS5-08-01LS-0508 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0509 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
69 | PS5-08-01LS-0510-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 25 |  | PS5-08-01LS-0509 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0510 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
70 | PS5-08-01LS-0511-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 50 |  | PS5-08-01LS-0510 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0511 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
71 | PS5-08-01LS-0512-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 40 |  | PS5-08-01LS-0511 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0512 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E
72 | PS5-08-01LS-0517-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 35 |  | PS5-08-01LS-0512 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E |  | PS5-08-01LS-0517 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E
73 | PS5-08-01LS-0518-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 20 |  | PS5-08-01LS-0517 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E |  | PS5-08-01LS-0518 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
74 | PS5-08-01LS-0519-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 35 |  | PS5-08-01LS-0518 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0519 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E
75 | PS5-08-01LS-0520-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 35 |  | PS5-08-01LS-0519 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E |  | PS5-08-01LS-0520 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E
76 | PS5-08-01LS-0521-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 25 |  | PS5-08-01LS-0520 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E |  | PS5-08-01LS-0521 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E
77 | PS5-08-01LS-0522-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 35 |  | PS5-08-01LS-0521 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E |  | PS5-08-01LS-0522 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
78 | PS5-08-01LS-0522-CR02 |  | G1 |  |  |  | 1P X 2.5 OS FR | 95 |  | PS5-08-01BT-1903 |  | PAGA JUNCTION BOX |  | POWER GEN BLDG | M20 20A2 |  | PS5-08-01LS-0522 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
79 | PS5-08-01BT-1901-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 30 |  | PS5-08-01BT-1903 |  | PAGA JUNCTION BOX |  | POWER GEN BLDG | M20 20-E1FX |  | PS5-08-01BT-1901 |  | PAGA JUNCTION BOX |  | GEN. ELECT. BLDG | M20 20-E1FX
80 | PS5-08-01LS-0523-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 5 |  | PS5-08-01BT-1901 |  | PAGA JUNCTION BOX |  | GEN. ELECT. BLDG | M20 20A2 |  | PS5-08-01LS-0523 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN
81 | PS5-08-01LS-0524-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 45 |  | PS5-08-01LS-0523 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0524 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN
82 | PS5-08-01LS-0525-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 20 |  | PS5-08-01LS-0524 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0525 |  | PAGA LOUDSPEAKER (EX) |  | GEN. ELECT. BLDG | M20 20A2E
83 | PS5-08-01LS-0526-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0525 |  | PAGA LOUDSPEAKER (EX) |  | GEN. ELECT. BLDG | M20 20A2E |  | PS5-08-01LS-0526 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN
84 | PS5-08-01LS-0527-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 5 |  | PS5-08-01LS-0526 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0527 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN
85 | PS5-08-01LS-0528-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0527 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0528 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN
86 | PS5-08-01LS-0529-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 5 |  | PS5-08-01LS-0528 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0529 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN
87 | PS5-08-01LS-0530-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 25 |  | PS5-08-01LS-0529 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0530 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN
88 | PS5-08-01LS-0530-CR02 |  | G1 |  |  |  | 1P X 2.5 OS FR | 25 |  | PS5-08-01BT-1901 |  | PAGA JUNCTION BOX |  | GEN. ELECT. BLDG | M20 20A2 |  | PS5-08-01LS-0530 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN
89 | PS5-08-01BT-1901-CR02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 180 |  | PS5-08-01BT-1901 |  | PAGA JUNCTION BOX |  | POWER GEN BLDG | M20 20-E1FX |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  |  |  |  | A=0 B=1 C=0 |  |  | 2026-07-01 00:00:00 | CPP-RFI-68-65-05-0034
90 | PS5-08-01BT-1904-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 125 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-1904 |  | PAGA JUNCTION BOX |  | POWER GEN BLDG | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
91 | PS5-08-01LS-0601-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 5 |  | PS5-08-01BT-1904 |  | PAGA JUNCTION BOX |  | POWER GEN BLDG | M20 20A2 |  | PS5-08-01LS-0601 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
92 | PS5-08-01LS-0602-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 45 |  | PS5-08-01LS-0601 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0602 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
93 | PS5-08-01LS-0603-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 35 |  | PS5-08-01LS-0602 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0603 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
94 | PS5-08-01LS-0604-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 40 |  | PS5-08-01LS-0603 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0604 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
95 | PS5-08-01LS-0605-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 50 |  | PS5-08-01LS-0604 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0605 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
96 | PS5-08-01LS-0606-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 20 |  | PS5-08-01LS-0605 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0606 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
97 | PS5-08-01LS-0607-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 40 |  | PS5-08-01LS-0606 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0607 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
98 | PS5-08-01LS-0608-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 35 |  | PS5-08-01LS-0607 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0608 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
99 | PS5-08-01LS-0609-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 55 |  | PS5-08-01LS-0608 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0609 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
100 | PS5-08-01LS-0610-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0609 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0610 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
101 | PS5-08-01LS-0611-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 55 |  | PS5-08-01LS-0610 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0611 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
102 | PS5-08-01LS-0612-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 30 |  | PS5-08-01LS-0611 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0612 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E
103 | PS5-08-01LS-0617-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 40 |  | PS5-08-01LS-0612 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E |  | PS5-08-01LS-0617 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN
104 | PS5-08-01LS-0618-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 20 |  | PS5-08-01LS-0617 |  | PAGA LOUDSPEAKER |  | POWER GEN BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0618 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E
105 | PS5-08-01LS-0619-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 40 |  | PS5-08-01LS-0618 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E |  | PS5-08-01LS-0619 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E
106 | PS5-08-01LS-0620-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 35 |  | PS5-08-01LS-0619 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E |  | PS5-08-01LS-0620 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E
107 | PS5-08-01LS-0621-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 25 |  | PS5-08-01LS-0620 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E |  | PS5-08-01LS-0621 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E
108 | PS5-08-01LS-0621-CR02 |  | G1 |  |  |  | 1P X 2.5 OS FR | 105 |  | PS5-08-01LS-0621 |  | PAGA LOUDSPEAKER (EX) |  | POWER GEN BLDG | M20 20A2E |  | PS5-08-01BT-1904 |  | PAGA JUNCTION BOX |  | POWER GEN BLDG | M20 20A2
109 | PS5-08-01BT-1902-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 10 |  | PS5-08-01BT-1904 |  | PAGA JUNCTION BOX |  | POWER GEN BLDG | M20 20-E1FX |  | PS5-08-01BT-1902 |  | PAGA JUNCTION BOX |  | GEN. ELECT. BLDG | M20 20-E1FX
110 | PS5-08-01BT-1902-CR02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 170 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-1902 |  | PAGA JUNCTION BOX |  | GEN. ELECT. BLDG | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
111 | PS5-08-01LS-0622-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 30 |  | PS5-08-01BT-1902 |  | PAGA JUNCTION BOX |  | GEN. ELECT. BLDG | M20 20A2 |  | PS5-08-01LS-0622 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN
112 | PS5-08-01LS-0623-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 30 |  | PS5-08-01LS-0622 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0623 |  | PAGA LOUDSPEAKER (EX) |  | GEN. ELECT. BLDG | M20 20A2E
113 | PS5-08-01LS-0624-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 20 |  | PS5-08-01LS-0623 |  | PAGA LOUDSPEAKER (EX) |  | GEN. ELECT. BLDG | M20 20A2E |  | PS5-08-01LS-0624 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN
114 | PS5-08-01LS-0625-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0624 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0625 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN
115 | PS5-08-01LS-0626-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0625 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0626 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN
116 | PS5-08-01LS-0627-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 5 |  | PS5-08-01LS-0626 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0627 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN
117 | PS5-08-01LS-0628-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0627 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0628 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN
118 | PS5-08-01LS-0629-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 25 |  | PS5-08-01LS-0628 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0629 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN
119 | PS5-08-01LS-0629-CR02 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01BT-1902 |  | PAGA JUNCTION BOX |  | GEN. ELECT. BLDG | M20 20A2 |  | PS5-08-01LS-0629 |  | PAGA LOUDSPEAKER |  | GEN. ELECT. BLDG | M20 20DTSP2TN
120 | PS5-08-01BT-1201-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 135 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-1201 |  | PAGA JUNCTION BOX |  | OFFICE BLDG | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
121 | PS5-08-01BT-1201-CR02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 135 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-1201 |  | PAGA JUNCTION BOX |  | OFFICE BLDG | M20 20-E1FX | [5 empty] | 06
122 | PS5-08-01LS-0701-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 5 |  | PS5-08-01BT-1201 |  | PAGA JUNCTION BOX |  | OFFICE BLDG | M20 20A2 |  | PS5-08-01LS-0701 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
123 | PS5-08-01LS-0702-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0701 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0702 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
124 | PS5-08-01LS-0704-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0702 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0704 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
125 | PS5-08-01LS-0703-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0704 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0703 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
126 | PS5-08-01LS-0705-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 35 |  | PS5-08-01BT-1201 |  | PAGA JUNCTION BOX |  | OFFICE BLDG | M20 20A2 |  | PS5-08-01LS-0705 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
127 | PS5-08-01LS-0706-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0703 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0706 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
128 | PS5-08-01LS-0707-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0706 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0707 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
129 | PS5-08-01LS-0708-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0707 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0708 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
130 | PS5-08-01LS-0709-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0708 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0709 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
131 | PS5-08-01LS-0710-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0709 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0710 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
132 | PS5-08-01LS-0711-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0710 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0711 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
133 | PS5-08-01LS-0712-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01BT-1201 |  | PAGA JUNCTION BOX |  | OFFICE BLDG | M20 20A2 |  | PS5-08-01LS-0712 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
134 | PS5-08-01LS-0713-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 20 |  | PS5-08-01LS-0712 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0713 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
135 | PS5-08-01LS-0714-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0711 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0714 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
136 | PS5-08-01LS-0715-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0714 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0715 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
137 | PS5-08-01LS-0716-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 25 |  | PS5-08-01LS-0715 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0716 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
138 | PS5-08-01LS-0716-CR02 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01BT-1201 |  | PAGA JUNCTION BOX |  | OFFICE BLDG | M20 20A2 |  | PS5-08-01LS-0716 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
139 | PS5-08-01BT-0001-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 110 |  | PS5-08-01BT-1201 |  | PAGA JUNCTION BOX |  | OFFICE BLDG | M20 20-E1FX |  | PS5-08-01BT-0001 |  | PAGA JUNCTION BOX |  | PRIMARY MUSTER AREA | M20 20-E1FX
140 | PS5-08-01BT-0001-CR02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 5 |  | PS5-08-01OC-0001 |  | OVERRIDE CONTROL UNIT |  | PRIMARY MUSTER AREA | M20 20-E1FX |  | PS5-08-01BT-0001 |  | PAGA JUNCTION BOX |  | PRIMARY MUSTER AREA | M20 20-E1FX
141 | PS5-08-01LS-0719-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 5 |  | PS5-08-01OC-0001 |  | OVERRIDE CONTROL UNIT |  | PRIMARY MUSTER AREA | M20 20-E1FX |  | PS5-08-01LS-0719 |  | PAGA LOUDSPEAKER |  | PRIMARY MUSTER AREA | M20 20-E1FX
142 | PS5-08-01LS-0717-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 25 |  | PS5-08-01LS-0713 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0717 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
143 | PS5-08-01LS-0718-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0717 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0718 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
144 | PS5-08-01LS-0720-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 240 |  | PS5-08-01BT-0001 |  | PAGA JUNCTION BOX |  | PRIMARY MUSTER AREA | M20 20-E1FX |  | PS5-08-01LS-0720 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX
145 | PS5-08-01BT-1601-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 50 |  | PS5-08-01LS-0720 |  | PAGA LOUDSPEAKER |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-1601 |  | PAGA JUNCTION BOX |  | WAREHOUSE/WORKSHOP | M20 20-E1FX
146 | PS5-08-01BT-1601-CR02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 235 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-1601 |  | PAGA JUNCTION BOX |  | WAREHOUSE/WORKSHOP | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
147 | PS5-08-01LS-0721-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 5 |  | PS5-08-01BT-1601 |  | PAGA JUNCTION BOX |  | WAREHOUSE/WORKSHOP | M20 20A2 |  | PS5-08-01LS-0721 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
148 | PS5-08-01LS-0722-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0721 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0722 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
149 | PS5-08-01LS-0723-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 25 |  | PS5-08-01LS-0722 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0723 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
150 | PS5-08-01LS-0724-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0723 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0724 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
151 | PS5-08-01LS-0725-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0724 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0725 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
152 | PS5-08-01LS-0726-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 20 |  | PS5-08-01LS-0725 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0726 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
153 | PS5-08-01LS-0727-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 20 |  | PS5-08-01LS-0726 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0727 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
154 | PS5-08-01LS-0728-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0727 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0728 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
155 | PS5-08-01LS-0729-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0728 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0729 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
156 | PS5-08-01LS-0730-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 5 |  | PS5-08-01LS-0729 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0730 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
157 | PS5-08-01LS-0731-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0730 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0731 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
158 | PS5-08-01LS-0732-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 5 |  | PS5-08-01LS-0731 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0732 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
159 | PS5-08-01LS-0733-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 5 |  | PS5-08-01LS-0732 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0733 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
160 | PS5-08-01LS-0733-CR02 |  | G1 |  |  |  | 1P X 2.5 OS FR | 20 |  | PS5-08-01BT-1601 |  | PAGA JUNCTION BOX |  | WAREHOUSE/WORKSHOP | M20 20A2 |  | PS5-08-01LS-0733 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN | [5 empty] | 06
161 | PS5-08-01BT-1202-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 125 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-1202 |  | PAGA JUNCTION BOX |  | OFFICE BLDG | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
162 | PS5-08-01BT-1202-CR02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 125 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-1202 |  | PAGA JUNCTION BOX |  | OFFICE BLDG | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
163 | PS5-08-01LS-0804-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 35 |  | PS5-08-01BT-1202 |  | PAGA JUNCTION BOX |  | OFFICE BLDG | M20 20A2 |  | PS5-08-01LS-0804 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
164 | PS5-08-01LS-0801-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 20 |  | PS5-08-01BT-1202 |  | PAGA JUNCTION BOX |  | OFFICE BLDG | M20 20A2 |  | PS5-08-01LS-0801 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
165 | PS5-08-01LS-0802-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0801 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0802 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
166 | PS5-08-01LS-0803-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0802 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0803 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
167 | PS5-08-01LS-0805-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 25 |  | PS5-08-01LS-0803 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0805 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
168 | PS5-08-01LS-0806-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 20 |  | PS5-08-01LS-0805 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0806 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
169 | PS5-08-01LS-0807-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0806 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0807 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
170 | PS5-08-01LS-0808-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0807 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0808 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
171 | PS5-08-01LS-0809-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0808 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0809 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
172 | PS5-08-01LS-0810-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 25 |  | PS5-08-01LS-0809 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0810 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
173 | PS5-08-01LS-0813-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 5 |  | PS5-08-01LS-0810 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0813 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
174 | PS5-08-01LS-0814-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0813 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0814 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
175 | PS5-08-01LS-0815-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0814 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0815 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
176 | PS5-08-01LS-0816-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 20 |  | PS5-08-01LS-0815 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0816 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
177 | PS5-08-01LS-0816-CR02 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01BT-1202 |  | PAGA JUNCTION BOX |  | OFFICE BLDG | M20 20A2 |  | PS5-08-01LS-0816 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
178 | PS5-08-01LS-0811-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 35 |  | PS5-08-01BT-1202 |  | PAGA JUNCTION BOX |  | OFFICE BLDG | M20 20A2 |  | PS5-08-01LS-0811 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
179 | PS5-08-01LS-0812-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0811 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0812 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
180 | PS5-08-01LS-0817-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 20 |  | PS5-08-01LS-0812 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0817 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
181 | PS5-08-01LS-0818-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0817 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN |  | PS5-08-01LS-0818 |  | PAGA LOUDSPEAKER |  | OFFICE BLDG | M20 20DTSP2TN
182 | PS5-08-01BT-0002-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 110 |  | PS5-08-01BT-1202 |  | PAGA JUNCTION BOX |  | OFFICE BLDG | M20 20-E1FX |  | PS5-08-01BT-0002 |  | PAGA JUNCTION BOX |  | PRIMARY MUSTER AREA | M20 20-E1FX
183 | PS5-08-01BT-0002-CR02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 5 |  | PS5-08-01BT-0002 |  | PAGA JUNCTION BOX |  | PRIMARY MUSTER AREA | M20 20-E1FX |  | PS5-08-01OC-0001 |  | OVERRIDE CONTROL UNIT |  | PRIMARY MUSTER AREA | M20 20-E1FX
184 | PS5-08-01LS-0819-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 5 |  | PS5-08-01OC-0001 |  | OVERRIDE CONTROL UNIT |  | PRIMARY MUSTER AREA | M20 20-E1FX |  | PS5-08-01LS-0819 |  | PAGA LOUDSPEAKER |  | PRIMARY MUSTER AREA | M20 20-E1FX
185 | PS5-08-01BT-1602-CR01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 210 |  | PS5-08-01BT-0002 |  | PAGA JUNCTION BOX |  | PRIMARY MUSTER AREA | M20 20-E1FX |  | PS5-08-01BT-1602 |  | PAGA JUNCTION BOX |  | WAREHOUSE/WORKSHOP | M20 20-E1FX
186 | PS5-08-01BT-1602-CR02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 230 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-1602 |  | PAGA JUNCTION BOX |  | WAREHOUSE/WORKSHOP | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
187 | PS5-08-01LS-0820-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01BT-1602 |  | PAGA JUNCTION BOX |  | WAREHOUSE/WORKSHOP | M20 20A2 |  | PS5-08-01LS-0820 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
188 | PS5-08-01LS-0821-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0820 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0821 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
189 | PS5-08-01LS-0822-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 5 |  | PS5-08-01LS-0821 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0822 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
190 | PS5-08-01LS-0823-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0822 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0823 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
191 | PS5-08-01LS-0824-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0823 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0824 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
192 | PS5-08-01LS-0825-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 25 |  | PS5-08-01LS-0824 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0825 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
193 | PS5-08-01LS-0826-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 20 |  | PS5-08-01LS-0825 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0826 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
194 | PS5-08-01LS-0827-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0826 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0827 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
195 | PS5-08-01LS-0828-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 20 |  | PS5-08-01LS-0827 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0828 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
196 | PS5-08-01LS-0829-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0828 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0829 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
197 | PS5-08-01LS-0830-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 5 |  | PS5-08-01LS-0829 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0830 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
198 | PS5-08-01LS-0831-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0830 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0831 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
199 | PS5-08-01LS-0832-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0831 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0832 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
200 | PS5-08-01LS-0833-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 10 |  | PS5-08-01LS-0832 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0833 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
201 | PS5-08-01LS-0834-CR01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01LS-0833 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN |  | PS5-08-01LS-0834 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
202 | PS5-08-01LS-0834-CR02 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-01BT-1602 |  | PAGA JUNCTION BOX |  | WAREHOUSE/WORKSHOP | M20 20A2 |  | PS5-08-01LS-0834 |  | PAGA LOUDSPEAKER |  | WAREHOUSE/WORKSHOP | M20 20DTSP2TN
203 | PS5-08-01OC-0001-CJ01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 210 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01OC-0001 |  | OVERRIDE CONTROL UNIT |  | PRIMARY MUSTER AREA | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
204 | PS5-08-01OC-0001-CJ02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 210 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01OC-0001 |  | OVERRIDE CONTROL UNIT |  | PRIMARY MUSTER AREA | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
205 | PS5-08-01OC-0001-CN01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 210 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01OC-0001 |  | OVERRIDE CONTROL UNIT |  | PRIMARY MUSTER AREA | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
206 | PS5-08-01OC-0001-CN02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 210 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01OC-0001 |  | OVERRIDE CONTROL UNIT |  | PRIMARY MUSTER AREA | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
207 | PS5-08-01OC-0002-CJ01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 330 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01OC-0002 |  | OVERRIDE CONTROL UNIT |  | SECONDARY MUSTER AREA | M20 20-E1FX
208 | PS5-08-01OC-0002-CJ02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 330 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01OC-0002 |  | OVERRIDE CONTROL UNIT |  | SECONDARY MUSTER AREA | M20 20-E1FX
209 | PS5-08-01OC-0002-CN01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 330 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01OC-0002 |  | OVERRIDE CONTROL UNIT |  | SECONDARY MUSTER AREA | M20 20-E1FX
210 | PS5-08-01OC-0002-CN02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 330 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01OC-0002 |  | OVERRIDE CONTROL UNIT |  | SECONDARY MUSTER AREA | M20 20-E1FX
211 | PS5-08-01BT-1503-CJ01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 310 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-1503 |  | PAGA JUNCTION BOX |  | GUARD HOUSE | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
212 | PS5-08-01BT-1503-CJ02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 310 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-1503 |  | PAGA JUNCTION BOX |  | GUARD HOUSE | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
213 | PS5-08-01BT-1203-CJ01 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 145 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-1203 |  | PAGA JUNCTION BOX |  | OFFICE BLDG | M20 20-E1FX
214 | PS5-08-01BT-1203-CJ02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 145 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | FIELD | M20 20-E1FX |  | PS5-08-01BT-1203 |  | PAGA JUNCTION BOX |  | OFFICE BLDG | M20 20-E1FX | [7 empty] | 03-July-2026 | CPP-RFI-68-65-20-0035
215 | PS5-08-85DC-0001-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0017 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0001 |  | ACS GATE CONTACT |  | FIELD | [5 empty] | Note 12 | 06
216 | PS5-08-85ML-0001-CN01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 5 |  | PS5-08-85BT-0017 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85ML-0001 |  | MAGNETIC DOORLOCK |  | FIELD | - | [5 empty] | 06
217 | PS5-08-85PB-0001-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 5 |  | PS5-08-85BT-0017 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85PB-0001 |  | EXIT PUSHBUTTON |  | FIELD | - | [5 empty] | 06
218 | PS5-08-85BT-0017-CC01 |  | A4 |  |  |  | 6P X 1.0 GSWB FL RET | 60 |  | PS5-08-85CP-1501 |  | CONTROL PANEL |  | GUARD HOUSE | - |  | PS5-08-85BT-0017 |  | ACS JUNCTION BOX |  | FIELD | M25 25-E1X |  |  |  |  | A=1 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
219 | PS5-08-85BT-0017-CN01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 175 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARD HOUSE | - |  | PS5-08-85BT-0017 |  | ACS JUNCTION BOX |  | FIELD | 20SE1X1RA5 |  |  |  |  | A=0 B=2 C=0 | 06 |  | 19-June-2026 | CPP-RFI-68-65-05-0032
220 | PS5-08-85DC-0002-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0001 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0002 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
221 | PS5-08-85DC-0024-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0001 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0024 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
222 | PS5-08-85DC-0003-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0019 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0003 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
223 | PS5-08-85BT-0019-CC01 |  | A4 |  |  |  | 6P X 1.0 GSWB FL RET | 70 |  | PS5-08-85CP-1501 |  | CONTROL PANEL |  | GUARD HOUSE | - |  | PS5-08-85BT-0019 |  | ACS JUNCTION BOX |  | FIELD | M25 25-E1X |  |  |  |  | A=1 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
224 | PS5-82-MGV-0002-CC01 |  | A3 |  |  |  | 4P X 1.0 GSWB FL RET | 110 |  | PS5-08-85BT-0019 |  | ACS JUNCTION BOX |  | FIELD | M25 25S-E1X |  | PS5-82-MGV-0002 |  | SLIDING GATE |  | FIELD | M25 25S-E1X
225 | PS5-08-85DC-0004-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0002 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0004 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
226 | PS5-08-85BT-0002-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 35 |  | PS5-08-15CP-0004 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0002 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX |  |  |  |  | A=0 B=2 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
227 | PS5-08-85DC-0005-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0003 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0005 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
228 | PS5-08-85BT-0003-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 25 |  | PS5-08-15CP-0004 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0003 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX |  |  |  |  | A=0 B=2 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
229 | PS5-08-85DC-0006-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0004 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0006 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
230 | PS5-08-85BT-0004-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 125 |  | PS5-08-15CP-0005 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0004 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX
231 | PS5-08-85DC-0007-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0005 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0007 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
232 | PS5-08-85BT-0005-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 135 |  | PS5-08-15CP-0005 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0005 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX | [7 empty] | 2025-12-06 00:00:00 | CPP-RFI-68-65-05-0011
233 | PS5-08-85DC-0008-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0006 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0008 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
234 | PS5-08-85BT-0006-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 165 |  | PS5-08-15CP-0005 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0006 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX
235 | PS5-08-85DC-0009-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0007 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0009 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
236 | PS5-08-85BT-0007-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 185 |  | PS5-08-15CP-0005 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0007 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX | [7 empty] | 2025-12-06 00:00:00 | CPP-RFI-68-65-05-0011
237 | PS5-08-85DC-0010-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0008 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0010 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
238 | PS5-08-85BT-0008-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 330 |  | PS5-08-15CP-0007 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0008 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX
239 | PS5-08-85DC-0011-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0010 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0011 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
240 | PS5-08-85BT-0010-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 365 |  | PS5-08-15CP-0007 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0010 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX | [7 empty] | 2025-12-11 00:00:00 | CPP-RFI-68-65-05-0013
241 | PS5-08-85DC-0012-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0009 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0012 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
242 | PS5-08-85DC-0025-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0009 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0025 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
243 | PS5-08-85BT-0009-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 175 |  | PS5-08-15CP-0007 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0009 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX
244 | PS5-08-85DC-0013-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0012 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0013 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
245 | PS5-08-85BT-0012-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 350 |  | PS5-08-15CP-0007 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0012 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX
246 | PS5-08-85DC-0014-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0011 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0014 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
247 | PS5-08-85BT-0011-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 405 |  | PS5-08-15CP-0007 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0011 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX
248 | PS5-08-85DC-0015-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0013 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0015 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
249 | PS5-08-85BT-0013-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 20 |  | PS5-08-15CP-0002 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0013 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX | [7 empty] | 2025-12-15 00:00:00 | CPP-RFI-68-65-05-0015
250 | PS5-08-85DC-0016-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0014 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0016 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
251 | PS5-08-85BT-0014-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 40 |  | PS5-08-15CP-0002 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0014 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX | [7 empty] | 2026-04-10 00:00:00 | CPP-RFI-68-65-05-0023
252 | PS5-08-85DC-0017-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0015 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0017 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
253 | PS5-08-85BT-0015-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 100 |  | PS5-08-15CP-0002 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0015 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX | [7 empty] | 2025-12-15 00:00:00 | CPP-RFI-68-65-05-0015
254 | PS5-08-85DC-0018-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0016 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0018 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
255 | PS5-08-85BT-0016-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 80 |  | PS5-08-15CP-0002 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0016 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX |  |  |  |  | A=1 B=1 C=0 |  |  | 2026-07-01 00:00:00 | CPP-RFI-68-65-05-0034
256 | PS5-08-85DC-0019-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0024 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0019 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
257 | PS5-08-85DC-0026-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0024 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0026 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
258 | PS5-08-85BT-0024-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 100 |  | PS5-08-15CP-0004 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0024 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1X |  |  |  |  | A=0 B=2 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
259 | PS5-08-85BT-0021-CC01 |  | A4 |  |  |  | 6P X 1.0 GSWB FL RET | 45 |  | PS5-08-85CP-1501 |  | CONTROL PANEL |  | GUARD HOUSE | - |  | PS5-08-85BT-0021 |  | ACS JUNCTION BOX |  | FIELD | M25 25-E1X |  |  |  |  | A=1 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
260 | PS5-82-MBA-0001-CC01 |  | A3 |  |  |  | 4P X 1.0 GSWB FL RET | 15 |  | PS5-08-85BT-0021 |  | ACS JUNCTION BOX |  | FIELD | M25 25S-E1X |  | PS5-82-MBA-0001 |  | VEHICLE BARRIER |  | FIELD | M25 25S-E1X
261 | PS5-08-85BR-0005-CC01 |  | A2 |  |  |  | 2P X 1.0 GSWB FL RET | 45 |  | PS5-08-85CP-1501 |  | CONTROL PANEL |  | GUARD HOUSE | - |  | PS5-08-85BR-0005 |  | BADGE READER |  | FIELD | - |  |  |  |  | A=1 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
262 | PS5-08-85BR-0006-CC01 |  | A2 |  |  |  | 2P X 1.0 GSWB FL RET | 45 |  | PS5-08-85CP-1501 |  | CONTROL PANEL |  | GUARD HOUSE | - |  | PS5-08-85BR-0006 |  | BADGE READER |  | FIELD | - |  |  |  |  | A=1 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
263 | PS5-08-85BT-0022-CC01 |  | A4 |  |  |  | 6P X 1.0 GSWB FL RET | 40 |  | PS5-08-85CP-1501 |  | CONTROL PANEL |  | GUARD HOUSE | - |  | PS5-08-85BT-0022 |  | ACS JUNCTION BOX |  | FIELD | M25 25-E1X |  |  |  |  | A=1 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
264 | PS5-82-MTL-0001-CC01 |  | A3 |  |  |  | 4P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0022 |  | ACS JUNCTION BOX |  | FIELD | M25 25S-E1X |  | PS5-82-MTL-0001 |  | TURNSTILE |  | FIELD | M25 25S-E1X
265 | PS5-08-85BR-0003-CC01 |  | A2 |  |  |  | 2P X 1.0 GSWB FL RET | 40 |  | PS5-08-85CP-1501 |  | CONTROL PANEL |  | GUARD HOUSE | - |  | PS5-08-85BR-0003 |  | BADGE READER |  | FIELD | - |  |  |  |  | A=1 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
266 | PS5-08-85BR-0004-CC01 |  | A2 |  |  |  | 2P X 1.0 GSWB FL RET | 40 |  | PS5-08-85CP-1501 |  | CONTROL PANEL |  | GUARD HOUSE | - |  | PS5-08-85BR-0004 |  | BADGE READER |  | FIELD | - |  |  |  |  | A=1 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
267 | PS5-08-85DC-0021-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0025 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0021 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
268 | PS5-08-85DC-0027-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0025 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0027 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
269 | PS5-08-85BT-0025-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 150 |  | PS5-08-15CP-0004 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0025 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1X |  |  |  |  | A=0 B=2 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
270 | PS5-08-85BT-0020-CC01 |  | A4 |  |  |  | 6P X 1.0 GSWB FL RET | 35 |  | PS5-08-85CP-1501 |  | CONTROL PANEL |  | GUARD HOUSE | - |  | PS5-08-85BT-0020 |  | ACS JUNCTION BOX |  | FIELD | M25 25-E1X |  |  |  |  | A=1 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
271 | PS5-82-MBA-0003-CC01 |  | A3 |  |  |  | 4P X 1.0 GSWB FL RET | 15 |  | PS5-08-85BT-0020 |  | ACS JUNCTION BOX |  | FIELD | M25 25S-E1X |  | PS5-82-MBA-0003 |  | VEHICLE BARRIER |  | FIELD | M25 25S-E1X
272 | PS5-08-85BR-0001-CC01 |  | A2 |  |  |  | 2P X 1.0 GSWB FL RET | 35 |  | PS5-08-85CP-1501 |  | CONTROL PANEL |  | GUARD HOUSE | - |  | PS5-08-85BR-0001 |  | BADGE READER |  | FIELD | - |  |  |  |  | A=1 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
273 | PS5-08-85BR-0002-CC01 |  | A2 |  |  |  | 2P X 1.0 GSWB FL RET | 35 |  | PS5-08-85CP-1501 |  | CONTROL PANEL |  | GUARD HOUSE | - |  | PS5-08-85BR-0002 |  | BADGE READER |  | FIELD | - |  |  |  |  | A=1 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
274 | PS5-08-85DC-0022-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0026 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0022 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
275 | PS5-08-85DC-0028-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0026 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0028 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
276 | PS5-08-85BT-0026-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 45 |  | PS5-08-15CP-0004 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0026 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX |  |  |  |  | A=0 B=2 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
277 | PS5-08-85BT-0023-CC01 |  | A4 |  |  |  | 6P X 1.0 GSWB FL RET | 100 |  | PS5-08-85CP-1501 |  | CONTROL PANEL |  | GUARD HOUSE | - |  | PS5-08-85BT-0023 |  | ACS JUNCTION BOX |  | FIELD | M25 25-E1X |  |  |  |  | A=1 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
278 | PS5-08-85BR-0007-CC01 |  | A2 |  |  |  | 2P X 1.0 GSWB FL RET | 100 |  | PS5-08-85CP-1501 |  | CONTROL PANEL |  | GUARD HOUSE | - |  | PS5-08-85BR-0007 |  | BADGE READER |  | FIELD | - |  |  |  |  | A=1 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
279 | PS5-08-85BR-0008-CC01 |  | A2 |  |  |  | 2P X 1.0 GSWB FL RET | 100 |  | PS5-08-85CP-1501 |  | CONTROL PANEL |  | GUARD HOUSE | - |  | PS5-08-85BR-0008 |  | BADGE READER |  | FIELD | - |  |  |  |  | A=1 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
280 | PS5-08-85DC-0023-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 10 |  | PS5-08-85BT-0018 |  | ACS JUNCTION BOX |  | FIELD | M20 20S16A2 |  | PS5-08-85DC-0023 |  | ACS GATE CONTACT |  | FIELD | - |  |  |  |  | Note 12 | 06
281 | PS5-08-85BT-0018-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 90 |  | PS5-08-15CP-0004 |  | CONTROL PANEL |  | FIELD | M20 20S-E1FX |  | PS5-08-85BT-0018 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1FX
282 | PS5-08-05IN-0001-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 30 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARD HOUSE | - |  | PS5-08-05IN-0001 |  | INTERCOM |  | FIELD | M20 20S-E1W |  |  |  |  | A=0 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
283 | PS5-08-05IN-0002-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 45 |  | PS5-08-15CP-0004 |  | CONTROL PANEL |  | FIELD | M20 20S-E1W |  | PS5-08-05IN-0002 |  | INTERCOM |  | FIELD | M20 20S-E1W |  |  |  |  | A=0 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
284 | PS5-08-05IN-0003-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 40 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARD HOUSE | - |  | PS5-08-05IN-0003 |  | INTERCOM |  | FIELD | M20 20S-E1W |  |  |  |  | A=0 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
285 | PS5-08-05IN-0004-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 35 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARD HOUSE | - |  | PS5-08-05IN-0004 |  | INTERCOM |  | FIELD | M20 20S-E1W |  |  |  |  | A=0 B=1 C=0 |  |  | 19-June-2026 | CPP-RFI-68-65-05-0032
286 | PS5-08-05IN-0005-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 80 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARD HOUSE | - |  | PS5-08-05IN-0005 |  | INTERCOM |  | FIELD | M20 20S-E1W |  |  |  |  | A=0 B=1 C=0 | 06 |  | 19-June-2026 | CPP-RFI-68-65-05-0032
287 | PS5-08-52CM-0001-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 60 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARD HOUSE | - |  | PS5-08-52CM-0001 |  | CCTV OPTICAL CAMERA |  | MAIN ENTRANCE | -
288 | PS5-08-52CM-0002-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 60 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARD HOUSE | - |  | PS5-08-52CM-0002 |  | CCTV OPTICAL CAMERA |  | MAIN ENTRANCE | -
289 | PS5-08-52CM-0003-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 35 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARD HOUSE | - |  | PS5-08-52CM-0003 |  | CCTV OPTICAL CAMERA |  | MAIN ENTRANCE | -
290 | PS5-08-52CM-0004-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 60 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARD HOUSE | - |  | PS5-08-52CM-0004 |  | CCTV OPTICAL CAMERA |  | MAIN ENTRANCE | -
291 | PS5-08-52CM-0005-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 60 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARD HOUSE | - |  | PS5-08-52CM-0005 |  | CCTV OPTICAL CAMERA |  | MAIN ENTRANCE | -
292 | PS5-08-52CM-0034-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 45 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARD HOUSE | - |  | PS5-08-52CM-0034 |  | CCTV PANORAMIC CAMERA |  | MAIN ENTRANCE | -
293 | PS5-08-52CM-0931-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 75 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFF. & FACILITIES BLDG | - |  | PS5-08-52CM-0931 |  | CCTV SA PTZ CAMERA |  | TELECOM TOWER | -
294 | PS5-08-52TK-0931-CC01 |  | - |  |  |  | 2P (.75mm2) - Unarmoured, Manufacturer Cable | 10 |  | PS5-08-52CM-0931 |  | CCTV SA PTZ CAMERA |  | FIELD | - |  | PS5-08-52TK-0931 |  | CCTV WATER TANK |  | FIELD | M20 Pre-Fitted
295 | PS5-08-52CM-0131-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 120 |  | PS5-08-15CB-1001 |  | SII SP3 SEC CABINET |  | EITS BLDG / ITR | - |  | PS5-08-52CM-0131 |  | CCTV SA PTZ CAMERA |  | FIELD | - |  |  |  |  | A=0 B=2 C=0 |  |  | 11-May-2026 | CPP-RFI-68-65-05-0027
296 | PS5-08-52TK-0131-CC01 |  | - |  |  |  | 2P (.75mm2) - Unarmoured, Manufacturer Cable | 10 |  | PS5-08-52CM-0131 |  | CCTV SA PTZ CAMERA |  | FIELD | - |  | PS5-08-52TK-0131 |  | CCTV WATER TANK |  | FIELD | M20 Pre-Fitted
297 | PS5-08-52CM-0132-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 315 |  | PS5-08-15CB-1001 |  | SII SP3 SEC CABINET |  | EITS BLDG / ITR | - |  | PS5-08-52CM-0132 |  | CCTV SA PTZ CAMERA |  | FIELD | - |  |  |  |  | A=1 B=2 C=0
298 | PS5-08-52TK-0132-CC01 |  | - |  |  |  | 2P (.75mm2) - Unarmoured, Manufacturer Cable | 10 |  | PS5-08-52CM-0132 |  | CCTV SA PTZ CAMERA |  | FIELD | - |  | PS5-08-52TK-0132 |  | CCTV WATER TANK |  | FIELD | M20 Pre-Fitted
299 | PS5-08-52CM-0133-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 165 |  | PS5-08-15CB-1001 |  | SII SP3 SEC CABINET |  | EITS BLDG / ITR | - |  | PS5-08-52CM-0133 |  | CCTV SA PTZ CAMERA |  | FIELD | -
300 | PS5-08-52TK-0133-CC01 |  | - |  |  |  | 2P (.75mm2) - Unarmoured, Manufacturer Cable | 10 |  | PS5-08-52CM-0133 |  | CCTV SA PTZ CAMERA |  | FIELD | - |  | PS5-08-52TK-0133 |  | CCTV WATER TANK |  | FIELD | M20 Pre-Fitted
301 | PS5-08-52CM-0134-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 60 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-52CM-0134 |  | CCTV SA PTZ CAMERA |  | FIELD | -
302 | PS5-08-52TK-0134-CC01 |  | - |  |  |  | 2P (.75mm2) - Unarmoured, Manufacturer Cable | 10 |  | PS5-08-52CM-0134 |  | CCTV SA PTZ CAMERA |  | FIELD | - |  | PS5-08-52TK-0134 |  | CCTV WATER TANK |  | FIELD | M20 Pre-Fitted
303 | PS5-08-52CM-0138-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 420 |  | PS5-08-15CB-1001 |  | SII SP3 SEC CABINET |  | EITS BLDG / ITR | - |  | PS5-08-52CM-0138 |  | CCTV SA PTZ CAMERA |  | FIELD | -
304 | PS5-08-52TK-0138-CC01 |  | - |  |  |  | 2P (.75mm2) - Unarmoured, Manufacturer Cable | 10 |  | PS5-08-52CM-0138 |  | CCTV SA PTZ CAMERA |  | FIELD | - |  | PS5-08-52TK-0138 |  | CCTV WATER TANK |  | FIELD | M20 Pre-Fitted
305 | PS5-08-52CM-0139-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 600 |  | PS5-08-15CB-1001 |  | SII SP3 SEC CABINET |  | EITS BLDG / ITR | - |  | PS5-08-52CM-0139 |  | CCTV SA PTZ CAMERA |  | FIELD | -
306 | PS5-08-52TK-0139-CC01 |  | - |  |  |  | 2P (.75mm2) - Unarmoured, Manufacturer Cable | 10 |  | PS5-08-52CM-0139 |  | CCTV SA PTZ CAMERA |  | FIELD | - |  | PS5-08-52TK-0139 |  | CCTV WATER TANK |  | FIELD | M20 Pre-Fitted
307 | PS5-08-52CM-0031-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-15CP-0002 |  | CONTROL PANEL |  | FIELD | M20 20SA2 |  | PS5-08-52CM-0031 |  | CCTV SA PTZ CAMERA |  | FIELD | -
308 | PS5-08-52TK-0031-CC01 |  | - |  |  |  | 2P (.75mm2) - Unarmoured, Manufacturer Cable | 10 |  | PS5-08-52CM-0031 |  | CCTV SA PTZ CAMERA |  | FIELD | - |  | PS5-08-52TK-0031 |  | CCTV WATER TANK |  | FIELD | M20 Pre-Fitted
309 | PS5-08-52CM-0032-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-15CP-0006 |  | CONTROL PANEL |  | FIELD | M20 20SA2 |  | PS5-08-52CM-0032 |  | CCTV SA PTZ CAMERA |  | FIELD | -
310 | PS5-08-52TK-0032-CC01 |  | - |  |  |  | 2P (.75mm2) - Unarmoured, Manufacturer Cable | 10 |  | PS5-08-52CM-0032 |  | CCTV SA PTZ CAMERA |  | FIELD | - |  | PS5-08-52TK-0032 |  | CCTV WATER TANK |  | FIELD | M20 Pre-Fitted
311 | PS5-08-52CM-0033-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-15CP-0008 |  | CONTROL PANEL |  | FIELD | M20 20SA2 |  | PS5-08-52CM-0033 |  | CCTV SA PTZ CAMERA |  | FIELD | -
312 | PS5-08-52TK-0033-CC01 |  | - |  |  |  | 2P (.75mm2) - Unarmoured, Manufacturer Cable | 10 |  | PS5-08-52CM-0033 |  | CCTV SA PTZ CAMERA |  | FIELD | - |  | PS5-08-52TK-0033 |  | CCTV WATER TANK |  | FIELD | M20 Pre-Fitted
313 | PS5-08-15CP-0006-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 240 |  | PS5-08-15CB-1001 |  | SII SP3 SEC CABINET |  | EITS BLDG/ITR | - |  | PS5-08-15CP-0006 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X
314 | PS5-08-15CP-0007-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 470 |  | PS5-08-15CP-0006 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-15CP-0007 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X
315 | PS5-08-15CP-0008-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 125 |  | PS5-08-15CP-0007 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-15CP-0008 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X
316 | PS5-08-15CP-0001-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 275 |  | PS5-08-15CP-0008 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-15CP-0001 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X
317 | PS5-08-15CP-0002-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 150 |  | PS5-08-15CP-0001 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-15CP-0002 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X | [7 empty] | 2026-04-10 00:00:00 | CPP-RFI-68-65-05-0023
318 | PS5-08-15CP-0003-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 270 |  | PS5-08-15CP-0002 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-15CP-0003 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X
319 | PS5-08-15CP-0004-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 125 |  | PS5-08-15CP-0003 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-15CP-0004 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X
320 | PS5-08-15CP-0005-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 275 |  | PS5-08-15CP-0004 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-15CP-0005 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X
321 | PS5-08-15CP-0005-CX02 |  | P2 |  |  |  | 4C SM GSWB FOC | 175 |  | PS5-08-15CP-0005 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-15CB-1001 |  | SII SP3 SEC CABINET |  | EITS BLDG/ITR | -
322 | PS5-08-85BT-0027-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 90 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFF. & FACILITIES BLDG | - |  | PS5-08-85BT-0027 |  | WAP JUNCTION BOX |  | PRIMARY MUSTER AREA | M20 20S-E1W
323 | PS5-08-85BT-0028-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 90 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFF. & FACILITIES BLDG | - |  | PS5-08-85BT-0028 |  | WAP JUNCTION BOX |  | PRIMARY MUSTER AREA | M20 20S-E1W
324 | PS5-08-85AP-0001-CA01 |  | - |  |  |  | CAT6A (4P, 26 AWG FL RET) Manufacturer cable | 5 |  | PS5-08-85BT-0027 |  | WAP JUNCTION BOX |  | PRIMARY MUSTER AREA |  |  | PS5-08-85AP-0001 |  | WIRELESS ACCESS PONT |  | PRIMARY MUSTER AREA | [6 empty] | 06
325 | PS5-08-85AP-0002-CA01 |  | - |  |  |  | CAT6A (4P, 26 AWG FL RET) Manufacturer cable | 5 |  | PS5-08-85BT-0028 |  | WAP JUNCTION BOX |  | PRIMARY MUSTER AREA |  |  | PS5-08-85AP-0002 |  | WIRELESS ACCESS PONT |  | PRIMARY MUSTER AREA | [6 empty] | 06
326 | PS5-08-85BR-0009-CC01 |  | A2 |  |  |  | 2P X 1.0 GSWB FL RET | 100 |  | PS5-08-85CP-1201 |  | CONTROL PANEL |  | OFF. & FACILITIES BLDG | - |  | PS5-08-85BR-0009 |  | POB BADGE READER |  | PRIMARY MUSTER AREA | - | [5 empty] | 06
327 | PS5-08-85BR-0010-CC01 |  | A2 |  |  |  | 2P X 1.0 GSWB FL RET | 100 |  | PS5-08-85CP-1202 |  | CONTROL PANEL |  | OFF. & FACILITIES BLDG | - |  | PS5-08-85BR-0010 |  | POB BADGE READER |  | PRIMARY MUSTER AREA | - | [5 empty] | 06
328 | PS5-08-85AP-0003-CA01 |  | - |  |  |  | CAT6A (4P, 26 AWG FL RET) Manufacturer cable | 5 |  | PS5-08-85CP-0024 |  | CONTROL PANEL |  | SECONDARY MUSTER AREA |  |  | PS5-08-85AP-0003 |  | WIRELESS ACCESS POINT |  | SECONDARY MUSTER AREA | [6 empty] | 06
329 | PS5-08-85AP-0004-CA01 |  | - |  |  |  | CAT6A (4P, 26 AWG FL RET) Manufacturer cable | 5 |  | PS5-08-85CP-0025 |  | CONTROL PANEL |  | SECONDARY MUSTER AREA |  |  | PS5-08-85AP-0004 |  | WIRELESS ACCESS POINT |  | SECONDARY MUSTER AREA | [6 empty] | 06
330 | PS5-08-85BR-0011-CC01 |  | - |  |  |  | 2P (.75mm2) - Unarmoured, Manufacturer Cable | 5 |  | PS5-08-85CP-0024 |  | CONTROL PANEL |  | SECONDARY MUSTER AREA | M20-20S16A2 |  | PS5-08-85BR-0011 |  | POB BADGE READER |  | SECONDARY MUSTER AREA | -
331 | PS5-08-85BR-0012-CC01 |  | - |  |  |  | 2P (.75mm2) - Unarmoured, Manufacturer Cable | 5 |  | PS5-08-85CP-0025 |  | CONTROL PANEL |  | SECONDARY MUSTER AREA | M20-20S16A2 |  | PS5-08-85BR-0012 |  | POB BADGE READER |  | SECONDARY MUSTER AREA | -
332 | PS5-08-85CP-0024-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 380 |  | PS5-08-15CB-1001 |  | SII SP3 SEC CABINET |  | EITS BLDG / ITR | - |  | PS5-08-85CP-0024 |  | CONTROL PANEL |  | SECONDARY MUSTER AREA | M20 20S-E1X
333 | PS5-08-85CP-0025-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 380 |  | PS5-08-15CB-1001 |  | SII SP3 SEC CABINET |  | EITS BLDG / ITR | - |  | PS5-08-85CP-0025 |  | CONTROL PANEL |  | SECONDARY MUSTER AREA | M20 20S-E1X
334 | PS5-08-85CP-0024-CX02 |  | P2 |  |  |  | 4C SM GSWB FOC | 380 |  | PS5-08-15CB-1001 |  | SII SP3 SEC CABINET |  | EITS BLDG / ITR | - |  | PS5-08-85CP-0024 |  | CONTROL PANEL |  | SECONDARY MUSTER AREA | M20 20S-E1X
335 | PS5-08-85CP-0025-CX02 |  | P2 |  |  |  | 4C SM GSWB FOC | 380 |  | PS5-08-15CB-1001 |  | SII SP3 SEC CABINET |  | EITS BLDG / ITR | - |  | PS5-08-85CP-0025 |  | CONTROL PANEL |  | SECONDARY MUSTER AREA | M20 20S-E1X
336 | PS5-08-12BT-0001-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 320 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-12BT-0001 |  | WAP JUNCTION BOX |  | FIELD | M20 20S-E1X
337 | PS5-08-12BT-0002-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 50 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-12BT-0002 |  | WAP JUNCTION BOX |  | FIELD | M20 20S-E1W
338 | PS5-08-12BT-0003-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 60 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFF. & FACILITIES BLDG | - |  | PS5-08-12BT-0003 |  | WAP JUNCTION BOX |  | FIELD | M20 20S-E1W
339 | PS5-08-12BT-0101-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 75 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GENERATOR ELECTRIC BLDG | - |  | PS5-08-12BT-0101 |  | WAP JUNCTION BOX |  | FIELD | M20 20S-E1W
340 | PS5-08-12BT-0103-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 60 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-12BT-0103 |  | WAP JUNCTION BOX |  | FIELD | M20 20S-E1W
341 | PS5-08-12BT-0104-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 375 |  | PS5-08-11CB-1001 |  | SIE CABINET |  | EITS BLDG / ITR | - |  | PS5-08-12BT-0104 |  | WAP JUNCTION BOX |  | FIELD | M20 20S-E1X | [7 empty] | 11-May-2026 | CPP-RFI-68-65-05-0028
342 | PS5-08-12BT-0105-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 275 |  | PS5-08-11CB-1001 |  | SIE CABINET |  | EITS BLDG / ITR | - |  | PS5-08-12BT-0105 |  | WAP JUNCTION BOX |  | FIELD | M20 20S-E1X
343 | PS5-08-12BT-0106-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 90 |  | PS5-08-11CB-1001 |  | SIE CABINET |  | EITS BLDG / ITR | - |  | PS5-08-12BT-0106 |  | WAP JUNCTION BOX |  | FIELD | M20 20S-E1X
344 | PS5-08-12BT-0107-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 370 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GENERATOR ELECTRIC BLDG | - |  | PS5-08-12BT-0107 |  | WAP JUNCTION BOX |  | FIELD | M20 20S-E1X
345 | PS5-08-12AP-0001-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-12BT-0001 |  | WAP JUNCTION BOX |  | FIELD | M20 20SA2 |  | PS5-08-12AP-0001 |  | WIRELESS ACCESS POINT |  | FIELD | M20 Pre-Fitted
346 | PS5-08-12AP-0002-CA01 |  | - |  |  |  | CAT6A (4P, 26 AWG FL RET) Manufacturer cable | 5 |  | PS5-08-12BT-0002 |  | WAP JUNCTION BOX |  | FIELD | M20-20S16A2 |  | PS5-08-12AP-0002 |  | WIRELESS ACCESS POINT |  | FIELD | M20 Pre-Fitted
347 | PS5-08-12AP-0003-CA01 |  | - |  |  |  | CAT6A (4P, 26 AWG FL RET) Manufacturer cable | 5 |  | PS5-08-12BT-0003 |  | WAP JUNCTION BOX |  | FIELD | M20-20S16A2 |  | PS5-08-12AP-0003 |  | WIRELESS ACCESS POINT |  | FIELD | M20 Pre-Fitted
348 | PS5-08-12AP-0101-CA01 |  | - |  |  |  | CAT6A (4P, 26 AWG FL RET) Manufacturer cable | 5 |  | PS5-08-12BT-0101 |  | WAP JUNCTION BOX |  | FIELD | M20-20S16A2 |  | PS5-08-12AP-0101 |  | WIRELESS ACCESS POINT |  | FIELD | M20 Pre-Fitted
349 | PS5-08-12AP-0103-CA01 |  | - |  |  |  | CAT6A (4P, 26 AWG FL RET) Manufacturer cable | 5 |  | PS5-08-12BT-0103 |  | WAP JUNCTION BOX |  | FIELD | M20-20S16A2 |  | PS5-08-12AP-0103 |  | WIRELESS ACCESS POINT |  | FIELD | M20 Pre-Fitted
350 | PS5-08-12AP-0104-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-12BT-0104 |  | WAP JUNCTION BOX |  | FIELD | M20 20SA2 |  | PS5-08-12AP-0104 |  | WIRELESS ACCESS POINT |  | FIELD | M20 Pre-Fitted
351 | PS5-08-12AP-0105-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-12BT-0105 |  | WAP JUNCTION BOX |  | FIELD | M20 20SA2 |  | PS5-08-12AP-0105 |  | WIRELESS ACCESS POINT |  | FIELD | M20 Pre-Fitted
352 | PS5-08-12AP-0106-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-12BT-0106 |  | WAP JUNCTION BOX |  | FIELD | M20 20SA2 |  | PS5-08-12AP-0106 |  | WIRELESS ACCESS POINT |  | FIELD | M20 Pre-Fitted
353 | PS5-08-12AP-0107-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-12BT-0107 |  | WAP JUNCTION BOX |  | FIELD | M20 20SA2 |  | PS5-08-12AP-0107 |  | WIRELESS ACCESS POINT |  | FIELD | M20 Pre-Fitted
354 | PS5-08-12BT-0108-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 285 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GENERATOR ELECTRIC BLDG | - |  | PS5-08-12BT-0108 |  | WAP JUNCTION BOX |  | FIELD | M20 20S-E1X
355 | PS5-08-12AP-0108-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-12BT-0108 |  | WAP JUNCTION BOX |  | FIELD | M20 20SA2 |  | PS5-08-12AP-0108 |  | WIRELESS ACCESS POINT |  | FIELD | M20 Pre-Fitted
356 | PS5-08-12BT-0109-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 175 |  | PS5-08-11CB-1001 |  | SIE CABINET |  | EITS BLDG / ITR | - |  | PS5-08-12BT-0109 |  | WAP JUNCTION BOX |  | FIELD | M20 20S-E1X
357 | PS5-08-12AP-0109-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-12BT-0109 |  | WAP JUNCTION BOX |  | FIELD | M20 20SA2 |  | PS5-08-12AP-0109 |  | WIRELESS ACCESS POINT |  | FIELD | M20 Pre-Fitted
358 | PS5-08-03TP-0001-CJ01 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 225 |  | PS5-08-11CB-1001 |  | SIE CABINET |  | EITS BLDG / ITR | - |  | PS5-08-03TP-0001 |  | OUTDOOR TELEPHONE |  | FIELD | M20 20S16-E1X
359 | PS5-08-03TP-0001-CJ02 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 5 |  | PS5-08-03TP-0001 |  | OUTDOOR TELEPHONE |  | FIELD | M20 20S16-E1X |  | PS5-08-03FB-0001 |  | FLASHING BEACON/SOUNDER |  | FIELD | M20 20S16-E1X
360 | PS5-08-03TP-0002-CJ01 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 265 |  | PS5-08-11CB-1001 |  | SIE CABINET |  | EITS BLDG / ITR | - |  | PS5-08-03TP-0002 |  | OUTDOOR TELEPHONE |  | FIELD | M20 20S16-E1X
361 | PS5-08-03TP-0002-CJ02 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 5 |  | PS5-08-03TP-0002 |  | OUTDOOR TELEPHONE |  | FIELD | M20 20S16-E1X |  | PS5-08-03FB-0002 |  | FLASHING BEACON/SOUNDER |  | FIELD | M20 20S16-E1X
362 | PS5-08-03TP-0003-CJ01 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 360 |  | PS5-08-11CB-1001 |  | SIE CABINET |  | EITS BLDG / ITR | - |  | PS5-08-03TP-0003 |  | OUTDOOR TELEPHONE |  | PRIMARY MUSTER AREA | M20 20S16-E1X
363 | PS5-08-03TP-0003-CJ02 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 5 |  | PS5-08-03TP-0003 |  | OUTDOOR TELEPHONE |  | FIELD | M20 20S16-E1X |  | PS5-08-03FB-0003 |  | FLASHING BEACON/SOUNDER |  | FIELD | M20 20S16-E1X
364 | PS5-08-03TP-0004-CJ01 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 215 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GENERATOR ELECTRIC BUILDING | - |  | PS5-08-03TP-0004 |  | OUTDOOR TELEPHONE |  | SECONDARY MUSTER AREA | M20 20S16-E1X
365 | PS5-08-03TP-0004-CJ02 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 5 |  | PS5-08-03TP-0004 |  | OUTDOOR TELEPHONE |  | FIELD | M20 20S16-E1X |  | PS5-08-03FB-0004 |  | FLASHING BEACON/SOUNDER |  | FIELD | M20 20S16-E1X
366 | PS5-08-03TP-0101-CJ01 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 125 |  | PS5-08-11CB-1001 |  | SIE CABINET |  | EITS BLDG / ITR | - |  | PS5-08-03TP-0101 |  | OUTDOOR TELEPHONE |  | FIELD | M20 20S16-E1X
367 | PS5-08-03TP-0101-CJ02 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 5 |  | PS5-08-03TP-0101 |  | OUTDOOR TELEPHONE |  | FIELD | M20 20S16-E1X |  | PS5-08-03FB-0101 |  | FLASHING BEACON/SOUNDER |  | FIELD | M20 20S16-E1X
368 | PS5-08-03TP-0102-CJ01 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 100 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GENERATOR ELECTRIC BUILDING | - |  | PS5-08-03TP-0102 |  | OUTDOOR TELEPHONE |  | FIELD | M20 20S16-E1X
369 | PS5-08-03TP-0102-CJ02 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 5 |  | PS5-08-03TP-0102 |  | OUTDOOR TELEPHONE |  | FIELD | M20 20S16-E1X |  | PS5-08-03FB-0102 |  | FLASHING BEACON/SOUNDER |  | FIELD | M20 20S16-E1X
370 | PS5-08-03TP-0103-CJ01 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 380 |  | PS5-08-11CB-1001 |  | SIE CABINET |  | EITS BLDG / ITR | - |  | PS5-08-03TP-0103 |  | OUTDOOR TELEPHONE |  | FIELD | M20 20S16-E1X | [7 empty] | 11-May-2026 | CPP-RFI-68-65-05-0029
371 | PS5-08-03TP-0103-CJ02 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 5 |  | PS5-08-03TP-0103 |  | OUTDOOR TELEPHONE |  | FIELD | M20 20S16-E1X |  | PS5-08-03FB-0103 |  | FLASHING BEACON/SOUNDER |  | FIELD | M20 20S16-E1X
372 | PS5-08-61SN-0003-CZ01 |  | - |  |  |  | SENSOR CABLE | 5 |  | PS5-08-61SN-0003 |  | TEMP/HUMIDITY SENSOR |  | FIELD | M20 Pre-Fitted |  | PS5-08-61BT-0001 |  | METEOCEAN JB |  | FIELD | M20 Pre-Fitted
373 | PS5-08-61SN-0005-CZ01 |  | - |  |  |  | SENSOR CABLE | 5 |  | PS5-08-61SN-0005 |  | CLOUD SENSOR |  | FIELD | M20 Pre-Fitted |  | PS5-08-61BT-0002 |  | CLOUD SENSOR JB |  | FIELD | M20 Pre-Fitted
374 | PS5-08-61SN-0005-CZ02 |  | - |  |  |  | SENSOR CABLE | 5 |  | PS5-08-61SN-0005 |  | CLOUD SENSOR |  | FIELD | M20 Pre-Fitted |  | PS5-08-61BT-0002 |  | CLOUD SENSOR JB |  | FIELD | M20 Pre-Fitted
375 | PS5-08-61SN-0004-CZ01 |  | - |  |  |  | SENSOR CABLE | 5 |  | PS5-08-61SN-0004 |  | PRECIPITATION SENSOR |  | FIELD | M20 Pre-Fitted |  | PS5-08-61BT-0001 |  | METEOCEAN JB |  | FIELD | M20 Pre-Fitted
376 | PS5-08-61SN-0901-CZ01 |  | - |  |  |  | SENSOR CABLE | 10 |  | PS5-08-61SN-0901 |  | WIND SENSOR |  | TELECOM TOWER | M20 Pre-Fitted |  | PS5-08-61BT-0901 |  | WIND SENSOR JB |  | TELECOM TOWER | M20 Pre-Fitted
377 | PS5-08-61BT-0901-CC01 |  | A3 |  |  |  | 4P X 1.0 GSWB FL RET | 20 |  | PS5-08-61BT-0001 |  | METEOCEAN JUNCTION BOX |  | FIELD | M25 25S-E1X |  | PS5-08-61BT-0901 |  | METEOCEAN JUNCTION BOX |  | TELECOM TOWER | M25 25S-E1X
378 | PS5-08-61BT-0001-CC01 |  | A3 |  |  |  | 4P X 1.0 GSWB FL RET | 70 |  | PS5-08-14CB-1201 |  | SII SP1 CABINET |  | OFF. & FACILITIES BLDG | - |  | PS5-08-61BT-0001 |  | METEOCEAN JUNCTION BOX |  | FIELD | M25 25S-E1X
379 | PS5-08-61BT-0001-CC02 |  | A3 |  |  |  | 4P X 1.0 GSWB FL RET | 70 |  | PS5-08-14CB-1201 |  | SII SP1 CABINET |  | OFF. & FACILITIES BLDG | - |  | PS5-08-61BT-0001 |  | METEOCEAN JUNCTION BOX |  | FIELD | M25 25S-E1X
380 | PS5-08-61BT-0001-CN01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 70 |  | PS5-08-14CB-1201 |  | SII SP1 CABINET |  | OFF. & FACILITIES BLDG | - |  | PS5-08-61BT-0001 |  | METEOCEAN JUNCTION BOX |  | FIELD | M20 20S-E1FX
381 | PS5-08-61BT-0002-CC01 |  | A3 |  |  |  | 4P X 1.0 GSWB FL RET | 75 |  | PS5-08-14CB-1201 |  | SII SP1 CABINET |  | OFF. & FACILITIES BLDG | - |  | PS5-08-61BT-0002 |  | METEOCEAN JUNCTION BOX |  | FIELD | M25 25S-E1X
382 | PS5-08-83SP-0001-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 3400 |  | PS5-08-15CB-1001 |  | SII SP3 SEC CABINET |  | EITS BLDG / ITR | - |  | PS5-08-83SP-0001 |  | IDS MANHOLE |  | OUTDOOR | - | [5 empty] | 06
383 | PS5-08-83SP-0001-CX02 |  | P2 |  |  |  | 4C SM GSWB FOC | 1635 |  | PS5-08-15CB-1001 |  | SII SP3 SEC CABINET |  | EITS BLDG / ITR | - |  | PS5-08-83SP-0001 |  | IDS MANHOLE |  | OUTDOOR | - | [5 empty] | 06
384 | PS5-08-36SP-0101-CX02 |  | N |  |  |  | 96C SM GSWB FOC | 400 |  | PS5-08-35CB-1001 |  | OTN CABINET |  | EITS BLDG / ITR | - |  | PS5-08-36SP-0101 |  | PIPELINE SPLICE BOX |  | STATION FOC CHAMBER | - | [5 empty] | 06
385 | PS5-08-36SP-0102-CX02 |  | N |  |  |  | 96C SM GSWB FOC | 400 |  | PS5-08-35CB-1001 |  | OTN CABINET |  | EITS BLDG / ITR | - |  | PS5-08-36SP-0102 |  | PIPELINE SPLICE BOX |  | STATION FOC CHAMBER | - | [5 empty] | 06
386 | PS5-08-36SP-0101-CX06 |  | P2 |  |  |  | 24C SM GSWB FL RET FOC | 770 |  | PS5-08-36MH-0001 |  | 3RD PARTY FOC CHAMBER |  | FIELD | - |  | PS5-08-36SP-0101 |  | PIPELINE SPLICE BOX |  | STATION FOC CHAMBER | - | [5 empty] | 06
387 | PS5-08-36SP-0102-CX06 |  | P2 |  |  |  | 24C SM GSWB FL RET FOC | 770 |  | PS5-08-36MH-0001 |  | 3RD PARTY FOC CHAMBER |  | FIELD | - |  | PS5-08-36SP-0102 |  | PIPELINE SPLICE BOX |  | STATION FOC CHAMBER | - | [5 empty] | 06
388 | PS5-08-11CB-1201-CX01 |  | P2 |  |  |  | 24C SM GSWB FR RES FOC | 330 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-11CB-1001 |  | SIE CABINET |  | EITS BLDG / ITR | -
389 | PS5-08-11CB-1501-CX01 |  | P2 |  |  |  | 24C SM GSWB FR RES FOC | 335 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-11CB-1001 |  | SIE CABINET |  | EITS BLDG / ITR | -
390 | PS5-08-11CB-1601-CX01 |  | P2 |  |  |  | 24C SM GSWB FR RES FOC | 335 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-11CB-1001 |  | SIE CABINET |  | EITS BLDG / ITR | -
391 | PS5-08-11CB-1901-CX01 |  | P2 |  |  |  | 24C SM GSWB FR RES FOC | 190 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-11CB-1001 |  | SIE CABINET |  | EITS BLDG / ITR | -
392 | PS5-82-MBA-0002-CC01 |  | A3 |  |  |  | 4P X 1.0 GSWB FL RET | 15 |  | PS5-08-85BT-0023 |  | ACS JUNCTION BOX |  | FIELD | M25 25S-E1X |  | PS5-82-MBA-0002 |  | VEHICLE BARRIER |  | FIELD | M25 25S-E1X
393 | PS5-08-85BT-0001-CJ01 |  | A1 |  |  |  | 1P X 1.0 GSWB FL RET | 60 |  | PS5-08-15CP-0004 |  | CONTROL PANEL |  | FIELD | M20 20S-E1X |  | PS5-08-85BT-0001 |  | ACS JUNCTION BOX |  | FIELD | M20 20S-E1X
394 | PS5-08-52CM-0071-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-15CP-0001 |  | CONTROL PANEL |  | FIELD | M20 20SA2 |  | PS5-08-52CM-0071 |  | CCTV THERMAL CAMERA |  | FIELD | -
395 | PS5-08-52CM-0072-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-15CP-0002 |  | CONTROL PANEL |  | FIELD | M20 20SA2 |  | PS5-08-52CM-0072 |  | CCTV THERMAL CAMERA |  | FIELD | -
396 | PS5-08-52CM-0073-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-15CP-0003 |  | CONTROL PANEL |  | FIELD | M20 20SA2 |  | PS5-08-52CM-0073 |  | CCTV THERMAL CAMERA |  | FIELD | -
397 | PS5-08-52CM-0074-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-15CP-0004 |  | CONTROL PANEL |  | FIELD | M20 20SA2 |  | PS5-08-52CM-0074 |  | CCTV THERMAL CAMERA |  | FIELD | -
398 | PS5-08-52CM-0075-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-15CP-0005 |  | CONTROL PANEL |  | FIELD | M20 20SA2 |  | PS5-08-52CM-0075 |  | CCTV THERMAL CAMERA |  | FIELD | -
399 | PS5-08-52CM-0076-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-15CP-0006 |  | CONTROL PANEL |  | FIELD | M20 20SA2 |  | PS5-08-52CM-0076 |  | CCTV THERMAL CAMERA |  | FIELD | -
400 | PS5-08-52CM-0077-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-15CP-0007 |  | CONTROL PANEL |  | FIELD | M20 20SA2 |  | PS5-08-52CM-0077 |  | CCTV THERMAL CAMERA |  | FIELD | -
401 | PS5-08-52CM-0078-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-15CP-0008 |  | CONTROL PANEL |  | FIELD | M20 20SA2 |  | PS5-08-52CM-0078 |  | CCTV THERMAL CAMERA |  | FIELD | -
402 | PS5-08-01LS-0418-CR02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 30 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | EITS BLDG | M20 20-E1FX |  | PS5-08-01LS-0418 |  | PAGA LOUDSPEAKER |  | EITS BLDG | M20 20-E1FX
403 | PS5-08-01LS-0318-CR02 |  | G1 |  |  |  | 1P X 2.5 OS GSWB FR | 30 |  | PS5-08-01MP-0001 |  | MARSHALLING ENCLOSURE |  | EITS BLDG | M20 20-E1FX |  | PS5-08-01LS-0318 |  | PAGA LOUDSPEAKER |  | EITS BLDG | M20 20-E1FX
404 | PS5-08-13CB-1201-CJ01 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 335 |  | PS5-08-13CB-1201 |  | SII SP3 SAF CABINET |  | OFFICE & FACILITY BUILDING | - |  | PS5-04-PMC-0006 |  | INSTRUMENTATION CABINET |  | EITS BUILDING | -
405 | PS5-08-01PA-1201-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE BLDG/TER | - |  | PS5-08-01PA-1201 |  | PAGA ACCESS UNIT |  | OFFICE | -
406 | PS5-08-01PA-1201-CC01 |  | - |  |  |  | 6P X 0.5 SQMM PIGTAIL | 10 |  | PS5-08-01BT-1203 |  | PAGA JUNCTION BOX |  | OFFICE BLDG/TER | M20 20A2 |  | PS5-08-01PA-1201 |  | PAGA ACCESS UNIT |  | OFFICE | M20 20A2
407 | PS5-08-01BT-1203-CN01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE BLDG/TER | - |  | PS5-08-01BT-1203 |  | PAGA JUNCTION BOX |  | OFFICE | M20 20A2
408 | PS5-08-01BT-1203-CN02 |  | G1 |  |  |  | 1P X 2.5 OS FR | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE BLDG/TER | - |  | PS5-08-01BT-1203 |  | PAGA JUNCTION BOX |  | OFFICE | M20 20A2
409 | PS5-08-01BT-1201-CR03 |  | S1 |  |  |  | 1P X 1.0 OS FR | 40 |  | PS5-08-01BT-1203 |  | PAGA JUNCTION BOX |  | OFFICE BLDG/TER | M20 20A2 |  | PS5-08-01BT-1201 |  | PAGA JUNCTION BOX |  | OFFICE | M20 20A2
410 | PS5-08-01BT-1202-CR03 |  | S1 |  |  |  | 1P X 1.0 OS FR | 40 |  | PS5-08-01BT-1203 |  | PAGA JUNCTION BOX |  | OFFICE BLDG/TER | M20 20A2 |  | PS5-08-01BT-1202 |  | PAGA JUNCTION BOX |  | OFFICE | M20 20A2
411 | PS5-08-85BR-1201-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 45 |  | PS5-08-85CP-1202 |  | CONTROL PANEL |  | TELECOM ROOM | - |  | PS5-08-85BR-1201 |  | BADGE READER |  | MAIN ENTRANCE | -
412 | PS5-08-85DC-1201-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1201 |  | ACS JUNCTION BOX |  | MAIN ENTRANCE | M20 Pre-Fitted |  | PS5-08-85DC-1201 |  | ACS DOOR CONTACT |  | MAIN ENTRANCE | - |  |  |  |  | Note 12 | 06
413 | PS5-08-85ML-1201-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1201 |  | ACS JUNCTION BOX |  | MAIN ENTRANCE | M20 Pre-Fitted |  | PS5-08-85ML-1201 |  | MAGNETIC DOORLOCK |  | MAIN ENTRANCE | - | [5 empty] | 06
414 | PS5-08-85PB-1201-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1201 |  | ACS JUNCTION BOX |  | MAIN ENTRANCE | M20 Pre-Fitted |  | PS5-08-85PB-1201 |  | EXIT PUSHBUTTON |  | MAIN ENTRANCE | -
415 | PS5-08-85BG-1201-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 5 |  | PS5-08-85BT-1201 |  | ACS JUNCTION BOX |  | MAIN ENTRANCE | M20 Pre-Fitted |  | PS5-08-85BG-1201 |  | EMERGENCY BREAK GLASS |  | MAIN ENTRANCE | -
416 | PS5-08-85BT-1201-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-85BT-1201 |  | ACS JUNCTION BOX |  | MAIN ENTRANCE | M20 Pre-Fitted
417 | PS5-08-85BT-1201-CC01 |  | A4 |  |  |  | 6P X 1.0 FL RET | 45 |  | PS5-08-85CP-1202 |  | CONTROL PANEL |  | TELECOM ROOM | - |  | PS5-08-85BT-1201 |  | ACS JUNCTION BOX |  | MAIN ENTRANCE | M32 Pre-Fitted
418 | PS5-08-85BR-1202-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 35 |  | PS5-08-85CP-1202 |  | CONTROL PANEL |  | TELECOM ROOM | - |  | PS5-08-85BR-1202 |  | BADGE READER |  | CLINIC ENTRANCE | -
419 | PS5-08-85DC-1202-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1202 |  | ACS JUNCTION BOX |  | CLINIC ENTRANCE | M20 Pre-Fitted |  | PS5-08-85DC-1202 |  | ACS DOOR CONTACT |  | CLINIC ENTRANCE | - |  |  |  |  | Note 12 | 06
420 | PS5-08-85DC-1203-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1202 |  | ACS JUNCTION BOX |  | CLINIC ENTRANCE | M20 Pre-Fitted |  | PS5-08-85DC-1203 |  | ACS DOOR CONTACT |  | CLINIC ENTRANCE | - |  |  |  |  | Note 12 | 06
421 | PS5-08-85ML-1202-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1202 |  | ACS JUNCTION BOX |  | CLINIC ENTRANCE | M20 Pre-Fitted |  | PS5-08-85ML-1202 |  | MAGNETIC DOORLOCK |  | CLINIC ENTRANCE | - | [5 empty] | 06
422 | PS5-08-85PB-1202-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1202 |  | ACS JUNCTION BOX |  | CLINIC ENTRANCE | M20 Pre-Fitted |  | PS5-08-85PB-1202 |  | EXIT PUSHBUTTON |  | CLINIC ENTRANCE | -
423 | PS5-08-85BG-1202-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 5 |  | PS5-08-85BT-1202 |  | ACS JUNCTION BOX |  | CLINIC ENTRANCE | M20 Pre-Fitted |  | PS5-08-85BG-1202 |  | EMERGENCY BREAK GLASS |  | CLINIC ENTRANCE | -
424 | PS5-08-85BT-1202-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 15 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-85BT-1202 |  | ACS JUNCTION BOX |  | MAIN ENTRANCE | M20 Pre-Fitted
425 | PS5-08-85BT-1202-CC01 |  | A4 |  |  |  | 6P X 1.0 FL RET | 35 |  | PS5-08-85CP-1202 |  | CONTROL PANEL |  | TELECOM ROOM | - |  | PS5-08-85BT-1202 |  | ACS JUNCTION BOX |  | CLINIC ENTRANCE | M32 Pre-Fitted
426 | PS5-08-85BR-1203-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 15 |  | PS5-08-85CP-1202 |  | CONTROL PANEL |  | TELECOM ROOM | - |  | PS5-08-85BR-1203 |  | BADGE READER |  | DINING AREA | -
427 | PS5-08-85DC-1204-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1203 |  | ACS JUNCTION BOX |  | DINING AREA | M20 Pre-Fitted |  | PS5-08-85DC-1204 |  | ACS DOOR CONTACT |  | DINING AREA | - |  |  |  |  | Note 12 | 06
428 | PS5-08-85ML-1203-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1203 |  | ACS JUNCTION BOX |  | DINING AREA | M20 Pre-Fitted |  | PS5-08-85ML-1203 |  | MAGNETIC DOORLOCK |  | DINING AREA | - | [5 empty] | 06
429 | PS5-08-85PB-1203-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1203 |  | ACS JUNCTION BOX |  | DINING AREA | M20 Pre-Fitted |  | PS5-08-85PB-1203 |  | EXIT PUSHBUTTON |  | DINING AREA | -
430 | PS5-08-85BG-1203-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 5 |  | PS5-08-85BT-1203 |  | ACS JUNCTION BOX |  | DINING AREA | M20 Pre-Fitted |  | PS5-08-85BG-1203 |  | EMERGENCY BREAK GLASS |  | DINING AREA | -
431 | PS5-08-85BT-1203-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 15 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-85BT-1203 |  | ACS JUNCTION BOX |  | MAIN ENTRANCE | M20 Pre-Fitted
432 | PS5-08-85BT-1203-CC01 |  | A4 |  |  |  | 6P X 1.0 FL RET | 15 |  | PS5-08-85CP-1202 |  | CONTROL PANEL |  | TELECOM ROOM | - |  | PS5-08-85BT-1203 |  | ACS JUNCTION BOX |  | DINING AREA | M32 Pre-Fitted
433 | PS5-08-85DC-1205-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1204 |  | ACS JUNCTION BOX |  | TELECOM ROOM | M20 Pre-Fitted |  | PS5-08-85DC-1205 |  | ACS DOOR CONTACT |  | TELECOM ROOM | - |  |  |  |  | Note 12 | 06
434 | PS5-08-85DC-1206-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1204 |  | ACS JUNCTION BOX |  | TELECOM ROOM | M20 Pre-Fitted |  | PS5-08-85DC-1206 |  | ACS DOOR CONTACT |  | TELECOM ROOM | - |  |  |  |  | Note 12 | 06
435 | PS5-08-85BR-1204-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 10 |  | PS5-08-85CP-1202 |  | CONTROL PANEL |  | TELECOM ROOM | - |  | PS5-08-85BR-1204 |  | BADGE READER |  | TELECOM ROOM | -
436 | PS5-08-85DC-1207-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1205 |  | ACS JUNCTION BOX |  | TELECOM ROOM | M20 Pre-Fitted |  | PS5-08-85DC-1207 |  | ACS DOOR CONTACT |  | TELECOM ROOM | - |  |  |  |  | Note 12 | 06
437 | PS5-08-85ML-1204-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1205 |  | ACS JUNCTION BOX |  | TELECOM ROOM | M20 Pre-Fitted |  | PS5-08-85ML-1204 |  | MAGNETIC DOORLOCK |  | TELECOM ROOM | - | [5 empty] | 06
438 | PS5-08-85PB-1204-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1205 |  | ACS JUNCTION BOX |  | TELECOM ROOM | M20 Pre-Fitted |  | PS5-08-85PB-1204 |  | EXIT PUSHBUTTON |  | TELECOM ROOM | -
439 | PS5-08-85BT-1205-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 10 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-85BT-1205 |  | ACS JUNCTION BOX |  | MAIN ENTRANCE | M20 Pre-Fitted
440 | PS5-08-85BG-1204-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 5 |  | PS5-08-85BT-1205 |  | ACS JUNCTION BOX |  | TELECOM ROOM | M20 Pre-Fitted |  | PS5-08-85BG-1204 |  | EMERGENCY BREAK GLASS |  | TELECOM ROOM | -
441 | PS5-08-85BT-1205-CC01 |  | A4 |  |  |  | 6P X 1.0 FL RET | 10 |  | PS5-08-85CP-1202 |  | CONTROL PANEL |  | TELECOM ROOM | - |  | PS5-08-85BT-1205 |  | ACS JUNCTION BOX |  | TELECOM ROOM | M32 Pre-Fitted
442 | PS5-08-85BT-1204-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 10 |  | PS5-08-85CP-1201 |  | CONTROL PANEL |  | TELECOM ROOM | - |  | PS5-08-85BT-1204 |  | ACS JUNCTION BOX |  | TELECOM ROOM | M20 Pre-Fitted
443 | PS5-08-85CP-1201-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | TELECOM ROOM | - |  | PS5-08-85CP-1201 |  | ACS CONTROL PANEL |  | TELECOM ROOM | -
444 | PS5-08-85CP-1202-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | TELECOM ROOM | - |  | PS5-08-85CP-1202 |  | ACS CONTROL PANEL |  | TELECOM ROOM | -
445 | PS5-08-52CM-1201-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | TELECOM ROOM | - |  | PS5-08-52CM-1201 |  | OUTDOOR CAMERA |  | MAIN ENTRANCE | -
446 | PS5-08-52CM-1202-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | TELECOM ROOM | - |  | PS5-08-52CM-1202 |  | OUTDOOR CAMERA |  | CLINIC ENTRANCE | -
447 | PS5-08-85BR-1205-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 40 |  | PS5-08-85CP-1201 |  | CONTROL PANEL |  | TELECOM ROOM | - |  | PS5-08-85BR-1205 |  | POB CARD READER |  | SAFE HAVEN | -
448 | PS5-08-85BR-1206-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 40 |  | PS5-08-85CP-1202 |  | CONTROL PANEL |  | TELECOM ROOM | - |  | PS5-08-85BR-1206 |  | POB CARD READER |  | SAFE HAVEN | -
449 | PS5-08-85AP-1201-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET |  |  | PS5-08-71SK-1237 |  | RJ45 DATA SOCKET |  | OFFICE |  |  | PS5-08-85AP-1201 |  | WIRELESS ACCESS PONT |  | SAFE HAVEN
450 | PS5-08-85AP-1202-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET |  |  | PS5-08-71SK-1238 |  | RJ45 DATA SOCKET |  | OFFICE |  |  | PS5-08-85AP-1202 |  | WIRELESS ACCESS PONT |  | SAFE HAVEN
451 | PS5-08-71SK-1201-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1201 |  | RJ45 DATA SOCKET |  | OFFICE | -
452 | PS5-08-71SK-1202-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 20 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1202 |  | RJ45 DATA SOCKET |  | OFFICE | -
453 | PS5-08-71SK-1203-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1203 |  | RJ45 DATA SOCKET |  | OFFICE | -
454 | PS5-08-71SK-1204-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 25 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1204 |  | RJ45 DATA SOCKET |  | OFFICE | -
455 | PS5-08-71SK-1205-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1205 |  | RJ45 DATA SOCKET |  | OFFICE | -
456 | PS5-08-71SK-1206A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 25 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1206A |  | RJ45 DATA SOCKET |  | OFFICE | -
457 | PS5-08-71SK-1207-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1207 |  | RJ45 DATA SOCKET |  | OFFICE | -
458 | PS5-08-71SK-1208-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 15 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1208 |  | RJ45 DATA SOCKET |  | OFFICE | -
459 | PS5-08-71SK-1209-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 25 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1209 |  | RJ45 DATA SOCKET |  | OFFICE | -
460 | PS5-08-71SK-1210-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 25 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1210 |  | RJ45 DATA SOCKET |  | OFFICE | -
461 | PS5-08-71SK-1211-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1211 |  | RJ45 DATA SOCKET |  | OFFICE | -
462 | PS5-08-71SK-1212A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1212A |  | RJ45 DATA SOCKET |  | OFFICE | -
463 | PS5-08-71SK-1213-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 15 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1213 |  | RJ45 DATA SOCKET |  | OFFICE | -
464 | PS5-08-71SK-1213B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET |  |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE |  |  | PS5-08-71SK-1213B |  | RJ45 DATA SOCKET |  | OFFICE
465 | PS5-08-71SK-1214A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1214A |  | RJ45 DATA SOCKET |  | OFFICE | -
466 | PS5-08-71SK-1214B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1214B |  | RJ45 DATA SOCKET |  | OFFICE | -
467 | PS5-08-71SK-1215A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1215A |  | RJ45 DATA SOCKET |  | OFFICE | -
468 | PS5-08-71SK-1215B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1215B |  | RJ45 DATA SOCKET |  | OFFICE | -
469 | PS5-08-71SK-1216A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1216A |  | RJ45 DATA SOCKET |  | OFFICE | -
470 | PS5-08-71SK-1216B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1216B |  | RJ45 DATA SOCKET |  | OFFICE | -
471 | PS5-08-71SK-1217A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1217A |  | RJ45 DATA SOCKET |  | OFFICE | -
472 | PS5-08-71SK-1217B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1217B |  | RJ45 DATA SOCKET |  | OFFICE | -
473 | PS5-08-71SK-1218A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1218A |  | RJ45 DATA SOCKET |  | OFFICE | -
474 | PS5-08-71SK-1218B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1218B |  | RJ45 DATA SOCKET |  | OFFICE | -
475 | PS5-08-71SK-1219A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1219A |  | RJ45 DATA SOCKET |  | OFFICE | -
476 | PS5-08-71SK-1219B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1219B |  | RJ45 DATA SOCKET |  | OFFICE | -
477 | PS5-08-71SK-1219C-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET |  |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE |  |  | PS5-08-71SK-1219C |  | RJ45 DATA SOCKET |  | OFFICE
478 | PS5-08-71SK-1219D-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET |  |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE |  |  | PS5-08-71SK-1219D |  | RJ45 DATA SOCKET |  | OFFICE
479 | PS5-08-71SK-1220A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1220A |  | RJ45 DATA SOCKET |  | OFFICE | -
480 | PS5-08-71SK-1220B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1220B |  | RJ45 DATA SOCKET |  | OFFICE | -
481 | PS5-08-71SK-1221A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1221A |  | RJ45 DATA SOCKET |  | OFFICE | -
482 | PS5-08-71SK-1221B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1221B |  | RJ45 DATA SOCKET |  | OFFICE | -
483 | PS5-08-71SK-1222A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1222A |  | RJ45 DATA SOCKET |  | OFFICE | -
484 | PS5-08-71SK-1222B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1222B |  | RJ45 DATA SOCKET |  | OFFICE | -
485 | PS5-08-71SK-1223A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1223A |  | RJ45 DATA SOCKET |  | OFFICE | -
486 | PS5-08-71SK-1223B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1223B |  | RJ45 DATA SOCKET |  | OFFICE | -
487 | PS5-08-71SK-1224A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1224A |  | RJ45 DATA SOCKET |  | OFFICE | -
488 | PS5-08-71SK-1224B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1224B |  | RJ45 DATA SOCKET |  | OFFICE | -
489 | PS5-08-71SK-1225A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1225A |  | RJ45 DATA SOCKET |  | OFFICE | -
490 | PS5-08-71SK-1226A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1226A |  | RJ45 DATA SOCKET |  | OFFICE | -
491 | PS5-08-71SK-1227A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1227A |  | RJ45 DATA SOCKET |  | OFFICE | -
492 | PS5-08-71SK-1227B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1227B |  | RJ45 DATA SOCKET |  | OFFICE | -
493 | PS5-08-71SK-1228A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1228A |  | RJ45 DATA SOCKET |  | OFFICE | -
494 | PS5-08-71SK-1229-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1229 |  | RJ45 DATA SOCKET |  | OFFICE | -
495 | PS5-08-71SK-1229B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET |  |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE |  |  | PS5-08-71SK-1229B |  | RJ45 DATA SOCKET |  | OFFICE
496 | PS5-08-71SK-1230A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 45 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1230A |  | RJ45 DATA SOCKET |  | OFFICE | -
497 | PS5-08-71SK-1230B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 45 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1230B |  | RJ45 DATA SOCKET |  | OFFICE | -
498 | PS5-08-71SK-1231-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 25 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1231 |  | RJ45 DATA SOCKET |  | OFFICE | -
499 | PS5-08-71SK-1231B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET |  |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE |  |  | PS5-08-71SK-1231B |  | RJ45 DATA SOCKET |  | OFFICE
500 | PS5-08-71SK-1232A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 15 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1232A |  | RJ45 DATA SOCKET |  | OFFICE | -
501 | PS5-08-71SK-1233A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1233A |  | RJ45 DATA SOCKET |  | OFFICE | -
502 | PS5-08-71SK-1234-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1234 |  | RJ45 DATA SOCKET |  | OFFICE | -
503 | PS5-08-71SK-1235-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 25 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1235 |  | RJ45 DATA SOCKET |  | OFFICE | -
504 | PS5-08-71SK-1236A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1236A |  | RJ45 DATA SOCKET |  | OFFICE | -
505 | PS5-08-71SK-1237-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1237 |  | RJ45 DATA SOCKET |  | OFFICE | -
506 | PS5-08-71SK-1238-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1238 |  | RJ45 DATA SOCKET |  | OFFICE | -
507 | PS5-08-71SK-1239-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 15 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1239 |  | RJ45 DATA SOCKET |  | OFFICE | -
508 | PS5-08-71SK-1240-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1240 |  | RJ45 DATA SOCKET |  | OFFICE | -
509 | PS5-08-71SK-1241A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1241A |  | RJ45 DATA SOCKET |  | OFFICE | -
510 | PS5-08-71SK-1241B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1241B |  | RJ45 DATA SOCKET |  | OFFICE | -
511 | PS5-08-71SK-1242A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1242A |  | RJ45 DATA SOCKET |  | OFFICE | -
512 | PS5-08-71SK-1243A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 50 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1243A |  | RJ45 DATA SOCKET |  | OFFICE | -
513 | PS5-08-71SK-1244A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 45 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1244A |  | RJ45 DATA SOCKET |  | OFFICE | -
514 | PS5-08-71SK-1245A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1245A |  | RJ45 DATA SOCKET |  | OFFICE | -
515 | PS5-08-71SK-1246A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 50 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1246A |  | RJ45 DATA SOCKET |  | OFFICE | -
516 | PS5-08-71SK-1246B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 50 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1246B |  | RJ45 DATA SOCKET |  | OFFICE | -
517 | PS5-08-71SK-1247-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1247 |  | RJ45 DATA SOCKET |  | OFFICE | -
518 | PS5-08-71SK-1248-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1248 |  | RJ45 DATA SOCKET |  | OFFICE | -
519 | PS5-08-03AF-1201-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET |  |  | PS5-08-71SK-1228A |  | RJ45 DATA SOCKET |  | OFFICE |  |  | PS5-08-03AF-1201 |  | AUDIO CONFERENCE PHONE |  | OFFICE
520 | PS5-08-55VF-1201-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET |  |  | PS5-08-71SK-1230A |  | RJ45 DATA SOCKET |  | OFFICE |  |  | PS5-08-55VF-1201 |  | VIDEO CONFERENCE UNIT |  | OFFICE
521 | PS5-08-23LA-1201-CV01 |  | T7 |  |  |  | RG213 CV FL RET | 10 |  | PS5-08-23BS-1201 |  | RADIO BASESTATION |  | OFFICE | BNC Male (Ref 28) |  | PS5-08-23LA-1201 |  | LIGHTNING ARRESTOR |  | OFFICE | N Type Male (Ref 28)
522 | PS5-08-23AN-0001-CV01 |  | T7 |  |  |  | RG213 CV FL RET | 5 |  | PS5-08-23LA-1201 |  | LIGHTNING ARRESTOR |  | OFFICE | N Type Male (Ref 28) |  | PS5-08-23AN-0001 |  | VHF ANTENNA |  | OFFICE | N Type Male (Ref 28)
523 | PS5-08-23LA-1202-CV01 |  | T1 |  |  |  | 1/2" CV FL RET | 35 |  | PS5-08-13CB-1201 |  | SII SP3 SAF CABINET |  | OFFICE | N Type Male (Ref 28) |  | PS5-08-23LA-1202 |  | LIGHTNING ARRESTOR |  | OFFICE | N Type Male (Ref 28)
524 | PS5-08-23AN-0901-CV01 |  | T2 |  |  |  | 7/8" CV FL RET | 80 |  | PS5-08-23LA-1202 |  | LIGHTNING ARRESTOR |  | OFFICE | N Type Male (Ref 28) |  | PS5-08-23AN-0901 |  | VHF ANTENNA |  | TELECOM TOWER | N Type Male (Ref 28)
525 | PS5-08-23AN-1201-CV01 |  | T1 |  |  |  | 1/2" CV FL RET | 15 |  | PS5-08-13CB-1201 |  | SII SP3 SAF CABINET |  | OFFICE | N Type Male (Ref 28) |  | PS5-08-23AN-1201 |  | INDOOR ANTENNA |  | OFFICE | N Type Male (Ref 28)
526 | PS5-08-34LA-1201-CV01 |  | T7 |  |  |  | RG213 CV FL RET | 10 |  | PS5-08-34DS-1211 |  | SAT. PHONE BIAS BOX |  | OFFICE | N Type Male (Ref 28) |  | PS5-08-34LA-1201 |  | LIGHTNING ARRESTOR |  | OFFICE | TNC Female (Ref 28)
527 | PS5-08-34AN-0001-CV01 |  | T7 |  |  |  | RG213 CV FL RET | 5 |  | PS5-08-34LA-1201 |  | LIGHTNING ARRESTOR |  | OFFICE | TNC Male (Ref 28) |  | PS5-08-34AN-0001 |  | SAT. PHONE ANTENNA |  | OFFICE | TNC Male (Ref 28)
528 | PS5-08-51SK-1201-CV01 |  | T5 |  |  |  | RG6 CV FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | F TYPE MALE |  | PS5-08-51SK-1201 |  | ENTERTAINMENT TV SOCKET |  | OFFICE | F TYPE MALE
529 | PS5-08-51SK-1202-CV01 |  | T5 |  |  |  | RG6 CV FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | F TYPE MALE |  | PS5-08-51SK-1202 |  | ENTERTAINMENT TV SOCKET |  | OFFICE | F TYPE MALE
530 | PS5-08-51SK-1203-CV01 |  | T5 |  |  |  | RG6 CV FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | F TYPE MALE |  | PS5-08-51SK-1203 |  | ENTERTAINMENT TV SOCKET |  | OFFICE | F TYPE MALE
531 | PS5-08-51SK-1204-CV01 |  | T5 |  |  |  | RG6 CV FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | F TYPE MALE |  | PS5-08-51SK-1204 |  | ENTERTAINMENT TV SOCKET |  | OFFICE | F TYPE MALE
532 | PS5-08-51SK-1205-CV01 |  | T5 |  |  |  | RG6 CV FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | F TYPE MALE |  | PS5-08-51SK-1205 |  | ENTERTAINMENT TV SOCKET |  | OFFICE | F TYPE MALE
533 | PS5-08-51SK-1206-CV01 |  | T5 |  |  |  | RG6 CV FL RET | 30 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | F TYPE MALE |  | PS5-08-51SK-1206 |  | ENTERTAINMENT TV SOCKET |  | OFFICE | F TYPE MALE
534 | PS5-08-51SK-1207-CV01 |  | T5 |  |  |  | RG6 CV FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | F TYPE MALE |  | PS5-08-51SK-1207 |  | ENTERTAINMENT TV SOCKET |  | OFFICE | F TYPE MALE
535 | PS5-08-51SK-1208-CV01 |  | T5 |  |  |  | RG6 CV FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | F TYPE MALE |  | PS5-08-51SK-1208 |  | ENTERTAINMENT TV SOCKET |  | OFFICE | F TYPE MALE
536 | PS5-08-51SK-1209-CV01 |  | T5 |  |  |  | RG6 CV FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | F TYPE MALE |  | PS5-08-51SK-1209 |  | ENTERTAINMENT TV SOCKET |  | OFFICE | F TYPE MALE
537 | PS5-08-51SK-1210-CV01 |  | T5 |  |  |  | RG6 CV FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | F TYPE MALE |  | PS5-08-51SK-1210 |  | ENTERTAINMENT TV SOCKET |  | OFFICE | F TYPE MALE
538 | PS5-08-51LA-1201-CV01 |  | T5 |  |  |  | RG6 CV FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | F TYPE MALE |  | PS5-08-51LA-1201 |  | LIGHTNING ARRESTOR |  | OFFICE | F TYPE MALE
539 | PS5-08-51AN-0001-CV01 |  | T5 |  |  |  | RG6 CV FL RET | 10 |  | PS5-08-51LA-1201 |  | LIGHTNING ARRESTOR |  | OFFICE | F TYPE MALE |  | PS5-08-51AN-0001 |  | SATELLITE ANTENNA |  | OFFICE | F TYPE MALE
540 | PS5-08-51LA-1202-CV01 |  | T5 |  |  |  | RG6 CV FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | F TYPE MALE |  | PS5-08-51LA-1202 |  | LIGHTNING ARRESTOR |  | OFFICE | F TYPE MALE
541 | PS5-08-51AN-0001-CV02 |  | T5 |  |  |  | RG6 CV FL RET | 10 |  | PS5-08-51LA-1202 |  | LIGHTNING ARRESTOR |  | OFFICE | F TYPE MALE |  | PS5-08-51AN-0001 |  | SATELLITE ANTENNA |  | OFFICE | F TYPE MALE
542 | PS5-08-51LA-1203-CV01 |  | T5 |  |  |  | RG6 CV FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | F TYPE MALE |  | PS5-08-51LA-1203 |  | LIGHTNING ARRESTOR |  | OFFICE | F TYPE MALE
543 | PS5-08-51AN-0001-CV03 |  | T5 |  |  |  | RG6 CV FL RET | 10 |  | PS5-08-51LA-1203 |  | LIGHTNING ARRESTOR |  | OFFICE | F TYPE MALE |  | PS5-08-51AN-0001 |  | SATELLITE ANTENNA |  | OFFICE | F TYPE MALE
544 | PS5-08-51LA-1204-CV01 |  | T5 |  |  |  | RG6 CV FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | F TYPE MALE |  | PS5-08-51LA-1204 |  | LIGHTNING ARRESTOR |  | OFFICE | F TYPE MALE
545 | PS5-08-51AN-0001-CV04 |  | T5 |  |  |  | RG6 CV FL RET | 10 |  | PS5-08-51LA-1204 |  | LIGHTNING ARRESTOR |  | OFFICE | F TYPE MALE |  | PS5-08-51AN-0001 |  | SATELLITE ANTENNA |  | OFFICE | F TYPE MALE
546 | PS5-08-01BT-1202-CN01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-01BT-1202 |  | PAGA JUNCTION BOX |  | OFFICE | M20 20A2
547 | PS5-08-01BT-1201-CN01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 15 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-01BT-1201 |  | PAGA JUNCTION BOX |  | OFFICE | M20 20A2
548 | PS5-08-13CB-1201-CX01 |  | P2 |  |  |  | 12C FOC | 15 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-13CB-1201 |  | SII SP3 SAF CABINET |  | OFFICE | - | [5 empty] | 06
549 | PS5-08-14CB-1201-CX01 |  | P2 |  |  |  | 12C FOC | 15 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-14CB-1201 |  | SII SP1 CABINET |  | OFFICE | - | [5 empty] | 06
550 | PS5-08-71SK-1206B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 25 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1206B |  | RJ45 DATA SOCKET |  | OFFICE | -
551 | PS5-08-71SK-1212B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1212B |  | RJ45 DATA SOCKET |  | OFFICE | -
552 | PS5-08-71SK-1214C-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1214C |  | RJ45 DATA SOCKET |  | OFFICE | -
553 | PS5-08-71SK-1214D-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1214D |  | RJ45 DATA SOCKET |  | OFFICE | -
554 | PS5-08-71SK-1225B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1225B |  | RJ45 DATA SOCKET |  | OFFICE | -
555 | PS5-08-71SK-1226B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1226B |  | RJ45 DATA SOCKET |  | OFFICE | -
556 | PS5-08-71SK-1228B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1228B |  | RJ45 DATA SOCKET |  | OFFICE | -
557 | PS5-08-71SK-1232B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 15 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1232B |  | RJ45 DATA SOCKET |  | OFFICE | -
558 | PS5-08-71SK-1233B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1233B |  | RJ45 DATA SOCKET |  | OFFICE | -
559 | PS5-08-71SK-1236B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1236B |  | RJ45 DATA SOCKET |  | OFFICE | -
560 | PS5-08-71SK-1242B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1242B |  | RJ45 DATA SOCKET |  | OFFICE | -
561 | PS5-08-71SK-1243B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 50 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1243B |  | RJ45 DATA SOCKET |  | OFFICE | -
562 | PS5-08-71SK-1244B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 45 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1244B |  | RJ45 DATA SOCKET |  | OFFICE | -
563 | PS5-08-71SK-1245B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 40 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-71SK-1245B |  | RJ45 DATA SOCKET |  | OFFICE | -
564 | PS5-08-71SK-1249A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 50 |  | PS5-08-11CB-1201 |  | SIE / SII SP3 SEC CABINET |  | TELECOM ROOM | - |  | PS5-08-71SK-1249A |  | RJ45 DATA SOCKET |  | OFFICE | -
565 | PS5-08-71SK-1249B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 50 |  | PS5-08-11CB-1201 |  | SIE / SII SP3 SEC CABINET |  | TELECOM ROOM | - |  | PS5-08-71SK-1249B |  | RJ45 DATA SOCKET |  | OFFICE | -
566 | PS5-08-71SK-1249C-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 50 |  | PS5-08-11CB-1201 |  | SIE / SII SP3 SEC CABINET |  | TELECOM ROOM | - |  | PS5-08-71SK-1249C |  | RJ45 DATA SOCKET |  | OFFICE | -
567 | PS5-08-71SK-1249D-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 50 |  | PS5-08-11CB-1201 |  | SIE / SII SP3 SEC CABINET |  | TELECOM ROOM | - |  | PS5-08-71SK-1249D |  | RJ45 DATA SOCKET |  | OFFICE | -
568 | PS5-08-71SK-1250A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 55 |  | PS5-08-11CB-1201 |  | SIE / SII SP3 SEC CABINET |  | TELECOM ROOM | - |  | PS5-08-71SK-1250A |  | RJ45 DATA SOCKET |  | OFFICE | -
569 | PS5-08-71SK-1250B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 55 |  | PS5-08-11CB-1201 |  | SIE / SII SP3 SEC CABINET |  | TELECOM ROOM | - |  | PS5-08-71SK-1250B |  | RJ45 DATA SOCKET |  | OFFICE | -
570 | PS5-08-13CB-1201-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-13CB-1201 |  | SP3 SAF CABINET |  | OFFICE | -
571 | PS5-08-13CB-1201-CA02 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-13CB-1201 |  | SP3 SAF CABINET |  | OFFICE | -
572 | PS5-08-13CB-1201-CA03 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-13CB-1201 |  | SP3 SAF CABINET |  | OFFICE | -
573 | PS5-08-13CB-1201-CA04 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-13CB-1201 |  | SP3 SAF CABINET |  | OFFICE | -
574 | PS5-08-13CB-1201-CA05 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-13CB-1201 |  | SP3 SAF CABINET |  | OFFICE | -
575 | PS5-08-13CB-1201-CA06 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-13CB-1201 |  | SP3 SAF CABINET |  | OFFICE | -
576 | PS5-08-14CB-1201-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-14CB-1201 |  | SII SP1 CABINET |  | OFFICE | -
577 | PS5-08-14CB-1201-CA02 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-14CB-1201 |  | SII SP1 CABINET |  | OFFICE | -
578 | PS5-08-14CB-1201-CA03 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-14CB-1201 |  | SII SP1 CABINET |  | OFFICE | -
579 | PS5-08-14CB-1201-CA04 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-14CB-1201 |  | SII SP1 CABINET |  | OFFICE | -
580 | PS5-08-14CB-1201-CA05 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-14CB-1201 |  | SII SP1 CABINET |  | OFFICE | -
581 | PS5-08-14CB-1201-CA06 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1201 |  | SIE CABINET |  | OFFICE | - |  | PS5-08-14CB-1201 |  | SII SP1 CABINET |  | OFFICE | -
582 | PS5-08-13CB-1201-CC01 |  | - |  |  |  | 8-P CABLE - 0.5 SQ. MM | 10 |  | PS5-08-13CB-1201 |  | SII SP3 SAF CABINET |  | OFFICE | - |  | PS5-08-14CB-1201 |  | SII SP1 CABINET |  | OFFICE | -
583 | PS5-08-01PA-1501-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-01PA-1501 |  | PAGA ACCESS UNIT |  | GUARDHOUSE | -
584 | PS5-08-01PA-1501-CC01 |  | - |  |  |  | 6P X 0.5 SQMM PIGTAIL | 10 |  | PS5-08-01BT-1503 |  | PAGA JUNCTION BOX |  | GUARDHOUSE | M20 20A2 |  | PS5-08-01PA-1501 |  | PAGA ACCESS UNIT |  | GUARDHOUSE | - | [5 empty] | 06
585 | PS5-08-01BT-1503-CN01 |  | G1 |  |  |  | 1P X 2.5 OS FR | 5 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-01BT-1503 |  | PAGA JUNCTION BOX |  | GUARDHOUSE | M20 20A2
586 | PS5-08-01BT-1503-CN02 |  | G1 |  |  |  | 1P X 2.5 OS FR | 5 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-01BT-1503 |  | PAGA JUNCTION BOX |  | GUARDHOUSE | M20 20A2
587 | PS5-08-01BT-1501-CR02 |  | S1 |  |  |  | 1P X 1.0 OS FR | 10 |  | PS5-08-01BT-1503 |  | PAGA JUNCTION BOX |  | GUARDHOUSE | M20 20A2 |  | PS5-08-01BT-1501 |  | PAGA JUNCTION BOX |  | GUARDHOUSE | M20 20A2
588 | PS5-08-01BT-1502-CR02 |  | S1 |  |  |  | 1P X 1.0 OS FR | 10 |  | PS5-08-01BT-1503 |  | PAGA JUNCTION BOX |  | GUARDHOUSE | M20 20A2 |  | PS5-08-01BT-1502 |  | PAGA JUNCTION BOX |  | GUARDHOUSE | M20 20A2
589 | PS5-08-85DC-1501-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1501 |  | ACS JUNCTION BOX |  | EMERGENCY EXIT | M20 Pre-Fitted |  | PS5-08-85DC-1501 |  | ACS DOOR CONTACT |  | EMERGENCY EXIT | - |  |  |  |  | Note 12 | 06
590 | PS5-08-85BT-1501-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85CP-1501 |  | ACS CONTROL PANEL |  | SAFE HAVEN | - |  | PS5-08-85BT-1501 |  | ACS JUNCTION BOX |  | EMERGENCY EXIT | M20 Pre-Fitted
591 | PS5-08-85DC-1502-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1502 |  | ACS JUNCTION BOX |  | ENTRANCE | M20 Pre-Fitted |  | PS5-08-85DC-1502 |  | ACS DOOR CONTACT |  | ENTRANCE | - |  |  |  |  | Note 12 | 06
592 | PS5-08-85BT-1502-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 10 |  | PS5-08-85CP-1501 |  | ACS CONTROL PANEL |  | SAFE HAVEN | - |  | PS5-08-85BT-1502 |  | ACS JUNCTION BOX |  | ENTRANCE | M20 Pre-Fitted
593 | PS5-08-85BR-1501-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 5 |  | PS5-08-85CP-1501 |  | ACS CONTROL PANEL |  | SECURITY ROOM | - |  | PS5-08-85BR-1501 |  | BADGE READER |  | SAFE HAVEN | -
594 | PS5-08-85BR-1502-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 5 |  | PS5-08-85CP-1501 |  | ACS CONTROL PANEL |  | SECURITY ROOM | - |  | PS5-08-85BR-1502 |  | BADGE READER |  | SAFE HAVEN | - | [5 empty] | 06
595 | PS5-08-85DC-1503-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1503 |  | ACS JUNCTION BOX |  | SAFE HAVEN | M20 Pre-Fitted |  | PS5-08-85DC-1503 |  | ACS DOOR CONTACT |  | SAFE HAVEN | - |  |  |  |  | Note 12 | 06
596 | PS5-08-85ML-1501-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1503 |  | ACS JUNCTION BOX |  | SAFE HAVEN | M20 Pre-Fitted |  | PS5-08-85ML-1501 |  | MAGNETIC DOORLOCK |  | SAFE HAVEN | - | [5 empty] | 06
597 | PS5-08-85BG-1501-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 5 |  | PS5-08-85BT-1503 |  | ACS JUNCTION BOX |  | SAFE HAVEN | M20 Pre-Fitted |  | PS5-08-85BG-1501 |  | EMERGENCY BREAK GLASS |  | SAFE HAVEN | -
598 | PS5-08-85BT-1503-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | SECURITY ROOM | - |  | PS5-08-85BT-1503 |  | ACS JUNCTION BOX |  | SAFE HAVEN | M20 Pre-Fitted
599 | PS5-08-85BT-1503-CC01 |  | A4 |  |  |  | 6P X 1.0 FL RET | 5 |  | PS5-08-85CP-1501 |  | ACS CONTROL PANEL |  | SECURITY ROOM | - |  | PS5-08-85BT-1503 |  | ACS JUNCTION BOX |  | SAFE HAVEN | M32 Pre-Fitted
600 | PS5-08-85PB-1501-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85CP-1501 |  | ACS CONTROL PANEL |  | SECURITY ROOM | - |  | PS5-08-85PB-1501 |  | PANIC PUSHBUTTON |  | SECURITY ROOM | -
601 | PS5-08-85CP-1501-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | SECURITY ROOM | - |  | PS5-08-85CP-1501 |  | ACS CONTROL PANEL |  | SECURITY ROOM | -
602 | PS5-08-71SK-1501A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1501A |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
603 | PS5-08-71SK-1501B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1501B |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
604 | PS5-08-71SK-1502A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1502A |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
605 | PS5-08-71SK-1502B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1502B |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
606 | PS5-08-71SK-1503A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1503A |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
607 | PS5-08-71SK-1503B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1503B |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
608 | PS5-08-71SK-1504A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1504A |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
609 | PS5-08-71SK-1504B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1504B |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
610 | PS5-08-71SK-1505-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1505 |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
611 | PS5-08-71SK-1506-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1506 |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
612 | PS5-08-71SK-1507-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1507 |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
613 | PS5-08-71SK-1508-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1508 |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
614 | PS5-08-71SK-1509-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1509 |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
615 | PS5-08-71SK-1511A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1511A |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
616 | PS5-08-71SK-1511B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1511B |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
617 | PS5-08-71SK-1512-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1512 |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
618 | PS5-08-71SK-1513-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1513 |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
619 | PS5-08-71SK-1514A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET |  |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE |  |  | PS5-08-71SK-1514A |  | RJ45 DATA SOCKET |  | GUARDHOUSE
620 | PS5-08-71SK-1514B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET |  |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE |  |  | PS5-08-71SK-1514B |  | RJ45 DATA SOCKET |  | GUARDHOUSE
621 | PS5-08-34LA-1501-CV01 |  | T7 |  |  |  | RG213 CV FL RET | 10 |  | PS5-08-34DS-1511 |  | SAT. PHONE BIAS BOX |  | GUARDHOUSE | N Type Male (Ref 28) |  | PS5-08-34LA-1501 |  | LIGHTNING ARRESTOR |  | GUARDHOUSE | TNC Female (Ref 28)
622 | PS5-08-34AN-0002-CV01 |  | T7 |  |  |  | RG213 CV FL RET | 5 |  | PS5-08-34LA-1501 |  | LIGHTNING ARRESTOR |  | GUARDHOUSE | TNC Male (Ref 28) |  | PS5-08-34AN-0002 |  | SAT. PHONE ANTENNA |  | GUARDHOUSE | TNC Male (Ref 28)
623 | PS5-08-23LA-1501-CV01 |  | T7 |  |  |  | RG213 CV FL RET | 5 |  | PS5-08-23BS-1501 |  | VHF RADIO BASESTATION |  | GUARDHOUSE | BNC Male (Ref 28) |  | PS5-08-23LA-1501 |  | LIGHTNING ARRESTOR |  | GUARDHOUSE | N Type Male (Ref 28)
624 | PS5-08-23AN-0002-CV01 |  | T7 |  |  |  | RG213 CV FL RET | 5 |  | PS5-08-23LA-1501 |  | LIGHTNING ARRESTOR |  | GUARDHOUSE | N Type Male (Ref 28) |  | PS5-08-23AN-0002 |  | VHF ANTENNA |  | GUARDHOUSE | N Type Male (Ref 28)
625 | PS5-08-71SK-1510A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 15 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1510A |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
626 | PS5-08-71SK-1510B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 15 |  | PS5-08-11CB-1501 |  | SIE CABINET |  | GUARDHOUSE | - |  | PS5-08-71SK-1510B |  | RJ45 DATA SOCKET |  | GUARDHOUSE | -
627 | PS5-08-85DC-1601-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1601 |  | ACS JUNCTION BOX |  | WAREHOUSE RAMP | M20 Pre-Fitted |  | PS5-08-85DC-1601 |  | ACS DOOR CONTACT |  | WAREHOUSE RAMP | - |  |  |  |  | Note 12 | 06
628 | PS5-08-85BT-1601-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 35 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | ELECT./TELECOM ROOM | - |  | PS5-08-85BT-1601 |  | ACS JUNCTION BOX |  | WAREHOUSE RAMP | M20 Pre-Fitted
629 | PS5-08-85DC-1602-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1602 |  | ACS JUNCTION BOX |  | WAREHOUSE EMERGENCY | M20 Pre-Fitted |  | PS5-08-85DC-1602 |  | ACS DOOR CONTACT |  | WAREHOUSE EMERGENCY | - |  |  |  |  | Note 12 | 06
630 | PS5-08-85BT-1602-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 30 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | ELECT./TELECOM ROOM | - |  | PS5-08-85BT-1602 |  | ACS JUNCTION BOX |  | WAREHOUSE EMERGENCY | M20 Pre-Fitted
631 | PS5-08-85DC-1603-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1603 |  | ACS JUNCTION BOX |  | WORKSHOP/WAREHOUSE | M20 Pre-Fitted |  | PS5-08-85DC-1603 |  | ACS DOOR CONTACT |  | WAREHOUSE ACCESS | - |  |  |  |  | Note 12 | 06
632 | PS5-08-85DC-1604-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1603 |  | ACS JUNCTION BOX |  | WORKSHOP/WAREHOUSE | M20 Pre-Fitted |  | PS5-08-85DC-1604 |  | ACS DOOR CONTACT |  | WAREHOUSE ACCESS | - |  |  |  |  | Note 12 | 06
633 | PS5-08-85ML-1601-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1603 |  | ACS JUNCTION BOX |  | WORKSHOP/WAREHOUSE | M20 Pre-Fitted |  | PS5-08-85ML-1601 |  | MAGNETIC DOORLOCK |  | WAREHOUSE ACCESS | - | [5 empty] | 06
634 | PS5-08-85PB-1601-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1603 |  | ACS JUNCTION BOX |  | WORKSHOP/WAREHOUSE | M20 Pre-Fitted |  | PS5-08-85PB-1601 |  | EXIT PUSHBUTTON |  | WAREHOUSE ACCESS | -
635 | PS5-08-85BG-1601-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 5 |  | PS5-08-85BT-1603 |  | ACS JUNCTION BOX |  | WORKSHOP/WAREHOUSE | M20 Pre-Fitted |  | PS5-08-85BG-1601 |  | EMERGENCY BREAK GLASS |  | WAREHOUSE ACCESS | -
636 | PS5-08-85BT-1603-CC01 |  | A4 |  |  |  | 6P X 1.0 FL RET | 10 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85BT-1603 |  | ACS JUNCTION BOX |  | WAREHOUSE ACCESS | M32 Pre-Fitted
637 | PS5-08-85BR-1601-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 10 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85BR-1601 |  | BADGE READER |  | WORKSHOP/WAREHOUSE | -
638 | PS5-08-85BT-1603-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 10 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | ELECT./TELECOM ROOM | - |  | PS5-08-85BT-1603 |  | ACS JUNCTION BOX |  | WORKSHOP/WAREHOUSE | M20 Pre-Fitted
639 | PS5-08-85DC-1605-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1604 |  | ACS JUNCTION BOX |  | WORKSHOP/WAREHOUSE | M20 Pre-Fitted |  | PS5-08-85DC-1605 |  | ACS DOOR CONTACT |  | WORKSHOP/WAREHOUSE | - |  |  |  |  | Note 12 | 06
640 | PS5-08-85DC-1606-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1604 |  | ACS JUNCTION BOX |  | WORKSHOP/WAREHOUSE | M20 Pre-Fitted |  | PS5-08-85DC-1606 |  | ACS DOOR CONTACT |  | WORKSHOP/WAREHOUSE | - |  |  |  |  | Note 12 | 06
641 | PS5-08-85BT-1604-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 25 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85BT-1604 |  | ACS JUNCTION BOX |  | WORKSHOP/WAREHOUSE | M20 Pre-Fitted
642 | PS5-08-85BR-1604-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 10 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85BR-1604 |  | BADGE READER |  | WORKSHOP/WAREHOUSE | -
643 | PS5-08-85DC-1607-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1607 |  | ACS JUNCTION BOX |  | AC CONTROLLED STORE | M20 Pre-Fitted |  | PS5-08-85DC-1607 |  | ACS DOOR CONTACT |  | WORKSHOP/WAREHOUSE | - |  |  |  |  | Note 12 | 06
644 | PS5-08-85ML-1605-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1607 |  | ACS JUNCTION BOX |  | AC CONTROLLED STORE | M20 Pre-Fitted |  | PS5-08-85ML-1605 |  | MAGNETIC DOORLOCK |  | WORKSHOP/WAREHOUSE | - | [5 empty] | 06
645 | PS5-08-85PB-1604-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1607 |  | ACS JUNCTION BOX |  | AC CONTROLLED STORE | M20 Pre-Fitted |  | PS5-08-85PB-1604 |  | EXIT PUSHBUTTON |  | WORKSHOP/WAREHOUSE | -
646 | PS5-08-85BG-1604-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 5 |  | PS5-08-85BT-1607 |  | ACS JUNCTION BOX |  | AC CONTROLLED STORE | M20 Pre-Fitted |  | PS5-08-85BG-1604 |  | EMERGENCY BREAK GLASS |  | WORKSHOP/WAREHOUSE | -
647 | PS5-08-85BT-1607-CC01 |  | A4 |  |  |  | 6P X 1.0 FL RET | 10 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85BT-1607 |  | ACS JUNCTION BOX |  | WORKSHOP/WAREHOUSE | M32 Pre-Fitted
648 | PS5-08-85BT-1607-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 15 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | ELECT./TELECOM ROOM | - |  | PS5-08-85BT-1607 |  | ACS JUNCTION BOX |  | AC CONTROLLED STORE | M20 Pre-Fitted
649 | PS5-08-85BR-1603-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 10 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85BR-1603 |  | BADGE READER |  | ELEC. INS. STORE ENTRANCE | -
650 | PS5-08-85DC-1608-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1606 |  | ACS JUNCTION BOX |  | ELEC. INS. STORE ENTRANCE | M20 Pre-Fitted |  | PS5-08-85DC-1608 |  | ACS DOOR CONTACT |  | ELEC. INS. STORE ENTRANCE | - |  |  |  |  | Note 12 | 06
651 | PS5-08-85DC-1609-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1606 |  | ACS JUNCTION BOX |  | ELEC. INS. STORE ENTRANCE | M20 Pre-Fitted |  | PS5-08-85DC-1609 |  | ACS DOOR CONTACT |  | ELEC. INS. STORE ENTRANCE | - |  |  |  |  | Note 12 | 06
652 | PS5-08-85ML-1603-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1606 |  | ACS JUNCTION BOX |  | ELEC. INS. STORE ENTRANCE | M20 Pre-Fitted |  | PS5-08-85ML-1603 |  | MAGNETIC DOORLOCK |  | ELEC. INS. STORE ENTRANCE | - | [5 empty] | 06
653 | PS5-08-85PB-1603-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1606 |  | ACS JUNCTION BOX |  | ELEC. INS. STORE ENTRANCE | M20 Pre-Fitted |  | PS5-08-85PB-1603 |  | EXIT PUSHBUTTON |  | ELEC. INS. STORE ENTRANCE | -
654 | PS5-08-85BG-1603-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 5 |  | PS5-08-85BT-1606 |  | ACS JUNCTION BOX |  | ELEC. INS. STORE ENTRANCE | M20 Pre-Fitted |  | PS5-08-85BG-1603 |  | EMERGENCY BREAK GLASS |  | ELEC. INS. STORE ENTRANCE | -
655 | PS5-08-85BT-1606-CC01 |  | A4 |  |  |  | 6P X 1.0 FL RET | 10 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85BT-1606 |  | ACS JUNCTION BOX |  | ELEC. INS. STORE ENTRANCE | M32 Pre-Fitted
656 | PS5-08-85BT-1606-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 15 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | ELECT./TELECOM ROOM | - |  | PS5-08-85BT-1606 |  | ACS JUNCTION BOX |  | ELEC. INS. STORE ENTRANCE | M20 Pre-Fitted
657 | PS5-08-85BR-1602-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 25 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85BR-1602 |  | BADGE READER |  | WAREHOUSE OFFICE ENTRANCE | -
658 | PS5-08-85DC-1617-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1605 |  | ACS JUNCTION BOX |  | WAREHOUSE OFFICE ENTRANCE | M20 Pre-Fitted |  | PS5-08-85DC-1617 |  | ACS DOOR CONTACT |  | WAREHOUSE OFFICE ENTRANCE | - |  |  |  |  | Note 12 | 06
659 | PS5-08-85ML-1602-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1605 |  | ACS JUNCTION BOX |  | WAREHOUSE OFFICE ENTRANCE | M20 Pre-Fitted |  | PS5-08-85ML-1602 |  | MAGNETIC DOORLOCK |  | WAREHOUSE OFFICE ENTRANCE | - | [5 empty] | 06
660 | PS5-08-85PB-1602-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1605 |  | ACS JUNCTION BOX |  | WAREHOUSE OFFICE ENTRANCE | M20 Pre-Fitted |  | PS5-08-85PB-1602 |  | EXIT PUSHBUTTON |  | WAREHOUSE OFFICE ENTRANCE | -
661 | PS5-08-85BG-1602-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 5 |  | PS5-08-85BT-1605 |  | ACS JUNCTION BOX |  | WAREHOUSE OFFICE ENTRANCE | M20 Pre-Fitted |  | PS5-08-85BG-1602 |  | EMERGENCY BREAK GLASS |  | WAREHOUSE OFFICE ENTRANCE | -
662 | PS5-08-85BT-1605-CC01 |  | A4 |  |  |  | 6P X 1.0 FL RET | 30 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85BT-1605 |  | ACS JUNCTION BOX |  | WAREHOUSE OFFICE ENTRANCE | M32 Pre-Fitted
663 | PS5-08-85BT-1605-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 30 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | ELECT./TELECOM ROOM | - |  | PS5-08-85BT-1605 |  | ACS JUNCTION BOX |  | WAREHOUSE OFFICE ENTRANCE | M20 Pre-Fitted
664 | PS5-08-85DC-1610-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1614 |  | ACS JUNCTION BOX |  | WORKSHOP EMERG. ESCAPE | M20 Pre-Fitted |  | PS5-08-85DC-1610 |  | ACS DOOR CONTACT |  | WORKSHOP EMERG. ESCAPE | - |  |  |  |  | Note 12 | 06
665 | PS5-08-85BT-1614-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 10 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85BT-1614 |  | ACS JUNCTION BOX |  | WORKSHOP EMERG. ESCAPE | M20 Pre-Fitted
666 | PS5-08-85DC-1611-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1613 |  | ACS JUNCTION BOX |  | OIL SPILL RESPONSE STORE | M20 Pre-Fitted |  | PS5-08-85DC-1611 |  | ACS DOOR CONTACT |  | OIL SPILL RESPONSE STORE | - |  |  |  |  | Note 12 | 06
667 | PS5-08-85DC-1612-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1613 |  | ACS JUNCTION BOX |  | OIL SPILL RESPONSE STORE | M20 Pre-Fitted |  | PS5-08-85DC-1612 |  | ACS DOOR CONTACT |  | OIL SPILL RESPONSE STORE | - |  |  |  |  | Note 12 | 06
668 | PS5-08-85BT-1613-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 10 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85BT-1613 |  | ACS JUNCTION BOX |  | OIL SPILL RESPONSE STORE | M20 Pre-Fitted
669 | PS5-08-85DC-1613-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1612 |  | ACS JUNCTION BOX |  | AC CTRL. STORE EMERG. ESCAPE | M20 Pre-Fitted |  | PS5-08-85DC-1613 |  | ACS DOOR CONTACT |  | AC CTRL. STORE EMERG. ESCAPE | - |  |  |  |  | Note 12 | 06
670 | PS5-08-85BT-1612-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 15 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85BT-1612 |  | ACS JUNCTION BOX |  | AC CTRL. STORE EMERG. ESCAPE | M20 Pre-Fitted
671 | PS5-08-85DC-1614-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1611 |  | ACS JUNCTION BOX |  | WORKSHOP EMERG. ESCAPE | M20 Pre-Fitted |  | PS5-08-85DC-1614 |  | ACS DOOR CONTACT |  | WORKSHOP EMERG. ESCAPE | - |  |  |  |  | Note 12 | 06
672 | PS5-08-85BT-1611-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 30 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85BT-1611 |  | ACS JUNCTION BOX |  | WORKSHOP EMERG. ESCAPE | M20 Pre-Fitted
673 | PS5-08-85DC-1615-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1610 |  | ACS JUNCTION BOX |  | WORKSHOP RAMP | M20 Pre-Fitted |  | PS5-08-85DC-1615 |  | ACS DOOR CONTACT |  | WORKSHOP RAMP | - |  |  |  |  | Note 12 | 06
674 | PS5-08-85BT-1610-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 25 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85BT-1610 |  | ACS JUNCTION BOX |  | WORKSHOP RAMP | M20 Pre-Fitted
675 | PS5-08-85DC-1616-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1609 |  | ACS JUNCTION BOX |  | WORKSHOP ENTRANCE | M20 Pre-Fitted |  | PS5-08-85DC-1616 |  | ACS DOOR CONTACT |  | WORKSHOP ENTRANCE | - |  |  |  |  | Note 12 | 06
676 | PS5-08-85BT-1609-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 25 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85BT-1609 |  | ACS JUNCTION BOX |  | WORKSHOP ENTRANCE | M20 Pre-Fitted
677 | PS5-08-85BR-1605-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 15 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85BR-1605 |  | BADGE READER |  | ELEC. INS. WORKSHOP ENTRANCE | -
678 | PS5-08-85DC-1618-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1608 |  | ACS JUNCTION BOX |  | ELEC. INS. WORKSHOP ENTRANCE | M20 Pre-Fitted |  | PS5-08-85DC-1618 |  | ACS DOOR CONTACT |  | ELEC. INS. WORKSHOP ENTRANCE | - |  |  |  |  | Note 12 | 06
679 | PS5-08-85ML-1604-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1608 |  | ACS JUNCTION BOX |  | ELEC. INS. WORKSHOP ENTRANCE | M20 Pre-Fitted |  | PS5-08-85ML-1604 |  | MAGNETIC DOORLOCK |  | ELEC. INS. WORKSHOP ENTRANCE | - | [5 empty] | 06
680 | PS5-08-85PB-1605-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1608 |  | ACS JUNCTION BOX |  | ELEC. INS. WORKSHOP ENTRANCE | M20 Pre-Fitted |  | PS5-08-85PB-1605 |  | EXIT PUSHBUTTON |  | ELEC. INS. WORKSHOP ENTRANCE | -
681 | PS5-08-85BG-1605-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 5 |  | PS5-08-85BT-1608 |  | ACS JUNCTION BOX |  | ELEC. INS. WORKSHOP ENTRANCE | M20 Pre-Fitted |  | PS5-08-85BG-1605 |  | EMERGENCY BREAK GLASS |  | ELEC. INS. WORKSHOP ENTRANCE | -
682 | PS5-08-85BT-1608-CC01 |  | A4 |  |  |  | 6P X 1.0 FL RET | 15 |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | ELEC. INS. WORKSHOP ENTRANCE | - |  | PS5-08-85BT-1608 |  | ACS JUNCTION BOX |  | ELEC. INS. WORKSHOP ENTRANCE | M32 Pre-Fitted
683 | PS5-08-85CP-1601-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-85CP-1601 |  | CONTROL PANEL |  | WORKSHOP/WAREHOUSE | -
684 | PS5-08-85BT-1608-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 15 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | ELECT./TELECOM ROOM | - |  | PS5-08-85BT-1608 |  | ACS JUNCTION BOX |  | ELEC. INS. STORE ENTRANCE | M20 Pre-Fitted
685 | PS5-08-71SK-1601A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 25 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-71SK-1601A |  | RJ45 DATA SOCKET |  | WORKSHOP/WAREHOUSE | -
686 | PS5-08-71SK-1601B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 25 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-71SK-1601B |  | RJ45 DATA SOCKET |  | WORKSHOP/WAREHOUSE | -
687 | PS5-08-71SK-1602A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 25 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-71SK-1602A |  | RJ45 DATA SOCKET |  | WORKSHOP/WAREHOUSE | -
688 | PS5-08-71SK-1602B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 25 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-71SK-1602B |  | RJ45 DATA SOCKET |  | WORKSHOP/WAREHOUSE | -
689 | PS5-08-71SK-1603A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 20 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-71SK-1603A |  | RJ45 DATA SOCKET |  | WORKSHOP/WAREHOUSE | -
690 | PS5-08-71SK-1603B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 20 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-71SK-1603B |  | RJ45 DATA SOCKET |  | WORKSHOP/WAREHOUSE | -
691 | PS5-08-71SK-1604A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 20 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-71SK-1604A |  | RJ45 DATA SOCKET |  | WORKSHOP/WAREHOUSE | -
692 | PS5-08-71SK-1604B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 20 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-71SK-1604B |  | RJ45 DATA SOCKET |  | WORKSHOP/WAREHOUSE | -
693 | PS5-08-71SK-1605A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 25 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-71SK-1605A |  | RJ45 DATA SOCKET |  | WORKSHOP/WAREHOUSE | -
694 | PS5-08-71SK-1605B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 25 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-71SK-1605B |  | RJ45 DATA SOCKET |  | WORKSHOP/WAREHOUSE | -
695 | PS5-08-71SK-1606-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 15 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-71SK-1606 |  | RJ45 DATA SOCKET |  | WORKSHOP/WAREHOUSE | -
696 | PS5-08-71SK-1607-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 25 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-71SK-1607 |  | RJ45 DATA SOCKET |  | WORKSHOP/WAREHOUSE | -
697 | PS5-08-71SK-1608-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-71SK-1608 |  | RJ45 DATA SOCKET |  | WORKSHOP/WAREHOUSE | -
698 | PS5-08-71SK-1609-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-71SK-1609 |  | RJ45 DATA SOCKET |  | WORKSHOP/WAREHOUSE | -
699 | PS5-08-71SK-1610-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 20 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-71SK-1610 |  | RJ45 DATA SOCKET |  | WORKSHOP/WAREHOUSE | -
700 | PS5-08-71SK-1611-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 30 |  | PS5-08-11CB-1601 |  | SIE CABINET |  | WORKSHOP/WAREHOUSE | - |  | PS5-08-71SK-1611 |  | RJ45 DATA SOCKET |  | WORKSHOP/WAREHOUSE | -
701 | PS5-08-23AN-1601-CV01 |  | T1 |  |  |  | 1/2" CV FL RET | 40 |  | PS5-08-23LA-1601 |  | LIGHTNING ARRESTOR |  | WORKSHOP/WAREHOUSE | N Type Male (Ref 28) |  | PS5-08-23AN-1601 |  | FLAT PANELANTENNA |  | WORKSHOP/WAREHOUSE | N Type Male (Ref 28)
702 | PS5-08-23AN-0003-CV01 |  | T1 |  |  |  | 1/2" CV FL RET | 10 |  | PS5-08-23LA-1601 |  | LIGHTNING ARRESTOR |  | WORKSHOP/WAREHOUSE | N Type Male (Ref 28) |  | PS5-08-23AN-0003 |  | INDOOR ANTENNA |  | WORKSHOP/WAREHOUSE | N Type Male (Ref 28)
703 | PS5-08-85DC-1901-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1903 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85DC-1901 |  | ACS DOOR CONTACT |  | GEN. ELECT. BLDG | - |  |  |  |  | Note 12 | 06
704 | PS5-08-85DC-1902-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1903 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85DC-1902 |  | ACS DOOR CONTACT |  | GEN. ELECT. BLDG | - |  |  |  |  | Note 12 | 06
705 | PS5-08-85BT-1903-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 15 |  | PS5-08-85CP-1901 |  | CONTROL PANEL |  | GEN. ELECT. BLDG | - |  | PS5-08-85BT-1903 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted
706 | PS5-08-85DC-1903-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1904 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85DC-1903 |  | ACS DOOR CONTACT |  | GEN. ELECT. BLDG | - |  |  |  |  | Note 12 | 06
707 | PS5-08-85DC-1904-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1904 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85DC-1904 |  | ACS DOOR CONTACT |  | GEN. ELECT. BLDG | - |  |  |  |  | Note 12 | 06
708 | PS5-08-85BT-1904-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 20 |  | PS5-08-85CP-1901 |  | CONTROL PANEL |  | GEN. ELECT. BLDG | - |  | PS5-08-85BT-1904 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted
709 | PS5-08-85DC-1905-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1905 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85DC-1905 |  | ACS DOOR CONTACT |  | GEN. ELECT. BLDG | - |  |  |  |  | Note 12 | 06
710 | PS5-08-85DC-1906-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1905 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85DC-1906 |  | ACS DOOR CONTACT |  | GEN. ELECT. BLDG | - |  |  |  |  | Note 12 | 06
711 | PS5-08-85BT-1905-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 20 |  | PS5-08-85CP-1901 |  | CONTROL PANEL |  | GEN. ELECT. BLDG | - |  | PS5-08-85BT-1905 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted
712 | PS5-08-85DC-1907-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1906 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85DC-1907 |  | ACS DOOR CONTACT |  | GEN. ELECT. BLDG | - |  |  |  |  | Note 12 | 06
713 | PS5-08-85DC-1908-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1906 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85DC-1908 |  | ACS DOOR CONTACT |  | GEN. ELECT. BLDG | - |  |  |  |  | Note 12 | 06
714 | PS5-08-85BT-1906-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 15 |  | PS5-08-85CP-1901 |  | CONTROL PANEL |  | GEN. ELECT. BLDG | - |  | PS5-08-85BT-1906 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted
715 | PS5-08-85DC-1909-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1907 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85DC-1909 |  | ACS DOOR CONTACT |  | GEN. ELECT. BLDG | - |  |  |  |  | Note 12 | 06
716 | PS5-08-85DC-1910-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1907 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85DC-1910 |  | ACS DOOR CONTACT |  | GEN. ELECT. BLDG | - |  |  |  |  | Note 12 | 06
717 | PS5-08-85BT-1907-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 10 |  | PS5-08-85CP-1901 |  | CONTROL PANEL |  | GEN. ELECT. BLDG | - |  | PS5-08-85BT-1907 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted
718 | PS5-08-85DC-1911-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1901 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85DC-1911 |  | ACS DOOR CONTACT |  | GEN. ELECT. BLDG | - |  |  |  |  | Note 12 | 06
719 | PS5-08-85ML-1901-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1901 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85ML-1901 |  | MAGNETIC DOORLOCK |  | GEN. ELECT. BLDG | - | [5 empty] | 06
720 | PS5-08-85PB-1901-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1901 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85PB-1901 |  | EXIT PUSHBUTTON |  | GEN. ELECT. BLDG | -
721 | PS5-08-85BG-1901-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 5 |  | PS5-08-85BT-1901 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85BG-1901 |  | EMERGENCY BREAK GLASS |  | GEN. ELECT. BLDG | -
722 | PS5-08-85BR-1901-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 5 |  | PS5-08-85CP-1901 |  | CONTROL PANEL |  | GEN. ELECT. BLDG | - |  | PS5-08-85BR-1901 |  | BADGE READER |  | GEN. ELECT. BLDG | -
723 | PS5-08-85BT-1901-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 25 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-85BT-1901 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted
724 | PS5-08-85BT-1901-CC01 |  | A4 |  |  |  | 6P X 1.0 FL RET | 15 |  | PS5-08-85CP-1901 |  | CONTROL PANEL |  | GEN. ELECT. BLDG | - |  | PS5-08-85BT-1901 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M32 Pre-Fitted
725 | PS5-08-85BT-1901-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET |  |  | PS5-08-85CP-1901 |  | CONTROL PANEL |  | GEN. ELECT. BLDG |  |  | PS5-08-85BT-1901 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG
726 | PS5-08-85DC-1912-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1902 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85DC-1912 |  | ACS DOOR CONTACT |  | GEN. ELECT. BLDG | - |  |  |  |  | Note 12 | 06
727 | PS5-08-85ML-1902-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1902 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85ML-1902 |  | MAGNETIC DOORLOCK |  | GEN. ELECT. BLDG | -
728 | PS5-08-85PB-1902-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1902 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85PB-1902 |  | EXIT PUSHBUTTON |  | GEN. ELECT. BLDG | -
729 | PS5-08-85BG-1902-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 5 |  | PS5-08-85BT-1902 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85BG-1902 |  | EMERGENCY BREAK GLASS |  | GEN. ELECT. BLDG | -
730 | PS5-08-85BR-1902-CC01 |  | A2 |  |  |  | 2P X 1.0 FL RET | 35 |  | PS5-08-85CP-1901 |  | CONTROL PANEL |  | GEN. ELECT. BLDG | - |  | PS5-08-85BR-1902 |  | BADGE READER |  | GEN. ELECT. BLDG | -
731 | PS5-08-85BT-1902-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 30 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-85BT-1902 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted
732 | PS5-08-85BT-1902-CC01 |  | A4 |  |  |  | 6P X 1.0 FL RET | 35 |  | PS5-08-85CP-1901 |  | CONTROL PANEL |  | GEN. ELECT. BLDG | - |  | PS5-08-85BT-1902 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M32 Pre-Fitted
733 | PS5-08-85BT-1912-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET |  |  | PS5-08-85CP-1901 |  | CONTROL PANEL |  | GEN. ELECT. BLDG |  |  | PS5-08-85BT-1912 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG
734 | PS5-08-85DC-1913-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1908 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85DC-1913 |  | ACS DOOR CONTACT |  | GEN. ELECT. BLDG | - |  |  |  |  | Note 12 | 06
735 | PS5-08-85DC-1914-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1908 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85DC-1914 |  | ACS DOOR CONTACT |  | GEN. ELECT. BLDG | - |  |  |  |  | Note 12 | 06
736 | PS5-08-85DC-1915-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1908 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85DC-1915 |  | ACS DOOR CONTACT |  | GEN. ELECT. BLDG | - |  |  |  |  | Note 12 | 06
737 | PS5-08-85BT-1908-CJ01 |  | A4 |  |  |  | 6P X 1.0 FL RET | 40 |  | PS5-08-85CP-1901 |  | CONTROL PANEL |  | GEN. ELECT. BLDG | - |  | PS5-08-85BT-1908 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M32 Pre-Fitted
738 | PS5-08-85CP-1901-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 20 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-85CP-1901 |  | CONTROL PANEL |  | GEN. ELECT. BLDG | - | [5 empty] | 06
739 | PS5-08-71SK-1901-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 10 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-71SK-1901 |  | RJ45 DATA SOCKET |  | GEN. ELECT. BLDG | -
740 | PS5-08-71SK-1903A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-71SK-1903A |  | RJ45 DATA SOCKET |  | GEN. ELECT. BLDG | -
741 | PS5-08-71SK-1903B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-71SK-1903B |  | RJ45 DATA SOCKET |  | GEN. ELECT. BLDG | -
742 | PS5-08-71SK-1904A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-71SK-1904A |  | RJ45 DATA SOCKET |  | GEN. ELECT. BLDG | -
743 | PS5-08-71SK-1904B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-71SK-1904B |  | RJ45 DATA SOCKET |  | GEN. ELECT. BLDG | -
744 | PS5-08-71SK-1905A-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-71SK-1905A |  | RJ45 DATA SOCKET |  | GEN. ELECT. BLDG | -
745 | PS5-08-71SK-1905B-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 5 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-71SK-1905B |  | RJ45 DATA SOCKET |  | GEN. ELECT. BLDG | -
746 | PS5-08-52CM-1901-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-52CM-1901 |  | DOME CAMERA |  | GEN. ELECT. BLDG | -
747 | PS5-08-52CM-1902-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 45 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-52CM-1902 |  | DUAL DOME CAMERA-1 |  | GEN. ELECT. BLDG | -
748 | PS5-08-52CM-1903-CA01 |  | QI |  |  |  | 4P, 23 AWG FL RET | 35 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-52CM-1903 |  | DUAL DOME CAMERA-2 |  | GEN. ELECT. BLDG | -
749 | PS5-08-23AN-1901-CV01 |  | T1 |  |  |  | 1/2" CV FL RET | 10 |  | PS5-08-23LA-1901 |  | LIGHTNING ARRESTOR |  | GEN. ELECT. BLDG | N Type Male (Ref 28) |  | PS5-08-23AN-1901 |  | FLAT PANELANTENNA |  | GEN. ELECT. BLDG | N Type Male (Ref 28)
750 | PS5-08-23AN-0005-CV01 |  | T1 |  |  |  | 1/2" CV FL RET | 10 |  | PS5-08-23LA-1901 |  | LIGHTNING ARRESTOR |  | GEN. ELECT. BLDG | N Type Male (Ref 28) |  | PS5-08-23AN-0005 |  | INDOOR ANTENNA |  | GEN. ELECT. BLDG | N Type Male (Ref 28)
751 | PS5-08-85DC-1916-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-85BT-1909 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85DC-1916 |  | ACS DOOR CONTACT |  | GEN. ELECT. BLDG | - | [5 empty] | 06
752 | PS5-08-85BT-1909-CJ01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 38 |  | PS5-08-85CP-1901 |  | CONTROL PANEL |  | GEN. ELECT. BLDG | M20 Pre-Fitted |  | PS5-08-85BT-1909 |  | ACS JUNCTION BOX |  | GEN. ELECT. BLDG | M20 Pre-Fitted
753 | PS5-08-12BT-1903-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 115 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-12BT-1903 |  | WAP JUNCTION BOX |  | POWER GENERATOR BLDG | M20 20S-E1X
754 | PS5-08-12AP-1903-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-12BT-1903 |  | WAP JUNCTION BOX |  | POWER GENERATOR BLDG | M20 20SA2 |  | PS5-08-12AP-1903 |  | WIRELESS ACCESS POINT |  | POWER GENERATOR BLDG | M20 Pre-Fitted
755 | PS5-08-12BT-1904-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 140 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-12BT-1904 |  | WAP JUNCTION BOX |  | POWER GENERATOR BLDG | M20 20S-E1X
756 | PS5-08-12AP-1904-CN01 |  | A1 |  |  |  | 1P X 1.0 FL RET | 5 |  | PS5-08-12BT-1904 |  | WAP JUNCTION BOX |  | POWER GENERATOR BLDG | M20 20SA2 |  | PS5-08-12AP-1904 |  | WIRELESS ACCESS POINT |  | POWER GENERATOR BLDG | M20 Pre-Fitted
757 | PS5-08-03TP-1903-CJ01 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 115 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-03TP-1903 |  | OUTDOOR TELEPHONE |  | POWER GENERATOR BLDG | M20 20S16-E1X
758 | PS5-08-03TP-1903-CJ02 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 5 |  | PS5-08-03FB-1903 |  | FLASHING BEACON/SOUNDER |  | FIELD | M20 20S16-E1X |  | PS5-08-03TP-1903 |  | OUTDOOR TELEPHONE |  | POWER GENERATOR BLDG | M20 20S16-E1X
759 | PS5-08-03TP-1904-CJ01 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 70 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-03TP-1904 |  | OUTDOOR TELEPHONE |  | POWER GENERATOR BLDG | M20 20S16-E1X
760 | PS5-08-03TP-1904-CJ02 |  | R1 |  |  |  | 1P X 0.5 GSWB FL RET | 5 |  | PS5-08-03FB-1904 |  | FLASHING BEACON/SOUNDER |  | FIELD | M20 20S16-E1X |  | PS5-08-03TP-1904 |  | OUTDOOR TELEPHONE |  | POWER GENERATOR BLDG | M20 20S16-E1X
761 | PS5-08-52CM-0135-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 115 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-52CM-0135 |  | CCTV SA PTZ CAMERA |  | POWER GENERATOR BLDG | -
762 | PS5-08-52TK-0135-CC01 |  | - |  |  |  | 2P (.75mm2) - Unarmoured, Manufacturer Cable | 10 |  | PS5-08-52CM-0135 |  | CCTV SA PTZ CAMERA |  | POWER GENERATOR BLDG | - |  | PS5-08-52TK-0135 |  | CCTV WATER TANK |  | POWER GENERATOR BLDG | M20 Pre-Fitted
763 | PS5-08-52CM-0136-CX01 |  | P2 |  |  |  | 4C SM GSWB FOC | 100 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-52CM-0136 |  | CCTV SA PTZ CAMERA |  | POWER GENERATOR BLDG | -
764 | PS5-08-52TK-0136-CC01 |  | - |  |  |  | 2P (.75mm2) - Unarmoured, Manufacturer Cable | 10 |  | PS5-08-52CM-0136 |  | CCTV SA PTZ CAMERA |  | POWER GENERATOR BLDG | - |  | PS5-08-52TK-0136 |  | CCTV WATER TANK |  | POWER GENERATOR BLDG | M20 Pre-Fitted
765 | PS5-08-52CM-0137-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 85 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-52CM-0137 |  | CCTV SA PTZ CAMERA |  | POWER GENERATOR BLDG | -
766 | PS5-08-52TK-0137-CC01 |  | - |  |  |  | 2P (.75mm2) - Unarmoured, Manufacturer Cable | 10 |  | PS5-08-52CM-0137 |  | CCTV SA PTZ CAMERA |  | POWER GENERATOR BLDG | - |  | PS5-08-52TK-0137 |  | CCTV WATER TANK |  | POWER GENERATOR BLDG | M20 Pre-Fitted
767 | PS5-08-52CM-0140-CA01 |  | QO |  |  |  | 4P, 23 AWG SWA FL RET | 70 |  | PS5-08-11CB-1901 |  | SIE CABINET |  | GEN. ELECT. BLDG | - |  | PS5-08-52CM-0140 |  | CCTV SA PTZ CAMERA |  | POWER GENERATOR BLDG | -
768 | PS5-08-52TK-0140-CC01 |  | - |  |  |  | 2P (.75mm2) - Unarmoured, Manufacturer Cable | 10 |  | PS5-08-52CM-0140 |  | CCTV SA PTZ CAMERA |  | POWER GENERATOR BLDG | - |  | PS5-08-52TK-0140 |  | CCTV WATER TANK |  | POWER GENERATOR BLDG | M20 Pre-Fitted

## Trace Heating - Cable Schedule
PROJECT NO. : 415000-00095
Cable Details | [9 empty] | From Equipment | [6 empty] | To Equipment
Sr. No. | Cable Tag. | Voltage Grade | Type | System Voltage | Drum No | Cores | Size (mm²) | Actual length laying done (m) | planned Length (m) | Tag No. | Cub. Ref | Description | G&T completed | Location | Gland Type | Entry Thread | Tag No. | Cub. Ref | Description | G&T Completed | Location | Gland Type | Entry Thread | Cable routing plan | Cable Routing Drawing | Outer Diameter (mm) | Remarks | Rev | DPS | Cable pulling date | Cable laying RFI Num | Drum tested RFI | Coiled length
1 | PS5-79-IG-0001-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95 | 5 |  | PS5-79-IV-0001 | - | 63 kVA Transformer |  | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0001 |  | Heat Tracing Panel |  | Field | SIND M50-Metal-Gland | M50 |  | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
2 | PS5-79-IG-0002-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95 | 5 |  | PS5-79-IV-0002 | - | 100 kVA Transformer |  | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0002 |  | Heat Tracing Panel |  | Field | SIND M50-Metal-Gland | M50 |  | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
3 | PS5-79-IG-0003-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95 | 5 |  | PS5-79-IV-0003 | - | 63 kVA Transformer |  | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0003 |  | Heat Tracing Panel |  | Field | SIND M50-Metal-Gland | M50 |  | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
4 | PS5-79-IG-0004-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95 | 5 |  | PS5-79-IV-0004 | - | 63 kVA Transformer |  | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0004 |  | Heat Tracing Panel |  | Field | SIND M50-Metal-Gland | M50 |  | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
5 | PS5-79-IG-0005-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95 | 5 |  | PS5-79-IV-0005 | - | 100 kVA Transformer |  | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0005 |  | Heat Tracing Panel |  | Field | SIND M50-Metal-Gland | M50 |  | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
6 | PS5-79-IG-0006-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95 | 5 |  | PS5-79-IV-0006 | - | 63 kVA Transformer |  | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0006 |  | Heat Tracing Panel |  | Field | SIND M50-Metal-Gland | M50 |  | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
7 | PS5-79-IG-0007-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95 | 5 |  | PS5-79-IV-0007 | - | 100 kVA Transformer |  | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0007 |  | Heat Tracing Panel |  | Field | SIND M50-Metal-Gland | M50 |  | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
8 | PS5-79-IG-0008-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95 | 5 |  | PS5-79-IV-0008 | - | 100 kVA Transformer |  | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0008 |  | Heat Tracing Panel |  | Field | SIND M50-Metal-Gland | M50 |  | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
9 | PS5-79-IG-0009-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95 | 5 |  | PS5-79-IV-0009 | - | 100 kVA Transformer |  | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0009 |  | Heat Tracing Panel |  | Field | SIND M50-Metal-Gland | M50 |  | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
10 | PS5-79-IG-0010-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95 | 5 |  | PS5-79-IV-0010 | - | 100 kVA Transformer |  | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0010 |  | Heat Tracing Panel |  | Field | SIND M50-Metal-Gland | M50 |  | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
11 | PS5-79-IG-0011-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95 | 5 |  | PS5-79-IV-0011 | - | 100 kVA Transformer |  | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0011 |  | Heat Tracing Panel |  | Field | SIND M50-Metal-Gland | M50 |  | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
12 | PS5-79-IG-0012-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95 | 5 |  | PS5-79-IV-0012 | - | 100 kVA Transformer |  | Outdoor | SIND M50-Metal-Gland | M50 | PS5-79-IG-0012 |  | Heat Tracing Panel |  | Field | SIND M50-Metal-Gland | M50 |  | TZ-MID-68-NVS1-150359 | 45 |  | 00 | nVent
13 | PS5-79-IG-0001-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95 | 5 |  | PS5-79-IV-0001 | - | 63 kVA Transformer |  | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0001 |  | Heat Tracing Panel |  | Field | SIND M25-Metal-Gland-PE | M25 |  | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
14 | PS5-79-IG-0002-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95 | 5 |  | PS5-79-IV-0002 | - | 100 kVA Transformer |  | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0002 |  | Heat Tracing Panel |  | Field | SIND M25-Metal-Gland-PE | M25 |  | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
15 | PS5-79-IG-0003-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95 | 5 |  | PS5-79-IV-0003 | - | 63 kVA Transformer |  | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0003 |  | Heat Tracing Panel |  | Field | SIND M25-Metal-Gland-PE | M25 |  | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
16 | PS5-79-IG-0004-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95 | 5 |  | PS5-79-IV-0004 | - | 63 kVA Transformer |  | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0004 |  | Heat Tracing Panel |  | Field | SIND M25-Metal-Gland-PE | M25 |  | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
17 | PS5-79-IG-0005-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95 | 5 |  | PS5-79-IV-0005 | - | 100 kVA Transformer |  | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0005 |  | Heat Tracing Panel |  | Field | SIND M25-Metal-Gland-PE | M25 |  | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
18 | PS5-79-IG-0006-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95 | 5 |  | PS5-79-IV-0006 | - | 63 kVA Transformer |  | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0006 |  | Heat Tracing Panel |  | Field | SIND M25-Metal-Gland-PE | M25 |  | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
19 | PS5-79-IG-0007-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95 | 5 |  | PS5-79-IV-0007 | - | 100 kVA Transformer |  | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0007 |  | Heat Tracing Panel |  | Field | SIND M25-Metal-Gland-PE | M25 |  | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
20 | PS5-79-IG-0008-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95 | 5 |  | PS5-79-IV-0008 | - | 100 kVA Transformer |  | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0008 |  | Heat Tracing Panel |  | Field | SIND M25-Metal-Gland-PE | M25 |  | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
21 | PS5-79-IG-0009-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95 | 5 |  | PS5-79-IV-0009 | - | 100 kVA Transformer |  | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0009 |  | Heat Tracing Panel |  | Field | SIND M25-Metal-Gland-PE | M25 |  | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
22 | PS5-79-IG-0010-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95 | 5 |  | PS5-79-IV-0010 | - | 100 kVA Transformer |  | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0010 |  | Heat Tracing Panel |  | Field | SIND M25-Metal-Gland-PE | M25 |  | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
23 | PS5-79-IG-0011-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95 | 5 |  | PS5-79-IV-0011 | - | 100 kVA Transformer |  | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0011 |  | Heat Tracing Panel |  | Field | SIND M25-Metal-Gland-PE | M25 |  | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
24 | PS5-79-IG-0012-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95 | 5 |  | PS5-79-IV-0012 | - | 100 kVA Transformer |  | Outdoor | SIND M25-Metal-Gland-PE | M25 | PS5-79-IG-0012 |  | Heat Tracing Panel |  | Field | SIND M25-Metal-Gland-PE | M25 |  | TZ-MID-68-NVS1-150359 | 24 | PE Cable | 01 | nVent
25 | PS5-79-IG-0001-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 6 |  | PS5-79-IV-0001 | - | 63 kVA Transformer |  | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0001 |  | Heat Tracing Panel |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
26 | PS5-79-IG-0002-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 6 |  | PS5-79-IV-0002 | - | 100 kVA Transformer |  | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0002 |  | Heat Tracing Panel |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
27 | PS5-79-IG-0003-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 6 |  | PS5-79-IV-0003 | - | 63 kVA Transformer |  | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0003 |  | Heat Tracing Panel |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
28 | PS5-79-IG-0004-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 6 |  | PS5-79-IV-0004 | - | 63 kVA Transformer |  | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0004 |  | Heat Tracing Panel |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
29 | PS5-79-IG-0005-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 6 |  | PS5-79-IV-0005 | - | 100 kVA Transformer |  | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0005 |  | Heat Tracing Panel |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
30 | PS5-79-IG-0006-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 6 |  | PS5-79-IV-0006 | - | 63 kVA Transformer |  | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0006 |  | Heat Tracing Panel |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
31 | PS5-79-IG-0007-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 6 |  | PS5-79-IV-0007 | - | 100 kVA Transformer |  | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0007 |  | Heat Tracing Panel |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
32 | PS5-79-IG-0008-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 6 |  | PS5-79-IV-0008 | - | 100 kVA Transformer |  | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0008 |  | Heat Tracing Panel |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
33 | PS5-79-IG-0009-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 6 |  | PS5-79-IV-0009 | - | 100 kVA Transformer |  | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0009 |  | Heat Tracing Panel |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
34 | PS5-79-IG-0010-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 6 |  | PS5-79-IV-0010 | - | 100 kVA Transformer |  | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0010 |  | Heat Tracing Panel |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
35 | PS5-79-IG-0011-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 6 |  | PS5-79-IV-0011 | - | 100 kVA Transformer |  | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0011 |  | Heat Tracing Panel |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
36 | PS5-79-IG-0012-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 6 |  | PS5-79-IV-0012 | - | 100 kVA Transformer |  | Outdoor | SIND M20 Gland | M20 | PS5-79-IG-0012 |  | Heat Tracing Panel |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 17 |  | 00 | nVent
37 | PS5-79-BE-0316-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 88 |  | PS5-79-IG-0001 | 1 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0316 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
38 | PS5-79-BE-0315-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 87 |  | PS5-79-IG-0001 | 2 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0315 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
39 | PS5-79-BE-0168-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 84 |  | PS5-79-IG-0001 | 3 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0168 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
40 | PS5-79-BE-0170-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 84 |  | PS5-79-IG-0001 | 4 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0170 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
41 | PS5-79-BE-0163-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 76 |  | PS5-79-IG-0001 | 5 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0163 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
42 | PS5-79-BE-0167-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 84 |  | PS5-79-IG-0001 | 6 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0167 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
43 | PS5-79-SP-0167-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 4 |  | PS5-79-BE-0167 | 6 | Heat Tracing Junction Box |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0167 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01
44 | PS5-79-BE-0169-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 83 |  | PS5-79-IG-0001 | 7 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0169 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
45 | PS5-79-SP-0169-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 4 |  | PS5-79-BE-0169 | 7 | Heat Tracing Junction Box |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0169 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
46 | PS5-79-BE-0159-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 82 |  | PS5-79-IG-0001 | 8 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0159 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
47 | PS5-79-BE-0164-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 82 |  | PS5-79-IG-0001 | 9 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0164 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
48 | PS5-79-BE-0151-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 75 |  | PS5-79-IG-0001 | 10 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0151 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
49 | PS5-79-BE-0356-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 87 |  | PS5-79-IG-0001 | 11 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0356 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
50 | PS5-79-BE-0206-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 71 |  | PS5-79-IG-0001 | 12 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0206 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
51 | PS5-79-BE-0148-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 80 |  | PS5-79-IG-0001 | 13 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0148 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
52 | PS5-79-BE-0314-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 79 |  | PS5-79-IG-0001 | 14 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0314 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
53 | PS5-79-BE-0149-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 79 |  | PS5-79-IG-0001 | 15 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0149 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
54 | PS5-79-BE-0234-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 85 |  | PS5-79-IG-0001 | 16 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0234 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 00 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
55 | PS5-79-BE-0114-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 83 |  | PS5-79-IG-0001 | 17 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0114 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
56 | PS5-79-BE-0165-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 73 |  | PS5-79-IG-0001 | 18 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0165 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
57 | PS5-79-BE-0166-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 83 |  | PS5-79-IG-0001 | 19 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0166 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
58 | PS5-79-BE-0157-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 72 |  | PS5-79-IG-0001 | 20 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0157 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
59 | PS5-79-BE-0153-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 81 |  | PS5-79-IG-0001 | 21 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0153 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
60 | PS5-79-BE-0313-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 81 |  | PS5-79-IG-0001 | 22 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0313 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
61 | PS5-79-BE-0188-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 71 |  | PS5-79-IG-0001 | 23 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0188 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
62 | PS5-79-BE-0202-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 62 |  | PS5-79-IG-0001 | 24 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0202 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
63 | PS5-79-BE-0103-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 52 |  | PS5-79-IG-0001 | 25 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0103 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
64 | PS5-79-BE-0317-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 50 |  | PS5-79-IG-0001 | 26 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0317 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
65 | PS5-79-BE-0306-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 51 |  | PS5-79-IG-0001 | 27 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0306 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
66 | PS5-79-BE-0197-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 52 |  | PS5-79-IG-0001 | 28 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0197 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
67 | PS5-71-BE-0361-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 85 |  | PS5-79-IG-0001 | 31 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-71-BE-0361 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
68 | PS5-79-BE-0181-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 69 |  | PS5-79-IG-0002 | 1 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0181 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
69 | PS5-79-BE-0184-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 69 |  | PS5-79-IG-0002 | 2 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0184 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
70 | PS5-79-BE-0302-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 69 |  | PS5-79-IG-0002 | 3 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0302 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
71 | PS5-79-BE-0185-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 65 |  | PS5-79-IG-0002 | 4 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0185 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
72 | PS5-79-BE-0182-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 63 |  | PS5-79-IG-0002 | 5 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0182 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
73 | PS5-79-BE-0303-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 65 |  | PS5-79-IG-0002 | 6 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0303 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
74 | PS5-79-BE-0304-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 57 |  | PS5-79-IG-0002 | 7 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0304 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
75 | PS5-79-BE-0325-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 74 |  | PS5-79-IG-0002 | 8 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0325 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
76 | PS5-79-BE-0311-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 73 |  | PS5-79-IG-0002 | 9 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0311 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
77 | PS5-79-BE-0312-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 71 |  | PS5-79-IG-0002 | 10 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0312 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
78 | PS5-79-BE-0173-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 62 |  | PS5-79-IG-0002 | 11 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0173 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
79 | PS5-79-BE-0183-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 59 |  | PS5-79-IG-0002 | 12 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0183 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
80 | PS5-79-BE-0355-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 68 |  | PS5-79-IG-0002 | 13 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0355 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
81 | PS5-79-BE-0354-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 69 |  | PS5-79-IG-0002 | 14 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0354 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
82 | PS5-79-BE-0201-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 43 |  | PS5-79-IG-0002 | 15 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0201 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
83 | PS5-79-BE-0193-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 37 |  | PS5-79-IG-0002 | 16 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0193 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
84 | PS5-79-BE-0322-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 38 |  | PS5-79-IG-0002 | 17 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0322 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
85 | PS5-79-BE-0192-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 53 |  | PS5-79-IG-0002 | 18 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0192 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
86 | PS5-79-BE-0191-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 53 |  | PS5-79-IG-0002 | 19 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0191 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
87 | PS5-79-BE-0346-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 52 |  | PS5-79-IG-0002 | 20 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0346 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
88 | PS5-79-BE-0172-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 59 |  | PS5-79-IG-0002 | 21 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0172 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
89 | PS5-79-BE-0179-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 56 |  | PS5-79-IG-0002 | 22 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0179 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
90 | PS5-79-BE-0326-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 75 |  | PS5-79-IG-0002 | 23 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0326 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
91 | PS5-79-BE-0180-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 53 |  | PS5-79-IG-0002 | 24 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0180 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
92 | PS5-79-BE-0174-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 54 |  | PS5-79-IG-0002 | 25 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0174 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
93 | PS5-79-BE-0305-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 53 |  | PS5-79-IG-0002 | 26 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0305 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
94 | PS5-79-BE-0199-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 16 |  | PS5-79-IG-0002 | 27 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0199 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
95 | PS5-79-BE-0187-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 13 |  | PS5-79-IG-0002 | 28 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0187 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
96 | PS5-79-BE-0190-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 12 |  | PS5-79-IG-0002 | 29 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0190 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
97 | PS5-71-BE-0363-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 74 |  | PS5-79-IG-0002 | 31 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-71-BE-0363 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
98 | PS5-79-BE-0023-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 104 |  | PS5-79-IG-0003 | 1 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0023 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
99 | PS5-79-BE-0278-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 108 |  | PS5-79-IG-0003 | 2 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0278 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
100 | PS5-79-BE-0307-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 104 |  | PS5-79-IG-0003 | 3 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0307 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
101 | PS5-79-BE-0198-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 103 |  | PS5-79-IG-0003 | 4 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0198 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
102 | PS5-79-BE-0046-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 103 |  | PS5-79-IG-0003 | 5 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0046 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
103 | PS5-79-BE-0195-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 102 |  | PS5-79-IG-0003 | 6 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0195 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
104 | PS5-79-BE-0252-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 95 |  | PS5-79-IG-0003 | 7 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0252 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
105 | PS5-79-BE-0253-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 95 |  | PS5-79-IG-0003 | 8 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0253 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
106 | PS5-79-BE-0200-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 90 |  | PS5-79-IG-0003 | 9 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0200 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
107 | PS5-79-BE-0194-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 90 |  | PS5-79-IG-0003 | 10 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0194 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
108 | PS5-79-BE-0246-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 89 |  | PS5-79-IG-0003 | 11 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0246 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
109 | PS5-79-BE-0189-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 91 |  | PS5-79-IG-0003 | 12 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0189 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
110 | PS5-79-BE-0210-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 65 |  | PS5-79-IG-0003 | 13 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0210 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
111 | PS5-79-BE-0186-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 87 |  | PS5-79-IG-0003 | 14 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0186 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 00 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
112 | PS5-79-BE-0279-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 99 |  | PS5-79-IG-0003 | 15 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0279 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
113 | PS5-79-BE-0260-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 61 |  | PS5-79-IG-0003 | 16 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0260 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
114 | PS5-79-BE-0211-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 64 |  | PS5-79-IG-0003 | 17 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0211 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
115 | PS5-79-BE-0196-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 76 |  | PS5-79-IG-0003 | 18 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0196 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
116 | PS5-79-BE-0244-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 77 |  | PS5-79-IG-0003 | 19 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0244 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
117 | PS5-79-BE-0238-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 93 |  | PS5-79-IG-0003 | 20 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0238 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 00 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
118 | PS5-79-BE-0348-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 131 |  | PS5-79-IG-0003 | 21 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0348 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
119 | PS5-79-BE-0352-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 142 |  | PS5-79-IG-0003 | 22 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0352 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
120 | PS5-79-BE-0242-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 157 |  | PS5-79-IG-0003 | 23 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0242 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
121 | PS5-79-BE-0109-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 144 |  | PS5-79-IG-0003 | 24 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0109 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
122 | PS5-79-BE-0113-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 145 |  | PS5-79-IG-0003 | 25 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0113 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
123 | PS5-79-BE-0106-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 146 |  | PS5-79-IG-0003 | 26 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0106 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
124 | PS5-79-BE-0351-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 160 |  | PS5-79-IG-0003 | 27 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0351 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
125 | PS5-79-BE-0243-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 141 |  | PS5-79-IG-0003 | 28 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0243 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
126 | PS5-60-BE-0365-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 85 |  | PS5-79-IG-0003 | 31 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0365 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
127 | PS5-79-BE-0280-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 79 |  | PS5-79-IG-0004 | 1 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0280 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
128 | PS5-79-BE-0331-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 75 |  | PS5-79-IG-0004 | 2 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0331 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
129 | PS5-79-BE-0327-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 73 |  | PS5-79-IG-0004 | 3 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0327 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
130 | PS5-79-BE-0266-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 73 |  | PS5-79-IG-0004 | 4 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0266 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
131 | PS5-79-BE-0265-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 72 |  | PS5-79-IG-0004 | 5 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0265 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
132 | PS5-79-BE-0212-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 16 |  | PS5-79-IG-0004 | 6 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0212 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
133 | PS5-79-BE-0049-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 76 |  | PS5-79-IG-0004 | 7 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0049 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
134 | PS5-79-BE-0329-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 67 |  | PS5-79-IG-0004 | 8 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0329 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
135 | PS5-79-BE-0285-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 65 |  | PS5-79-IG-0004 | 9 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0285 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
136 | PS5-79-BE-0220-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 58 |  | PS5-79-IG-0004 | 10 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0220 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
137 | PS5-79-BE-0217-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 65 |  | PS5-79-IG-0004 | 11 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0217 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
138 | PS5-79-BE-0219-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 54 |  | PS5-79-IG-0004 | 12 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0219 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
139 | PS5-79-BE-0237-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 52 |  | PS5-79-IG-0004 | 13 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0237 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
140 | PS5-79-SP-0237-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 4 |  | PS5-79-BE-0237 | 13 | Heat Tracing Junction Box |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0237 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
141 | PS5-79-BE-0282-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 43 |  | PS5-79-IG-0004 | 14 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0282 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
142 | PS5-79-BE-0213-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 34 |  | PS5-79-IG-0004 | 15 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0213 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
143 | PS5-79-BE-0086-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 48 |  | PS5-79-IG-0004 | 16 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0086 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
144 | PS5-79-BE-0214-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 48 |  | PS5-79-IG-0004 | 17 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0214 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 00 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
145 | PS5-79-BE-0283-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 44 |  | PS5-79-IG-0004 | 18 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0283 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
146 | PS5-79-BE-0092-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 68 |  | PS5-79-IG-0004 | 19 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0092 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 00 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
147 | PS5-79-BE-0216-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 67 |  | PS5-79-IG-0004 | 20 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0216 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
148 | PS5-79-BE-0215-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 68 |  | PS5-79-IG-0004 | 21 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0215 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
149 | PS5-79-BE-0099-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 71 |  | PS5-79-IG-0004 | 22 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0099 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
150 | PS5-79-BE-0171-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 74 |  | PS5-79-IG-0004 | 23 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0171 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
151 | PS5-79-BE-0264-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 73 |  | PS5-79-IG-0004 | 24 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0264 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
152 | PS5-79-BE-0281-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 22 |  | PS5-79-IG-0004 | 25 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0281 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
153 | PS5-79-BE-0284-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 24 |  | PS5-79-IG-0004 | 26 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0284 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
154 | PS5-60-BE-0366-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 90 |  | PS5-79-IG-0004 | 28 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0366 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
155 | PS5-79-BE-0332-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 90 |  | PS5-79-IG-0005 | 1 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0332 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
156 | PS5-79-BE-0330-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 87 |  | PS5-79-IG-0005 | 2 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0330 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
157 | PS5-79-BE-0269-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 87 |  | PS5-79-IG-0005 | 3 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0269 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
158 | PS5-79-BE-0267-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 88 |  | PS5-79-IG-0005 | 4 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0267 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
159 | PS5-79-BE-0268-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 87 |  | PS5-79-IG-0005 | 5 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0268 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
160 | PS5-79-BE-0334-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 81 |  | PS5-79-IG-0005 | 6 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0334 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
161 | PS5-79-BE-0333-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 78 |  | PS5-79-IG-0005 | 7 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0333 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
162 | PS5-79-BE-0272-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 78 |  | PS5-79-IG-0005 | 8 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0272 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
163 | PS5-79-BE-0270-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 78 |  | PS5-79-IG-0005 | 9 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0270 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
164 | PS5-79-BE-0271-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 77 |  | PS5-79-IG-0005 | 10 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0271 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
165 | PS5-79-BE-0335-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 85 |  | PS5-79-IG-0005 | 11 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0335 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
166 | PS5-79-BE-0339-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 88 |  | PS5-79-IG-0005 | 12 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0339 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
167 | PS5-79-BE-0275-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 85 |  | PS5-79-IG-0005 | 13 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0275 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
168 | PS5-79-BE-0273-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 83 |  | PS5-79-IG-0005 | 14 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0273 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
169 | PS5-79-BE-0274-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 83 |  | PS5-79-IG-0005 | 15 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0274 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
170 | PS5-79-BE-0328-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 76 |  | PS5-79-IG-0005 | 16 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0328 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
171 | PS5-79-BE-0061-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 73 |  | PS5-79-IG-0005 | 17 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0061 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
172 | PS5-79-BE-0218-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 65 |  | PS5-79-IG-0005 | 18 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0218 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
173 | PS5-79-BE-0229-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 81 |  | PS5-79-IG-0005 | 19 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0229 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
174 | PS5-79-BE-0223-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 61 |  | PS5-79-IG-0005 | 20 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0223 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
175 | PS5-79-BE-0224-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 64 |  | PS5-79-IG-0005 | 21 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0224 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
176 | PS5-79-BE-0221-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 72 |  | PS5-79-IG-0005 | 22 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0221 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
177 | PS5-79-BE-0235-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 69 |  | PS5-79-IG-0005 | 23 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0235 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
178 | PS5-79-BE-0222-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 68 |  | PS5-79-IG-0005 | 24 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0222 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
179 | PS5-79-BE-0350-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 71 |  | PS5-79-IG-0005 | 25 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0350 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
180 | PS5-79-BE-0228-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 77 |  | PS5-79-IG-0005 | 26 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0228 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
181 | PS5-79-BE-0236-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 60 |  | PS5-79-IG-0005 | 27 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0236 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
182 | PS5-60-BE-0367-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 86 |  | PS5-79-IG-0005 | 28 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0367 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
183 | PS5-79-BE-0136-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 111 |  | PS5-79-IG-0009 | 1 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0136 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
184 | PS5-79-BE-0027-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 109 |  | PS5-79-IG-0009 | 2 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0027 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
185 | PS5-79-BE-0039-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 87 |  | PS5-79-IG-0009 | 3 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0039 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
186 | PS5-79-BE-0037-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 82 |  | PS5-79-IG-0009 | 4 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0037 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
187 | PS5-79-BE-0025-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 91 |  | PS5-79-IG-0009 | 5 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0025 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
188 | PS5-79-BE-0343-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 109 |  | PS5-79-IG-0009 | 6 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0343 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
189 | PS5-79-BE-0118-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 96 |  | PS5-79-IG-0009 | 7 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0118 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
190 | PS5-79-BE-0137-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 89 |  | PS5-79-IG-0009 | 8 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0137 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
191 | PS5-79-BE-0024-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 87 |  | PS5-79-IG-0009 | 9 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0024 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
192 | PS5-79-BE-0150-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 99 |  | PS5-79-IG-0009 | 10 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0150 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
193 | PS5-79-BE-0203-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 72 |  | PS5-79-IG-0009 | 11 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0203 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
194 | PS5-79-BE-0204-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 70 |  | PS5-79-IG-0009 | 12 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0204 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
195 | PS5-79-BE-0262-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 74 |  | PS5-79-IG-0009 | 13 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0262 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
196 | PS5-79-BE-0102-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 75 |  | PS5-79-IG-0009 | 14 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0102 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
197 | PS5-79-BE-0081-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 85 |  | PS5-79-IG-0009 | 15 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0081 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
198 | PS5-79-BE-0036-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 85 |  | PS5-79-IG-0009 | 16 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0036 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
199 | PS5-79-BE-0066-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 73 |  | PS5-79-IG-0009 | 17 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0066 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
200 | PS5-79-BE-0067-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 82 |  | PS5-79-IG-0009 | 18 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0067 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
201 | PS5-79-BE-0245-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 86 |  | PS5-79-IG-0009 | 19 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0245 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
202 | PS5-79-BE-0134-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 92 |  | PS5-79-IG-0009 | 20 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0134 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
203 | PS5-79-BE-0063-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 91 |  | PS5-79-IG-0009 | 21 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0063 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
204 | PS5-79-BE-0154-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 98 |  | PS5-79-IG-0009 | 22 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0154 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
205 | PS5-79-BE-0319-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 77 |  | PS5-79-IG-0009 | 23 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0319 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
206 | PS5-79-BE-0290-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 101 |  | PS5-79-IG-0009 | 24 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0290 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
207 | PS5-79-BE-0152-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 100 |  | PS5-79-IG-0009 | 25 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0152 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
208 | PS5-79-BE-0002-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 83 |  | PS5-79-IG-0009 | 26 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0002 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
209 | PS5-79-BE-0005-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 102 |  | PS5-79-IG-0009 | 27 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0005 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
210 | PS5-79-BE-0146-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 84 |  | PS5-79-IG-0009 | 28 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0146 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
211 | PS5-79-BE-0041-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 86 |  | PS5-79-IG-0009 | 29 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0041 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
212 | PS5-79-BE-0135-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 102 |  | PS5-79-IG-0009 | 30 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0135 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
213 | PS5-79-BE-0239-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 104 |  | PS5-79-IG-0009 | 31 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0239 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
214 | PS5-79-IP-9901-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 107 |  | PS5-79-IG-0009 | 40 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9901 |  | Marshalling Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
215 | PS5-79-IP-9101-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 2 |  | PS5-79-IP-9901 | 40 | Marshalling Box |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9101 |  | ETS-05 |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
216 | PS5-79-IP-9102-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 2 |  | PS5-79-IP-9901 | 40 | Marshalling Box |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9102 |  | ETS-05 |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
217 | PS5-79-BE-0247-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 62 |  | PS5-79-IG-0007 | 1 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0247 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
218 | PS5-79-BE-0084-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 63 |  | PS5-79-IG-0007 | 2 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0084 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 00 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
219 | PS5-79-BE-0090-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 59 |  | PS5-79-IG-0007 | 3 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0090 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
220 | PS5-79-BE-0085-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 102 |  | PS5-79-IG-0007 | 4 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0085 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
221 | PS5-79-BE-0082-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 85 |  | PS5-79-IG-0007 | 5 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0082 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
222 | PS5-79-BE-0101-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 67 |  | PS5-79-IG-0007 | 6 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0101 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
223 | PS5-79-BE-0156-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 73 |  | PS5-79-IG-0007 | 7 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0156 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
224 | PS5-79-BE-0107-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 61 |  | PS5-79-IG-0007 | 8 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0107 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
225 | PS5-79-BE-0020-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 60 |  | PS5-79-IG-0007 | 9 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0020 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
226 | PS5-79-BE-0147-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 62 |  | PS5-79-IG-0007 | 10 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0147 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
227 | PS5-79-BE-0043-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 61 |  | PS5-79-IG-0007 | 11 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0043 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
228 | PS5-79-BE-0344-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 60 |  | PS5-79-IG-0007 | 12 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0344 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
229 | PS5-79-BE-0019-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 56 |  | PS5-79-IG-0007 | 13 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0019 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
230 | PS5-79-BE-0100-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 52 |  | PS5-79-IG-0007 | 14 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0100 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
231 | PS5-79-BE-0112-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 59 |  | PS5-79-IG-0007 | 15 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0112 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=3 C=0 | 00 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
232 | PS5-79-BE-0068-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 74 |  | PS5-79-IG-0007 | 16 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0068 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=3 C=0 | 01 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
233 | PS5-79-BE-0042-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 73 |  | PS5-79-IG-0007 | 17 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0042 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=3 C=0 | 01 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
234 | PS5-79-BE-0121-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 65 |  | PS5-79-IG-0007 | 18 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0121 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=3 C=0 | 01 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
235 | PS5-79-BE-0072-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 71 |  | PS5-79-IG-0007 | 19 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0072 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
236 | PS5-79-BE-0116-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 65 |  | PS5-79-IG-0007 | 20 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0116 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=3 C=0 | 01 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
237 | PS5-79-BE-0145-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 87 |  | PS5-79-IG-0007 | 21 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0145 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
238 | PS5-79-BE-0155-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 93 |  | PS5-79-IG-0007 | 22 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0155 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=3 C=0 | 00 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
239 | PS5-79-BE-0071-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 86 |  | PS5-79-IG-0007 | 23 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0071 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
240 | PS5-79-BE-0083-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 66 |  | PS5-79-IG-0007 | 24 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0083 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=3 C=0 | 01 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
241 | PS5-79-BE-0291-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 74 |  | PS5-79-IG-0007 | 25 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0291 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=3 C=0 | 00 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
242 | PS5-79-BE-0003-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 73 |  | PS5-79-IG-0007 | 26 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0003 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=3 C=0 | 01 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
243 | PS5-79-BE-0143-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 74 |  | PS5-79-IG-0007 | 27 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0143 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=3 C=0 | 00 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
244 | PS5-79-BE-0059-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 76 |  | PS5-79-IG-0007 | 28 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0059 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=3 C=0 | 01 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
245 | PS5-79-BE-0006-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 96 |  | PS5-79-IG-0007 | 29 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0006 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=3 C=0 | 01 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
246 | PS5-79-BE-0144-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 99 |  | PS5-79-IG-0007 | 30 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0144 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
247 | PS5-79-BE-0240-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 101 |  | PS5-79-IG-0007 | 31 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0240 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=3 C=0 | 01 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
248 | PS5-79-IP-9902-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 100 |  | PS5-79-IG-0007 | 40 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9902 |  | Marshalling Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
249 | PS5-79-IP-9103-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 2 |  | PS5-79-IP-9902 | 40 | Marshalling Box |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9103 |  | ETS-05 |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
250 | PS5-79-IP-9104-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 2 |  | PS5-79-IP-9902 | 40 | Marshalling Box |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9104 |  | ETS-05 |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
251 | PS5-79-BE-0241-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 87 |  | PS5-79-IG-0008 | 1 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0241 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=3 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
252 | PS5-79-BE-0208-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 60 |  | PS5-79-IG-0008 | 2 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0208 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
253 | PS5-79-BE-0292-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 73 |  | PS5-79-IG-0008 | 3 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0292 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=3 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
254 | PS5-79-BE-0058-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 77 |  | PS5-79-IG-0008 | 4 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0058 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
255 | PS5-79-BE-0140-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 75 |  | PS5-79-IG-0008 | 5 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0140 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=3 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
256 | PS5-79-BE-0004-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 73 |  | PS5-79-IG-0008 | 6 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0004 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=3 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
257 | PS5-79-BE-0007-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 92 |  | PS5-79-IG-0008 | 7 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0007 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=3 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
258 | PS5-79-BE-0161-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 72 |  | PS5-79-IG-0008 | 8 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0161 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
259 | PS5-79-BE-0139-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 69 |  | PS5-79-IG-0008 | 9 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0139 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=3 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
260 | PS5-79-BE-0162-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 73 |  | PS5-79-IG-0008 | 10 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0162 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
261 | PS5-79-BE-0074-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 75 |  | PS5-79-IG-0008 | 11 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0074 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
262 | PS5-79-BE-0142-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 76 |  | PS5-79-IG-0008 | 12 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0142 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=3 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
263 | PS5-79-BE-0160-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 73 |  | PS5-79-IG-0008 | 13 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0160 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
264 | PS5-79-BE-0077-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 68 |  | PS5-79-IG-0008 | 14 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0077 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
265 | PS5-79-BE-0075-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 61 |  | PS5-79-IG-0008 | 15 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0075 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
266 | PS5-79-BE-0053-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 55 |  | PS5-79-IG-0008 | 16 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0053 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
267 | PS5-79-BE-0076-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 57 |  | PS5-79-IG-0008 | 17 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0076 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
268 | PS5-79-BE-0070-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 69 |  | PS5-79-IG-0008 | 18 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0070 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
269 | PS5-79-BE-0158-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 67 |  | PS5-79-IG-0008 | 19 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0158 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
270 | PS5-79-BE-0060-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 63 |  | PS5-79-IG-0008 | 20 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0060 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
271 | PS5-79-BE-0115-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 70 |  | PS5-79-IG-0008 | 21 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0115 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
272 | PS5-79-BE-0108-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 69 |  | PS5-79-IG-0008 | 22 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0108 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 00 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
273 | PS5-79-BE-0111-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 70 |  | PS5-79-IG-0008 | 23 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0111 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
274 | PS5-79-BE-0062-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 60 |  | PS5-79-IG-0008 | 24 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0062 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
275 | PS5-79-BE-0141-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 89 |  | PS5-79-IG-0008 | 25 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0141 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=3 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
276 | PS5-79-BE-0207-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 61 |  | PS5-79-IG-0008 | 26 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0207 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
277 | PS5-79-BE-0205-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 54 |  | PS5-79-IG-0008 | 27 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0205 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
278 | PS5-79-BE-0044-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 59 |  | PS5-79-IG-0008 | 28 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0044 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
279 | PS5-79-BE-0045-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 51 |  | PS5-79-IG-0008 | 29 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0045 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
280 | PS5-79-BE-0261-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 45 |  | PS5-79-IG-0008 | 30 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0261 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
281 | PS5-79-BE-0209-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 37 |  | PS5-79-IG-0008 | 31 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0209 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
282 | PS5-79-IP-9903-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 90 |  | PS5-79-IG-0008 | 40 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9903 |  | Marshalling Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
283 | PS5-79-IP-9105-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 2 |  | PS5-79-IP-9903 | 40 | Marshalling Box |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9105 |  | ETS-05 |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
284 | PS5-79-IP-9106-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 2 |  | PS5-79-IP-9903 | 40 | Marshalling Box |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-IP-9106 |  | ETS-05 |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Export Pump (Power) | 01 | nVent
285 | PS5-79-BE-0064-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 127 |  | PS5-79-IG-0006 | 1 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0064 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
286 | PS5-79-BE-0057-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 129 |  | PS5-79-IG-0006 | 2 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0057 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
287 | PS5-79-BE-0021-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 119 |  | PS5-79-IG-0006 | 3 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0021 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
288 | PS5-79-BE-0128-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 128 |  | PS5-79-IG-0006 | 4 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0128 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
289 | PS5-79-BE-0008-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 123 |  | PS5-79-IG-0006 | 5 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0008 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
290 | PS5-79-SP-0008-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 4 |  | PS5-79-BE-0008 | 5 | Heat Tracing Junction Box |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0008 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
291 | PS5-79-BE-0047-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 113 |  | PS5-79-IG-0006 | 6 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0047 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
292 | PS5-79-BE-0052-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 127 |  | PS5-79-IG-0006 | 7 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0052 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
293 | PS5-79-BE-0056-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 129 |  | PS5-79-IG-0006 | 8 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0056 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
294 | PS5-79-BE-0055-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 130 |  | PS5-79-IG-0006 | 9 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0055 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
295 | PS5-79-BE-0028-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 111 |  | PS5-79-IG-0006 | 10 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0028 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
296 | PS5-79-BE-0294-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 124 |  | PS5-79-IG-0006 | 11 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0294 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
297 | PS5-79-BE-0293-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 125 |  | PS5-79-IG-0006 | 12 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0293 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
298 | PS5-79-BE-0129-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 124 |  | PS5-79-IG-0006 | 13 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0129 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
299 | PS5-79-BE-0073-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 117 |  | PS5-79-IG-0006 | 14 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0073 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
300 | PS5-79-BE-0010-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 117 |  | PS5-79-IG-0006 | 15 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0010 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
301 | PS5-79-SP-0010-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 4 |  | PS5-79-BE-0010 | 15 | Heat Tracing Junction Box |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0010 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
302 | PS5-79-BE-0124-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 126 |  | PS5-79-IG-0006 | 16 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0124 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
303 | PS5-79-BE-0295-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 119 |  | PS5-79-IG-0006 | 17 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0295 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
304 | PS5-79-BE-0030-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 111 |  | PS5-79-IG-0006 | 18 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0030 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
305 | PS5-79-BE-0127-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 118 |  | PS5-79-IG-0006 | 19 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0127 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
306 | PS5-79-BE-0051-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 113 |  | PS5-79-IG-0006 | 20 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0051 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
307 | PS5-79-BE-0032-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 113 |  | PS5-79-IG-0006 | 21 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0032 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
308 | PS5-79-BE-0033-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 112 |  | PS5-79-IG-0006 | 22 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0033 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
309 | PS5-79-BE-0126-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 126 |  | PS5-79-IG-0006 | 23 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0126 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
310 | PS5-79-BE-0125-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 128 |  | PS5-79-IG-0006 | 24 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0125 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
311 | PS5-79-BE-0011-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 137 |  | PS5-79-IG-0006 | 25 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0011 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
312 | PS5-79-BE-0301-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 118 |  | PS5-79-IG-0006 | 26 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0301 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
313 | PS5-79-BE-0001-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 127 |  | PS5-79-IG-0006 | 27 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0001 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
314 | PS5-79-BE-0009-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 121 |  | PS5-79-IG-0006 | 28 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0009 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
315 | PS5-79-BE-0014-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 122 |  | PS5-79-IG-0006 | 29 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0014 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
316 | PS5-79-BE-0034-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 110 |  | PS5-79-IG-0006 | 30 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0034 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
317 | PS5-79-BE-0353-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 116 |  | PS5-79-IG-0006 | 31 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0353 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
318 | PS5-71-BE-0362-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 96 |  | PS5-79-IG-0006 | 34 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-71-BE-0362 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
319 | PS5-79-BE-0132-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 129 |  | PS5-79-IG-0010 | 1 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0132 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
320 | PS5-79-BE-0131-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 123 |  | PS5-79-IG-0010 | 2 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0131 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
321 | PS5-79-BE-0040-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 115 |  | PS5-79-IG-0010 | 3 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0040 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
322 | PS5-79-BE-0233-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 117 |  | PS5-79-IG-0010 | 4 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0233 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
323 | PS5-79-BE-0054-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 119 |  | PS5-79-IG-0010 | 5 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0054 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
324 | PS5-79-BE-0022-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 120 |  | PS5-79-IG-0010 | 6 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0022 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
325 | PS5-79-BE-0078-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 115 |  | PS5-79-IG-0010 | 7 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0078 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
326 | PS5-79-BE-0105-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 112 |  | PS5-79-IG-0010 | 8 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0105 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
327 | PS5-79-BE-0029-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 112 |  | PS5-79-IG-0010 | 9 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0029 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
328 | PS5-79-BE-0035-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 103 |  | PS5-79-IG-0010 | 10 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0035 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
329 | PS5-79-BE-0094-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 117 |  | PS5-79-IG-0010 | 11 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0094 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
330 | PS5-79-BE-0120-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 102 |  | PS5-79-IG-0010 | 12 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0120 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
331 | PS5-79-BE-0095-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 105 |  | PS5-79-IG-0010 | 13 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0095 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 01 | nVent
332 | PS5-79-BE-0087-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 99 |  | PS5-79-IG-0010 | 14 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0087 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
333 | PS5-79-BE-0119-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 101 |  | PS5-79-IG-0010 | 15 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0119 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
334 | PS5-79-BE-0117-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 118 |  | PS5-79-IG-0010 | 16 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0117 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
335 | PS5-79-BE-0323-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 103 |  | PS5-79-IG-0010 | 17 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0323 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
336 | PS5-79-BE-0096-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 73 |  | PS5-79-IG-0010 | 18 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0096 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
337 | PS5-79-BE-0079-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 98 |  | PS5-79-IG-0010 | 19 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0079 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
338 | PS5-79-BE-0345-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 96 |  | PS5-79-IG-0010 | 20 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0345 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
339 | PS5-79-BE-0104-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10 | 93 |  | PS5-79-IG-0010 | 21 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0104 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 23 |  | 00 | nVent
340 | PS5-79-BE-0230-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 83 |  | PS5-79-IG-0010 | 22 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0230 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
341 | PS5-79-BE-0093-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 80 |  | PS5-79-IG-0010 | 23 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0093 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
342 | PS5-79-BE-0088-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 81 |  | PS5-79-IG-0010 | 24 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0088 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
343 | PS5-79-BE-0089-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 81 |  | PS5-79-IG-0010 | 25 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0089 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
344 | PS5-79-BE-0091-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 71 |  | PS5-79-IG-0010 | 26 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0091 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
345 | PS5-79-BE-0097-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 66 |  | PS5-79-IG-0010 | 27 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0097 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
346 | PS5-79-BE-0321-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 101 |  | PS5-79-IG-0010 | 28 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0321 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
347 | PS5-79-BE-0227-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 70 |  | PS5-79-IG-0010 | 29 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0227 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
348 | PS5-60-BE-0364-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 156 |  | PS5-79-IG-0010 | 31 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0364 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
349 | PS5-79-BE-0286-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 55 |  | PS5-79-IG-0011 | 1 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0286 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
350 | PS5-79-BE-0347-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 55 |  | PS5-79-IG-0011 | 2 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0347 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
351 | PS5-79-BE-0289-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 56 |  | PS5-79-IG-0011 | 3 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0289 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
352 | PS5-79-BE-0342-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 64 |  | PS5-79-IG-0011 | 4 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0342 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
353 | PS5-79-BE-0232-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 48 |  | PS5-79-IG-0011 | 5 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0232 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
354 | PS5-79-BE-0231-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 43 |  | PS5-79-IG-0011 | 6 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0231 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
355 | PS5-79-BE-0288-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 65 |  | PS5-79-IG-0011 | 7 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0288 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
356 | PS5-79-BE-0225-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 40 |  | PS5-79-IG-0011 | 8 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0225 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
357 | PS5-79-BE-0324-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 60 |  | PS5-79-IG-0011 | 9 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0324 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
358 | PS5-79-BE-0080-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 51 |  | PS5-79-IG-0011 | 10 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0080 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
359 | PS5-79-BE-0065-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 53 |  | PS5-79-IG-0011 | 11 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0065 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
360 | PS5-79-BE-0287-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 62 |  | PS5-79-IG-0011 | 12 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0287 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
361 | PS5-79-BE-0277-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 64 |  | PS5-79-IG-0011 | 13 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0277 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
362 | PS5-79-BE-0276-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 65 |  | PS5-79-IG-0011 | 14 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0276 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
363 | PS5-79-BE-0226-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 37 |  | PS5-79-IG-0011 | 15 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0226 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
364 | PS5-79-BE-0340-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 65 |  | PS5-79-IG-0011 | 16 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0340 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
365 | PS5-79-BE-0336-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 70 |  | PS5-79-IG-0011 | 17 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0336 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
366 | PS5-79-BE-0031-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 55 |  | PS5-79-IG-0011 | 18 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0031 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
367 | PS5-79-BE-0016-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 56 |  | PS5-79-IG-0011 | 19 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0016 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
368 | PS5-79-BE-0038-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 56 |  | PS5-79-IG-0011 | 20 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0038 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
369 | PS5-79-BE-0341-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 57 |  | PS5-79-IG-0011 | 21 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0341 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
370 | PS5-79-BE-0337-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 60 |  | PS5-79-IG-0011 | 22 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0337 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
371 | PS5-79-BE-0050-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 61 |  | PS5-79-IG-0011 | 23 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0050 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
372 | PS5-79-BE-0048-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 62 |  | PS5-79-IG-0011 | 24 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0048 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
373 | PS5-79-BE-0069-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 63 |  | PS5-79-IG-0011 | 25 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0069 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
374 | PS5-79-BE-0349-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 56 |  | PS5-79-IG-0011 | 26 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0349 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 00 | nVent
375 | PS5-79-BE-0338-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 64 |  | PS5-79-IG-0011 | 27 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0338 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
376 | PS5-60-BE-0368-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 69 |  | PS5-79-IG-0011 | 28 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0368 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
377 | PS5-60-BE-0369-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 59 |  | PS5-79-IG-0011 | 29 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0369 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
378 | PS5-60-BE-0370-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 64 |  | PS5-79-IG-0011 | 30 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-60-BE-0370 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | Sampling (Power) | 01 | nVent
379 | PS5-79-BE-0251-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 40 |  | PS5-79-IG-0012 | 1 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0251 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
380 | PS5-79-BE-0297-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 41 |  | PS5-79-IG-0012 | 2 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0297 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
381 | PS5-79-BE-0296-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 40 |  | PS5-79-IG-0012 | 3 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0296 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
382 | PS5-79-BE-0012-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 32 |  | PS5-79-IG-0012 | 4 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0012 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
383 | PS5-79-BE-0259-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 38 |  | PS5-79-IG-0012 | 5 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0259 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
384 | PS5-79-BE-0257-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 42 |  | PS5-79-IG-0012 | 6 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0257 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
385 | PS5-79-BE-0258-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 63 |  | PS5-79-IG-0012 | 7 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0258 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
386 | PS5-79-BE-0098-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 65 |  | PS5-79-IG-0012 | 8 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0098 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
387 | PS5-79-BE-0300-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 65 |  | PS5-79-IG-0012 | 9 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0300 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
388 | PS5-79-BE-0123-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 63 |  | PS5-79-IG-0012 | 10 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0123 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
389 | PS5-79-BE-0248-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 85 |  | PS5-79-IG-0012 | 11 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0248 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
390 | PS5-79-BE-0254-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 53 |  | PS5-79-IG-0012 | 12 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0254 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
391 | PS5-79-BE-0310-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 57 |  | PS5-79-IG-0012 | 13 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0310 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
392 | PS5-79-BE-0263-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 54 |  | PS5-79-IG-0012 | 14 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0263 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
393 | PS5-79-BE-0122-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 53 |  | PS5-79-IG-0012 | 15 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0122 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
394 | PS5-79-BE-0110-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 52 |  | PS5-79-IG-0012 | 16 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0110 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 00 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
395 | PS5-79-BE-0256-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 51 |  | PS5-79-IG-0012 | 17 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0256 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
396 | PS5-79-BE-0320-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 53 |  | PS5-79-IG-0012 | 18 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0320 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
397 | PS5-79-BE-0255-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 55 |  | PS5-79-IG-0012 | 19 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0255 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
398 | PS5-79-BE-0017-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 56 |  | PS5-79-IG-0012 | 20 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0017 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 00 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
399 | PS5-79-BE-0250-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 57 |  | PS5-79-IG-0012 | 21 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0250 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
400 | PS5-79-BE-0249-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 58 |  | PS5-79-IG-0012 | 22 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0249 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
401 | PS5-79-BE-0318-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 59 |  | PS5-79-IG-0012 | 23 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0318 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
402 | PS5-79-BE-0309-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 80 |  | PS5-79-IG-0012 | 24 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0309 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
403 | PS5-79-BE-0018-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 81 |  | PS5-79-IG-0012 | 25 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0018 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
404 | PS5-79-SP-0018-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 4 |  | PS5-79-BE-0018 | 25 | Heat Tracing Junction Box |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0018 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
405 | PS5-79-BE-0130-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 88 |  | PS5-79-IG-0012 | 26 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0130 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
406 | PS5-79-BE-0299-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 53 |  | PS5-79-IG-0012 | 27 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0299 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
407 | PS5-79-BE-0308-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 85 |  | PS5-79-IG-0012 | 28 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0308 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
408 | PS5-79-BE-0013-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 42 |  | PS5-79-IG-0012 | 29 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0013 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=2 B=2 C=0 | 00 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
409 | PS5-79-BE-0015-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 44 |  | PS5-79-IG-0012 | 30 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0015 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
410 | PS5-79-BE-0133-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 40 |  | PS5-79-IG-0012 | 31 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0133 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
411 | PS5-79-SP-0133-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 4 |  | PS5-79-BE-0133 | 31 | Heat Tracing Junction Box |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-SP-0133 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 |  | 01 | nVent
412 | PS5-79-BE-0298-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 43 |  | PS5-79-IG-0012 | 32 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0298 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 00 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
413 | PS5-79-BE-0026-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 42 |  | PS5-79-IG-0012 | 33 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0026 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
414 | PS5-79-BE-0138-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 24 |  | PS5-79-IG-0012 | 34 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-79-BE-0138 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=1 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
415 | PS5-25-BE-0364-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6 | 148 |  | PS5-79-IG-0012 | 37 | Heat Tracing Panel |  | Outdoor | GL38-M25-METAL | M25 | PS5-25-BE-0364 |  | Heat Tracing Junction Box |  | Field | GL38-M25-METAL | M25 |  | TZ-MID-68-NVS1-150359 | 20 | A=0 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
416 | PS5-79-TE-0316-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 88 |  | PS5-79-IG-0001 | 1 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0316 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
417 | PS5-79-TE-0315-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 87 |  | PS5-79-IG-0001 | 2 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0315 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
418 | PS5-79-TE-0168-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 83 |  | PS5-79-IG-0001 | 3 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0168 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
419 | PS5-79-TE-0170-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 83 |  | PS5-79-IG-0001 | 4 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0170 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
420 | PS5-79-TE-0163-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 76 |  | PS5-79-IG-0001 | 5 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0163 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
421 | PS5-79-TE-0167-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 83 |  | PS5-79-IG-0001 | 6 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0167 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
422 | PS5-79-TE-0169-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 83 |  | PS5-79-IG-0001 | 7 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0169 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
423 | PS5-79-TE-0159-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 82 |  | PS5-79-IG-0001 | 8 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0159 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
424 | PS5-79-TE-0164-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 74 |  | PS5-79-IG-0001 | 9 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0164 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
425 | PS5-79-TE-0151-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 75 |  | PS5-79-IG-0001 | 10 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0151 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
426 | PS5-79-TE-0356-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 86 |  | PS5-79-IG-0001 | 11 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0356 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 00 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
427 | PS5-79-TE-0206-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 70 |  | PS5-79-IG-0001 | 12 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0206 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
428 | PS5-79-TE-0148-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 79 |  | PS5-79-IG-0001 | 13 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0148 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
429 | PS5-79-TE-0314-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 79 |  | PS5-79-IG-0001 | 14 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0314 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
430 | PS5-79-TE-0149-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 78 |  | PS5-79-IG-0001 | 15 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0149 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
431 | PS5-79-TE-0234-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 84 |  | PS5-79-IG-0001 | 16 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0234 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
432 | PS5-79-TE-0114-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 82 |  | PS5-79-IG-0001 | 17 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0114 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
433 | PS5-79-TE-0165-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 73 |  | PS5-79-IG-0001 | 18 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0165 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
434 | PS5-79-TE-0166-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 82 |  | PS5-79-IG-0001 | 19 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0166 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
435 | PS5-79-TE-0157-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 72 |  | PS5-79-IG-0001 | 20 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0157 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
436 | PS5-79-TE-0153-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 71 |  | PS5-79-IG-0001 | 21 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0153 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
437 | PS5-79-TE-0313-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 80 |  | PS5-79-IG-0001 | 22 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0313 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
438 | PS5-79-TE-0188-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 70 |  | PS5-79-IG-0001 | 23 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0188 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
439 | PS5-79-TE-0202-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 61 |  | PS5-79-IG-0001 | 24 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0202 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
440 | PS5-79-TE-0103-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 51 |  | PS5-79-IG-0001 | 25 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0103 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
441 | PS5-79-TE-0317-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 49 |  | PS5-79-IG-0001 | 26 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0317 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 00 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
442 | PS5-79-TE-0306-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 51 |  | PS5-79-IG-0001 | 27 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0306 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
443 | PS5-79-TE-0197-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 51 |  | PS5-79-IG-0001 | 28 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0197 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 00 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
444 | PS5-71-TE-0361-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 84 |  | PS5-79-IG-0001 | 31 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-71-TE-0361 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
445 | PS5-79-TE-0181-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 68 |  | PS5-79-IG-0002 | 1 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0181 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
446 | PS5-79-TE-0184-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 69 |  | PS5-79-IG-0002 | 2 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0184 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
447 | PS5-79-TE-0302-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 68 |  | PS5-79-IG-0002 | 3 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0302 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
448 | PS5-79-TE-0185-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 65 |  | PS5-79-IG-0002 | 4 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0185 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
449 | PS5-79-TE-0182-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 63 |  | PS5-79-IG-0002 | 5 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0182 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
450 | PS5-79-TE-0303-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 65 |  | PS5-79-IG-0002 | 6 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0303 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
451 | PS5-79-TE-0304-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 56 |  | PS5-79-IG-0002 | 7 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0304 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
452 | PS5-79-TE-0325-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 74 |  | PS5-79-IG-0002 | 8 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0325 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
453 | PS5-79-TE-0311-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 72 |  | PS5-79-IG-0002 | 9 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0311 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
454 | PS5-79-TE-0312-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 71 |  | PS5-79-IG-0002 | 10 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0312 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
455 | PS5-79-TE-0173-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 62 |  | PS5-79-IG-0002 | 11 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0173 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
456 | PS5-79-TE-0183-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 58 |  | PS5-79-IG-0002 | 12 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0183 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
457 | PS5-79-TE-0355-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 68 |  | PS5-79-IG-0002 | 13 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0355 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
458 | PS5-79-TE-0354-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 68 |  | PS5-79-IG-0002 | 14 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0354 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
459 | PS5-79-TE-0201-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 70 |  | PS5-79-IG-0002 | 15 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0201 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
460 | PS5-79-TE-0193-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 37 |  | PS5-79-IG-0002 | 16 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0193 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
461 | PS5-79-TE-0322-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 38 |  | PS5-79-IG-0002 | 17 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0322 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
462 | PS5-79-TE-0192-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 52 |  | PS5-79-IG-0002 | 18 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0192 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
463 | PS5-79-TE-0191-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 53 |  | PS5-79-IG-0002 | 19 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0191 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
464 | PS5-79-TE-0346-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 52 |  | PS5-79-IG-0002 | 20 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0346 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
465 | PS5-79-TE-0172-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 58 |  | PS5-79-IG-0002 | 21 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0172 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
466 | PS5-79-TE-0179-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 56 |  | PS5-79-IG-0002 | 22 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0179 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
467 | PS5-79-TE-0326-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 74 |  | PS5-79-IG-0002 | 23 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0326 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
468 | PS5-79-TE-0180-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 53 |  | PS5-79-IG-0002 | 24 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0180 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
469 | PS5-79-TE-0174-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 53 |  | PS5-79-IG-0002 | 25 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0174 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
470 | PS5-79-TE-0305-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 52 |  | PS5-79-IG-0002 | 26 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0305 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
471 | PS5-79-TE-0199-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 15 |  | PS5-79-IG-0002 | 27 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0199 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
472 | PS5-79-TE-0187-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 13 |  | PS5-79-IG-0002 | 28 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0187 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
473 | PS5-79-TE-0190-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 12 |  | PS5-79-IG-0002 | 29 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0190 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
474 | PS5-71-TE-0363-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 74 |  | PS5-79-IG-0002 | 31 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-71-TE-0363 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
475 | PS5-79-TE-0023-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 104 |  | PS5-79-IG-0003 | 1 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0023 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
476 | PS5-79-TE-0278-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 107 |  | PS5-79-IG-0003 | 2 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0278 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
477 | PS5-79-TE-0307-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 104 |  | PS5-79-IG-0003 | 3 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0307 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
478 | PS5-79-TE-0198-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 103 |  | PS5-79-IG-0003 | 4 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0198 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
479 | PS5-79-TE-0046-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 103 |  | PS5-79-IG-0003 | 5 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0046 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
480 | PS5-79-TE-0195-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 102 |  | PS5-79-IG-0003 | 6 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0195 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
481 | PS5-79-TE-0252-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 95 |  | PS5-79-IG-0003 | 7 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0252 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
482 | PS5-79-TE-0253-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 95 |  | PS5-79-IG-0003 | 8 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0253 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
483 | PS5-79-TE-0200-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 90 |  | PS5-79-IG-0003 | 9 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0200 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
484 | PS5-79-TE-0194-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 90 |  | PS5-79-IG-0003 | 10 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0194 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
485 | PS5-79-TE-0246-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 90 |  | PS5-79-IG-0003 | 11 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0246 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
486 | PS5-79-TE-0189-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 91 |  | PS5-79-IG-0003 | 12 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0189 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
487 | PS5-79-TE-0210-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 66 |  | PS5-79-IG-0003 | 13 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0210 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
488 | PS5-79-TE-0186-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 91 |  | PS5-79-IG-0003 | 14 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0186 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
489 | PS5-79-TE-0279-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 99 |  | PS5-79-IG-0003 | 15 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0279 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
490 | PS5-79-TE-0260-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 62 |  | PS5-79-IG-0003 | 16 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0260 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
491 | PS5-79-TE-0211-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 64 |  | PS5-79-IG-0003 | 17 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0211 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
492 | PS5-79-TE-0196-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 77 |  | PS5-79-IG-0003 | 18 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0196 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
493 | PS5-79-TE-0244-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 78 |  | PS5-79-IG-0003 | 19 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0244 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
494 | PS5-79-TE-0238-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 94 |  | PS5-79-IG-0003 | 20 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0238 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
495 | PS5-79-TE-0348-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 132 |  | PS5-79-IG-0003 | 21 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0348 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
496 | PS5-79-TE-0352-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 143 |  | PS5-79-IG-0003 | 22 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0352 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
497 | PS5-79-TE-0242-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 158 |  | PS5-79-IG-0003 | 23 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0242 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
498 | PS5-79-TE-0109-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 145 |  | PS5-79-IG-0003 | 24 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0109 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
499 | PS5-79-TE-0113-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 146 |  | PS5-79-IG-0003 | 25 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0113 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
500 | PS5-79-TE-0106-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 147 |  | PS5-79-IG-0003 | 26 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0106 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
501 | PS5-79-TE-0351-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 161 |  | PS5-79-IG-0003 | 27 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0351 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
502 | PS5-79-TE-0243-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 142 |  | PS5-79-IG-0003 | 28 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0243 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
503 | PS5-60-TE-0365-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 85 |  | PS5-79-IG-0003 | 31 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0365 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
504 | PS5-79-TE-0280-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 79 |  | PS5-79-IG-0004 | 1 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0280 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
505 | PS5-79-TE-0331-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 76 |  | PS5-79-IG-0004 | 2 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0331 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
506 | PS5-79-TE-0327-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 74 |  | PS5-79-IG-0004 | 3 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0327 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
507 | PS5-79-TE-0266-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 73 |  | PS5-79-IG-0004 | 4 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0266 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
508 | PS5-79-TE-0265-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 73 |  | PS5-79-IG-0004 | 5 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0265 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
509 | PS5-79-TE-0212-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 16 |  | PS5-79-IG-0004 | 6 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0212 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
510 | PS5-79-TE-0049-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 76 |  | PS5-79-IG-0004 | 7 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0049 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
511 | PS5-79-TE-0329-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 67 |  | PS5-79-IG-0004 | 8 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0329 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
512 | PS5-79-TE-0285-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 65 |  | PS5-79-IG-0004 | 9 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0285 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
513 | PS5-79-TE-0220-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 59 |  | PS5-79-IG-0004 | 10 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0220 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
514 | PS5-79-TE-0217-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 66 |  | PS5-79-IG-0004 | 11 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0217 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
515 | PS5-79-TE-0219-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 55 |  | PS5-79-IG-0004 | 12 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0219 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
516 | PS5-79-TE-0237-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 52 |  | PS5-79-IG-0004 | 13 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0237 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
517 | PS5-79-TE-0282-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 43 |  | PS5-79-IG-0004 | 14 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0282 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
518 | PS5-79-TE-0213-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 32 |  | PS5-79-IG-0004 | 15 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0213 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
519 | PS5-79-TE-0086-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 47 |  | PS5-79-IG-0004 | 16 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0086 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
520 | PS5-79-TE-0214-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 47 |  | PS5-79-IG-0004 | 17 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0214 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
521 | PS5-79-TE-0283-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 45 |  | PS5-79-IG-0004 | 18 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0283 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
522 | PS5-79-TE-0092-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 68 |  | PS5-79-IG-0004 | 19 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0092 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
523 | PS5-79-TE-0216-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 66 |  | PS5-79-IG-0004 | 20 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0216 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
524 | PS5-79-TE-0215-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 68 |  | PS5-79-IG-0004 | 21 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0215 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
525 | PS5-79-TE-0099-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 70 |  | PS5-79-IG-0004 | 22 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0099 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
526 | PS5-79-TE-0171-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 74 |  | PS5-79-IG-0004 | 23 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0171 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
527 | PS5-79-TE-0264-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 73 |  | PS5-79-IG-0004 | 24 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0264 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
528 | PS5-79-TE-0281-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 22 |  | PS5-79-IG-0004 | 25 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0281 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
529 | PS5-79-TE-0284-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 24 |  | PS5-79-IG-0004 | 26 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0284 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
530 | PS5-60-TE-0366-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 90 |  | PS5-79-IG-0004 | 28 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0366 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
531 | PS5-79-TE-0332-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 89 |  | PS5-79-IG-0005 | 1 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0332 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
532 | PS5-79-TE-0330-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 86 |  | PS5-79-IG-0005 | 2 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0330 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
533 | PS5-79-TE-0269-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 87 |  | PS5-79-IG-0005 | 3 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0269 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
534 | PS5-79-TE-0267-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 87 |  | PS5-79-IG-0005 | 4 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0267 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
535 | PS5-79-TE-0268-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 87 |  | PS5-79-IG-0005 | 5 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0268 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
536 | PS5-79-TE-0334-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 81 |  | PS5-79-IG-0005 | 6 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0334 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
537 | PS5-79-TE-0333-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 77 |  | PS5-79-IG-0005 | 7 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0333 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
538 | PS5-79-TE-0272-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 77 |  | PS5-79-IG-0005 | 8 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0272 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
539 | PS5-79-TE-0270-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 78 |  | PS5-79-IG-0005 | 9 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0270 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
540 | PS5-79-TE-0271-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 77 |  | PS5-79-IG-0005 | 10 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0271 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
541 | PS5-79-TE-0335-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 85 |  | PS5-79-IG-0005 | 11 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0335 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
542 | PS5-79-TE-0339-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 88 |  | PS5-79-IG-0005 | 12 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0339 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
543 | PS5-79-TE-0275-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 85 |  | PS5-79-IG-0005 | 13 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0275 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
544 | PS5-79-TE-0273-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 83 |  | PS5-79-IG-0005 | 14 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0273 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
545 | PS5-79-TE-0274-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 82 |  | PS5-79-IG-0005 | 15 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0274 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
546 | PS5-79-TE-0328-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 75 |  | PS5-79-IG-0005 | 16 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0328 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
547 | PS5-79-TE-0061-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 72 |  | PS5-79-IG-0005 | 17 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0061 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
548 | PS5-79-TE-0218-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 65 |  | PS5-79-IG-0005 | 18 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0218 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
549 | PS5-79-TE-0229-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 81 |  | PS5-79-IG-0005 | 19 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0229 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
550 | PS5-79-TE-0223-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 60 |  | PS5-79-IG-0005 | 20 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0223 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
551 | PS5-79-TE-0224-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 64 |  | PS5-79-IG-0005 | 21 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0224 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
552 | PS5-79-TE-0221-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 71 |  | PS5-79-IG-0005 | 22 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0221 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
553 | PS5-79-TE-0235-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 96 |  | PS5-79-IG-0005 | 23 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0235 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
554 | PS5-79-TE-0222-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 67 |  | PS5-79-IG-0005 | 24 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0222 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
555 | PS5-79-TE-0350-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 70 |  | PS5-79-IG-0005 | 25 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0350 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
556 | PS5-79-TE-0228-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 76 |  | PS5-79-IG-0005 | 26 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0228 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
557 | PS5-79-TE-0236-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 90 |  | PS5-79-IG-0005 | 27 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0236 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
558 | PS5-60-TE-0367-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 85 |  | PS5-79-IG-0005 | 28 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0367 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
559 | PS5-79-TE-0136-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 110 |  | PS5-79-IG-0009 | 1 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0136 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
560 | PS5-79-TE-0027-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 109 |  | PS5-79-IG-0009 | 2 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0027 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
561 | PS5-79-TE-0039-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 87 |  | PS5-79-IG-0009 | 3 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0039 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
562 | PS5-79-TE-0037-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 75 |  | PS5-79-IG-0009 | 4 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0037 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
563 | PS5-79-TE-0025-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 97 |  | PS5-79-IG-0009 | 5 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0025 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
564 | PS5-79-TE-0343-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 109 |  | PS5-79-IG-0009 | 6 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0343 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
565 | PS5-79-TE-0118-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 88 |  | PS5-79-IG-0009 | 7 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0118 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
566 | PS5-79-TE-0137-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 88 |  | PS5-79-IG-0009 | 8 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0137 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
567 | PS5-79-TE-0024-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 87 |  | PS5-79-IG-0009 | 9 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0024 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
568 | PS5-79-TE-0150-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 99 |  | PS5-79-IG-0009 | 10 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0150 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
569 | PS5-79-TE-0203-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 69 |  | PS5-79-IG-0009 | 11 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0203 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
570 | PS5-79-TE-0204-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 68 |  | PS5-79-IG-0009 | 12 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0204 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
571 | PS5-79-TE-0262-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 73 |  | PS5-79-IG-0009 | 13 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0262 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
572 | PS5-79-TE-0102-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 75 |  | PS5-79-IG-0009 | 14 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0102 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
573 | PS5-79-TE-0081-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 84 |  | PS5-79-IG-0009 | 15 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0081 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
574 | PS5-79-TE-0036-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 85 |  | PS5-79-IG-0009 | 16 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0036 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
575 | PS5-79-TE-0066-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 73 |  | PS5-79-IG-0009 | 17 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0066 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
576 | PS5-79-TE-0067-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 78 |  | PS5-79-IG-0009 | 18 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0067 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
577 | PS5-79-TE-0245-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 82 |  | PS5-79-IG-0009 | 19 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0245 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
578 | PS5-79-TE-0134-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 92 |  | PS5-79-IG-0009 | 20 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0134 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
579 | PS5-79-TE-0063-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 91 |  | PS5-79-IG-0009 | 21 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0063 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
580 | PS5-79-TE-0154-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 97 |  | PS5-79-IG-0009 | 22 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0154 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
581 | PS5-79-TE-0319-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 74 |  | PS5-79-IG-0009 | 23 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0319 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
582 | PS5-79-TE-0290-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 100 |  | PS5-79-IG-0009 | 24 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0290 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
583 | PS5-79-TE-0152-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 99 |  | PS5-79-IG-0009 | 25 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0152 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
584 | PS5-79-TE-0002-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 83 |  | PS5-79-IG-0009 | 26 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0002 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
585 | PS5-79-TE-0005-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 96 |  | PS5-79-IG-0009 | 27 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0005 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
586 | PS5-79-TE-0146-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 83 |  | PS5-79-IG-0009 | 28 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0146 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
587 | PS5-79-TE-0041-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 85 |  | PS5-79-IG-0009 | 29 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0041 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
588 | PS5-79-TE-0135-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 102 |  | PS5-79-IG-0009 | 30 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0135 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
589 | PS5-79-TE-0239-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 103 |  | PS5-79-IG-0009 | 31 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0239 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
590 | PS5-79-TE-0247-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 61 |  | PS5-79-IG-0007 | 1 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0247 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
591 | PS5-79-TE-0084-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 63 |  | PS5-79-IG-0007 | 2 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0084 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
592 | PS5-79-TE-0090-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 58 |  | PS5-79-IG-0007 | 3 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0090 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
593 | PS5-79-TE-0085-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 101 |  | PS5-79-IG-0007 | 4 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0085 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
594 | PS5-79-TE-0082-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 84 |  | PS5-79-IG-0007 | 5 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0082 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
595 | PS5-79-TE-0101-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 67 |  | PS5-79-IG-0007 | 6 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0101 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
596 | PS5-79-TE-0156-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 72 |  | PS5-79-IG-0007 | 7 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0156 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=3 C=0 | 01 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
597 | PS5-79-TE-0107-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 61 |  | PS5-79-IG-0007 | 8 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0107 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
598 | PS5-79-TE-0020-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 59 |  | PS5-79-IG-0007 | 9 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0020 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 01 | nVent | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
599 | PS5-79-TE-0147-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 55 |  | PS5-79-IG-0007 | 10 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0147 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
600 | PS5-79-TE-0043-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 62 |  | PS5-79-IG-0007 | 11 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0043 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
601 | PS5-79-TE-0344-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 61 |  | PS5-79-IG-0007 | 12 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0344 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
602 | PS5-79-TE-0019-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 55 |  | PS5-79-IG-0007 | 13 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0019 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
603 | PS5-79-TE-0100-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 51 |  | PS5-79-IG-0007 | 14 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0100 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
604 | PS5-79-TE-0112-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 59 |  | PS5-79-IG-0007 | 15 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0112 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
605 | PS5-79-TE-0068-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 74 |  | PS5-79-IG-0007 | 16 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0068 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=3 C=0 | 00 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
606 | PS5-79-TE-0042-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 74 |  | PS5-79-IG-0007 | 17 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0042 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=3 C=0 | 00 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
607 | PS5-79-TE-0121-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 65 |  | PS5-79-IG-0007 | 18 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0121 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=3 C=0 | 00 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
608 | PS5-79-TE-0072-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 71 |  | PS5-79-IG-0007 | 19 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0072 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
609 | PS5-79-TE-0116-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 65 |  | PS5-79-IG-0007 | 20 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0116 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=3 C=0 | 01 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
610 | PS5-79-TE-0145-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 87 |  | PS5-79-IG-0007 | 21 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0145 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
611 | PS5-79-TE-0155-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 93 |  | PS5-79-IG-0007 | 22 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0155 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
612 | PS5-79-TE-0071-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 85 |  | PS5-79-IG-0007 | 23 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0071 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
613 | PS5-79-TE-0083-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 66 |  | PS5-79-IG-0007 | 24 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0083 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
614 | PS5-79-TE-0291-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 72 |  | PS5-79-IG-0007 | 25 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0291 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=3 C=0 | 00 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
615 | PS5-79-TE-0003-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 73 |  | PS5-79-IG-0007 | 26 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0003 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=3 C=0 | 00 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
616 | PS5-79-TE-0143-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 73 |  | PS5-79-IG-0007 | 27 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0143 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=3 C=0 | 01 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
617 | PS5-79-TE-0059-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 75 |  | PS5-79-IG-0007 | 28 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0059 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=3 C=0 | 00 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
618 | PS5-79-TE-0006-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 97 |  | PS5-79-IG-0007 | 29 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0006 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=3 C=0 | 01 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
619 | PS5-79-TE-0144-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 99 |  | PS5-79-IG-0007 | 30 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0144 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
620 | PS5-79-TE-0240-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 101 |  | PS5-79-IG-0007 | 31 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0240 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=3 C=0 | 00 | nVent | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
621 | PS5-79-TE-0241-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 87 |  | PS5-79-IG-0008 | 1 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0241 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=3 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
622 | PS5-79-TE-0208-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 58 |  | PS5-79-IG-0008 | 2 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0208 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
623 | PS5-79-TE-0292-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 72 |  | PS5-79-IG-0008 | 3 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0292 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=3 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
624 | PS5-79-TE-0058-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 76 |  | PS5-79-IG-0008 | 4 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0058 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
625 | PS5-79-TE-0140-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 74 |  | PS5-79-IG-0008 | 5 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0140 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=3 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
626 | PS5-79-TE-0004-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 73 |  | PS5-79-IG-0008 | 6 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0004 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=3 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
627 | PS5-79-TE-0007-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 92 |  | PS5-79-IG-0008 | 7 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0007 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=3 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
628 | PS5-79-TE-0161-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 71 |  | PS5-79-IG-0008 | 8 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0161 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
629 | PS5-79-TE-0139-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 68 |  | PS5-79-IG-0008 | 9 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0139 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=3 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
630 | PS5-79-TE-0162-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 72 |  | PS5-79-IG-0008 | 10 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0162 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 01 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
631 | PS5-79-TE-0074-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 74 |  | PS5-79-IG-0008 | 11 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0074 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
632 | PS5-79-TE-0142-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 74 |  | PS5-79-IG-0008 | 12 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0142 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=3 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
633 | PS5-79-TE-0160-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 72 |  | PS5-79-IG-0008 | 13 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0160 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
634 | PS5-79-TE-0077-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 67 |  | PS5-79-IG-0008 | 14 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0077 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
635 | PS5-79-TE-0075-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 59 |  | PS5-79-IG-0008 | 15 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0075 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
636 | PS5-79-TE-0053-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 54 |  | PS5-79-IG-0008 | 16 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0053 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
637 | PS5-79-TE-0076-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 57 |  | PS5-79-IG-0008 | 17 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0076 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
638 | PS5-79-TE-0070-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 69 |  | PS5-79-IG-0008 | 18 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0070 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
639 | PS5-79-TE-0158-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 67 |  | PS5-79-IG-0008 | 19 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0158 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
640 | PS5-79-TE-0060-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 64 |  | PS5-79-IG-0008 | 20 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0060 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
641 | PS5-79-TE-0115-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 71 |  | PS5-79-IG-0008 | 21 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0115 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
642 | PS5-79-TE-0108-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 69 |  | PS5-79-IG-0008 | 22 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0108 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
643 | PS5-79-TE-0111-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 70 |  | PS5-79-IG-0008 | 23 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0111 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
644 | PS5-79-TE-0062-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 59 |  | PS5-79-IG-0008 | 24 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0062 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
645 | PS5-79-TE-0141-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 89 |  | PS5-79-IG-0008 | 25 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0141 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
646 | PS5-79-TE-0207-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 59 |  | PS5-79-IG-0008 | 26 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0207 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
647 | PS5-79-TE-0205-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 53 |  | PS5-79-IG-0008 | 27 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0205 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 01 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
648 | PS5-79-TE-0044-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 59 |  | PS5-79-IG-0008 | 28 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0044 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
649 | PS5-79-TE-0045-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 53 |  | PS5-79-IG-0008 | 29 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0045 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
650 | PS5-79-TE-0261-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 52 |  | PS5-79-IG-0008 | 30 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0261 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=2 B=2 C=0 | 00 | nVent | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
651 | PS5-79-TE-0209-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 35 |  | PS5-79-IG-0008 | 31 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0209 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
652 | PS5-79-TE-0064-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 137 |  | PS5-79-IG-0006 | 1 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0064 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
653 | PS5-79-TE-0057-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 134 |  | PS5-79-IG-0006 | 2 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0057 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
654 | PS5-79-TE-0021-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 118 |  | PS5-79-IG-0006 | 3 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0021 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
655 | PS5-79-TE-0128-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 128 |  | PS5-79-IG-0006 | 4 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0128 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
656 | PS5-79-TE-0008-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 122 |  | PS5-79-IG-0006 | 5 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0008 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
657 | PS5-79-TE-0047-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 112 |  | PS5-79-IG-0006 | 6 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0047 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
658 | PS5-79-TE-0052-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 128 |  | PS5-79-IG-0006 | 7 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0052 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
659 | PS5-79-TE-0056-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 130 |  | PS5-79-IG-0006 | 8 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0056 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
660 | PS5-79-TE-0055-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 130 |  | PS5-79-IG-0006 | 9 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0055 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
661 | PS5-79-TE-0028-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 111 |  | PS5-79-IG-0006 | 10 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0028 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
662 | PS5-79-TE-0294-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 124 |  | PS5-79-IG-0006 | 11 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0294 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
663 | PS5-79-TE-0293-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 125 |  | PS5-79-IG-0006 | 12 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0293 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
664 | PS5-79-TE-0129-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 123 |  | PS5-79-IG-0006 | 13 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0129 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
665 | PS5-79-TE-0073-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 118 |  | PS5-79-IG-0006 | 14 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0073 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
666 | PS5-79-TE-0010-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 117 |  | PS5-79-IG-0006 | 15 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0010 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
667 | PS5-79-TE-0124-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 126 |  | PS5-79-IG-0006 | 16 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0124 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
668 | PS5-79-TE-0295-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 119 |  | PS5-79-IG-0006 | 17 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0295 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
669 | PS5-79-TE-0030-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 111 |  | PS5-79-IG-0006 | 18 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0030 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
670 | PS5-79-TE-0127-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 117 |  | PS5-79-IG-0006 | 19 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0127 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
671 | PS5-79-TE-0051-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 114 |  | PS5-79-IG-0006 | 20 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0051 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
672 | PS5-79-TE-0032-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 112 |  | PS5-79-IG-0006 | 21 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0032 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
673 | PS5-79-TE-0033-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 111 |  | PS5-79-IG-0006 | 22 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0033 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
674 | PS5-79-TE-0126-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 126 |  | PS5-79-IG-0006 | 23 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0126 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
675 | PS5-79-TE-0125-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 128 |  | PS5-79-IG-0006 | 24 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0125 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
676 | PS5-79-TE-0011-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 138 |  | PS5-79-IG-0006 | 25 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0011 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
677 | PS5-79-TE-0301-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 118 |  | PS5-79-IG-0006 | 26 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0301 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
678 | PS5-79-TE-0001-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 127 |  | PS5-79-IG-0006 | 27 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0001 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
679 | PS5-79-TE-0009-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 120 |  | PS5-79-IG-0006 | 28 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0009 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
680 | PS5-79-TE-0014-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 121 |  | PS5-79-IG-0006 | 29 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0014 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
681 | PS5-79-TE-0034-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 110 |  | PS5-79-IG-0006 | 30 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0034 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
682 | PS5-79-TE-0353-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 115 |  | PS5-79-IG-0006 | 31 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0353 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
683 | PS5-71-TE-0362-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 97 |  | PS5-79-IG-0006 | 34 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-71-TE-0362 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
684 | PS5-79-TE-0132-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 130 |  | PS5-79-IG-0010 | 1 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0132 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
685 | PS5-79-TE-0131-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 133 |  | PS5-79-IG-0010 | 2 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0131 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
686 | PS5-79-TE-0040-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 127 |  | PS5-79-IG-0010 | 3 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0040 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
687 | PS5-79-TE-0233-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 118 |  | PS5-79-IG-0010 | 4 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0233 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
688 | PS5-79-TE-0054-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 119 |  | PS5-79-IG-0010 | 5 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0054 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
689 | PS5-79-TE-0022-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 120 |  | PS5-79-IG-0010 | 6 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0022 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
690 | PS5-79-TE-0078-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 115 |  | PS5-79-IG-0010 | 7 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0078 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
691 | PS5-79-TE-0105-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 112 |  | PS5-79-IG-0010 | 8 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0105 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
692 | PS5-79-TE-0029-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 111 |  | PS5-79-IG-0010 | 9 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0029 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
693 | PS5-79-TE-0035-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 103 |  | PS5-79-IG-0010 | 10 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0035 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
694 | PS5-79-TE-0094-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 117 |  | PS5-79-IG-0010 | 11 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0094 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
695 | PS5-79-TE-0120-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 102 |  | PS5-79-IG-0010 | 12 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0120 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
696 | PS5-79-TE-0095-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 105 |  | PS5-79-IG-0010 | 13 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0095 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
697 | PS5-79-TE-0087-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 99 |  | PS5-79-IG-0010 | 14 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0087 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
698 | PS5-79-TE-0119-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 101 |  | PS5-79-IG-0010 | 15 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0119 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
699 | PS5-79-TE-0117-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 118 |  | PS5-79-IG-0010 | 16 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0117 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
700 | PS5-79-TE-0323-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 103 |  | PS5-79-IG-0010 | 17 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0323 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
701 | PS5-79-TE-0096-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 73 |  | PS5-79-IG-0010 | 18 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0096 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
702 | PS5-79-TE-0079-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 98 |  | PS5-79-IG-0010 | 19 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0079 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
703 | PS5-79-TE-0345-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 96 |  | PS5-79-IG-0010 | 20 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0345 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
704 | PS5-79-TE-0104-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 93 |  | PS5-79-IG-0010 | 21 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0104 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
705 | PS5-79-TE-0230-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 83 |  | PS5-79-IG-0010 | 22 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0230 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
706 | PS5-79-TE-0093-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 80 |  | PS5-79-IG-0010 | 23 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0093 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
707 | PS5-79-TE-0088-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 81 |  | PS5-79-IG-0010 | 24 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0088 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
708 | PS5-79-TE-0089-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 81 |  | PS5-79-IG-0010 | 25 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0089 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
709 | PS5-79-TE-0091-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 71 |  | PS5-79-IG-0010 | 26 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0091 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
710 | PS5-79-TE-0097-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 67 |  | PS5-79-IG-0010 | 27 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0097 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
711 | PS5-79-TE-0321-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 100 |  | PS5-79-IG-0010 | 28 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0321 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
712 | PS5-79-TE-0227-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 71 |  | PS5-79-IG-0010 | 29 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0227 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
713 | PS5-60-TE-0364-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 157 |  | PS5-79-IG-0010 | 31 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0364 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
714 | PS5-79-TE-0286-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 54 |  | PS5-79-IG-0011 | 1 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0286 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
715 | PS5-79-TE-0347-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 55 |  | PS5-79-IG-0011 | 2 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0347 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
716 | PS5-79-TE-0289-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 55 |  | PS5-79-IG-0011 | 3 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0289 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
717 | PS5-79-TE-0342-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 63 |  | PS5-79-IG-0011 | 4 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0342 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
718 | PS5-79-TE-0232-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 47 |  | PS5-79-IG-0011 | 5 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0232 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
719 | PS5-79-TE-0231-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 42 |  | PS5-79-IG-0011 | 6 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0231 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
720 | PS5-79-TE-0288-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 64 |  | PS5-79-IG-0011 | 7 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0288 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
721 | PS5-79-TE-0225-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 40 |  | PS5-79-IG-0011 | 8 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0225 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
722 | PS5-79-TE-0324-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 59 |  | PS5-79-IG-0011 | 9 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0324 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
723 | PS5-79-TE-0080-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 49 |  | PS5-79-IG-0011 | 10 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0080 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
724 | PS5-79-TE-0065-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 52 |  | PS5-79-IG-0011 | 11 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0065 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
725 | PS5-79-TE-0287-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 61 |  | PS5-79-IG-0011 | 12 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0287 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
726 | PS5-79-TE-0277-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 64 |  | PS5-79-IG-0011 | 13 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0277 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
727 | PS5-79-TE-0276-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 64 |  | PS5-79-IG-0011 | 14 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0276 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
728 | PS5-79-TE-0226-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 37 |  | PS5-79-IG-0011 | 15 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0226 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
729 | PS5-79-TE-0340-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 64 |  | PS5-79-IG-0011 | 16 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0340 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
730 | PS5-79-TE-0336-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 67 |  | PS5-79-IG-0011 | 17 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0336 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
731 | PS5-79-TE-0031-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 54 |  | PS5-79-IG-0011 | 18 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0031 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
732 | PS5-79-TE-0016-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 55 |  | PS5-79-IG-0011 | 19 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0016 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
733 | PS5-79-TE-0038-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 55 |  | PS5-79-IG-0011 | 20 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0038 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
734 | PS5-79-TE-0341-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 55 |  | PS5-79-IG-0011 | 21 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0341 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
735 | PS5-79-TE-0337-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 59 |  | PS5-79-IG-0011 | 22 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0337 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
736 | PS5-79-TE-0050-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 60 |  | PS5-79-IG-0011 | 23 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0050 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
737 | PS5-79-TE-0048-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 61 |  | PS5-79-IG-0011 | 24 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0048 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
738 | PS5-79-TE-0069-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 63 |  | PS5-79-IG-0011 | 25 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0069 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
739 | PS5-79-TE-0349-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 55 |  | PS5-79-IG-0011 | 26 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0349 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 00 | nVent
740 | PS5-79-TE-0338-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 62 |  | PS5-79-IG-0011 | 27 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0338 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 |  | 01 | nVent
741 | PS5-60-TE-0368-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 67 |  | PS5-79-IG-0011 | 28 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0368 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
742 | PS5-60-TE-0369-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 58 |  | PS5-79-IG-0011 | 29 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0369 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
743 | PS5-60-TE-0370-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 63 |  | PS5-79-IG-0011 | 30 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-60-TE-0370 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | Sampling (Control) | 01 | nVent
744 | PS5-79-TE-0251-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 40 |  | PS5-79-IG-0012 | 1 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0251 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
745 | PS5-79-TE-0297-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 41 |  | PS5-79-IG-0012 | 2 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0297 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
746 | PS5-79-TE-0296-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 40 |  | PS5-79-IG-0012 | 3 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0296 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
747 | PS5-79-TE-0012-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 52 |  | PS5-79-IG-0012 | 4 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0012 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
748 | PS5-79-TE-0259-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 28 |  | PS5-79-IG-0012 | 5 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0259 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
749 | PS5-79-TE-0257-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 55 |  | PS5-79-IG-0012 | 6 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0257 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
750 | PS5-79-TE-0258-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 62 |  | PS5-79-IG-0012 | 7 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0258 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
751 | PS5-79-TE-0098-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 63 |  | PS5-79-IG-0012 | 8 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0098 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
752 | PS5-79-TE-0300-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 64 |  | PS5-79-IG-0012 | 9 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0300 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
753 | PS5-79-TE-0123-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 62 |  | PS5-79-IG-0012 | 10 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0123 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
754 | PS5-79-TE-0248-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 84 |  | PS5-79-IG-0012 | 11 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0248 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
755 | PS5-79-TE-0254-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 51 |  | PS5-79-IG-0012 | 12 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0254 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
756 | PS5-79-TE-0310-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 56 |  | PS5-79-IG-0012 | 13 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0310 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
757 | PS5-79-TE-0263-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 53 |  | PS5-79-IG-0012 | 14 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0263 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
758 | PS5-79-TE-0122-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 53 |  | PS5-79-IG-0012 | 15 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0122 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
759 | PS5-79-TE-0110-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 51 |  | PS5-79-IG-0012 | 16 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0110 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
760 | PS5-79-TE-0256-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 51 |  | PS5-79-IG-0012 | 17 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0256 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
761 | PS5-79-TE-0320-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 53 |  | PS5-79-IG-0012 | 18 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0320 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
762 | PS5-79-TE-0255-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 52 |  | PS5-79-IG-0012 | 19 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0255 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
763 | PS5-79-TE-0017-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 54 |  | PS5-79-IG-0012 | 20 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0017 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
764 | PS5-79-TE-0250-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 56 |  | PS5-79-IG-0012 | 21 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0250 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
765 | PS5-79-TE-0249-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 58 |  | PS5-79-IG-0012 | 22 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0249 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 00 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
766 | PS5-79-TE-0318-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 58 |  | PS5-79-IG-0012 | 23 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0318 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
767 | PS5-79-TE-0309-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 79 |  | PS5-79-IG-0012 | 24 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0309 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
768 | PS5-79-TE-0018-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 80 |  | PS5-79-IG-0012 | 25 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0018 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
769 | PS5-79-TE-0130-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 87 |  | PS5-79-IG-0012 | 26 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0130 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
770 | PS5-79-TE-0299-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 52 |  | PS5-79-IG-0012 | 27 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0299 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
771 | PS5-79-TE-0308-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 63 |  | PS5-79-IG-0012 | 28 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0308 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
772 | PS5-79-TE-0013-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 26 |  | PS5-79-IG-0012 | 29 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0013 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
773 | PS5-79-TE-0015-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 44 |  | PS5-79-IG-0012 | 30 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0015 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
774 | PS5-79-TE-0133-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 40 |  | PS5-79-IG-0012 | 31 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0133 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
775 | PS5-79-TE-0298-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 42 |  | PS5-79-IG-0012 | 32 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0298 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 00 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
776 | PS5-79-TE-0026-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 41 |  | PS5-79-IG-0012 | 33 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0026 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
777 | PS5-79-TE-0138-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 24 |  | PS5-79-IG-0012 | 34 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0138 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=1 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
778 | PS5-25-TE-0364-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 146 |  | PS5-79-IG-0012 | 37 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-25-TE-0364 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | A=0 B=2 C=0 | 01 | nVent | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
779 | PS5-79-BE-0175-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 104 |  | PS5-79-IG-0009 | 40 | Heat Tracing Panel |  | Outdoor | SIND-M20-Gland | M20 | PS5-79-BE-0175 |  | Marshalling Box |  | Field | SIND M25 Metal Gland Alarm | M25 |  | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
780 | PS5-79-IP-9101-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 2 |  | PS5-79-BE-0175 | 40 | Marshalling Box |  | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9101 |  | ETS-05 |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
781 | PS5-79-IP-9102-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 2 |  | PS5-79-BE-0175 | 40 | Marshalling Box |  | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9102 |  | ETS-05 |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
782 | PS5-79-BE-0176-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 97 |  | PS5-79-IG-0007 | 40 | Heat Tracing Panel |  | Outdoor | SIND-M20-Gland | M20 | PS5-79-BE-0176 |  | Marshalling Box |  | Field | SIND M25 Metal Gland Alarm | M25 |  | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
783 | PS5-79-IP-9103-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 2 |  | PS5-79-BE-0176 | 40 | Marshalling Box |  | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9103 |  | ETS-05 |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
784 | PS5-79-IP-9104-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 2 |  | PS5-79-BE-0176 | 40 | Marshalling Box |  | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9104 |  | ETS-05 |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
785 | PS5-79-BE-0177-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 86 |  | PS5-79-IG-0008 | 40 | Heat Tracing Panel |  | Outdoor | SIND-M20-Gland | M20 | PS5-79-BE-0177 |  | Marshalling Box |  | Field | SIND M25 Metal Gland Alarm | M25 |  | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
786 | PS5-79-IP-9105-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 2 |  | PS5-79-BE-0177 | 40 | Marshalling Box |  | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9105 |  | ETS-05 |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
787 | PS5-79-IP-9106-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 2 |  | PS5-79-BE-0177 | 40 | Marshalling Box |  | Outdoor | SIND-M20-Gland | M20 | PS5-79-IP-9106 |  | ETS-05 |  | Field | SIND M20 Gland | M20 |  | TZ-MID-68-NVS1-150359 | 14 | Export Pump (Alarm) | 01 | nVent
788 | PS5-79-TE-0175-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 124 |  | PS5-79-IG-0006 | 37 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0175 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | 2nd Sensor on Pig Launcher | 01 | nVent
789 | PS5-79-TE-0176-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 125 |  | PS5-79-IG-0006 | 38 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0176 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | 2nd Sensor on Pig Launcher | 01 | nVent
790 | PS5-79-TE-0178-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 118 |  | PS5-79-IG-0006 | 39 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0178 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | 2nd Sensor on Pig Launcher | 01 | nVent
791 | PS5-79-TE-0177-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1,5 | 119 |  | PS5-79-IG-0006 | 40 | Heat Tracing Panel |  | Outdoor | SIND M20 Gland | M20 | PS5-79-TE-0177 |  | PT100 Junction Box |  | Field | SIND M20 Gland | M25 |  | TZ-MID-68-NVS1-150360 | 14 | 2nd Sensor on Pig Launcher | 01 | nVent
EHT POWER SCHEDULE DATA
1 | PS5-71-BE-0363-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 74.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
2 | PS5-79-BE-0123-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333449 | 2C+E | 6.0 | 63.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
3 | PS5-79-BE-0309-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333446 | 2C+E | 6.0 | 80.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
4 | PS5-79-BE-0018-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333446 | 2C+E | 6.0 | 81.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
5 | PS5-79-BE-0130-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333446 | 2C+E | 6.0 | 88.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
6 | PS5-79-BE-0015-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333446 | 2C+E | 6.0 | 44.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
7 | PS5-79-BE-0133-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333446 | 2C+E | 6.0 | 40.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
8 | PS5-79-BE-0298-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333446 | 2C+E | 6.0 | 43.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
9 | PS5-79-BE-0026-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333446 | 2C+E | 6.0 | 42.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
10 | PS5-79-TE-0309-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 79.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
11 | PS5-79-TE-0018-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 80.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
12 | PS5-79-TE-0130-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 87.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
13 | PS5-79-IG-0001-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95.0 | 5.0
14 | PS5-79-IG-0002-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95.0 | 5.0
15 | PS5-79-IG-0003-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95.0 | 5.0
16 | PS5-79-IG-0004-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95.0 | 5.0
17 | PS5-79-IG-0005-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95.0 | 5.0
18 | PS5-79-IG-0006-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95.0 | 5.0
19 | PS5-79-IG-0007-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95.0 | 5.0
20 | PS5-79-IG-0008-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95.0 | 5.0
21 | PS5-79-IG-0009-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95.0 | 5.0
22 | PS5-79-IG-0010-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95.0 | 5.0
23 | PS5-79-IG-0011-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95.0 | 5.0
24 | PS5-79-IG-0012-CL01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 4C | 95.0 | 5.0
25 | PS5-79-IG-0001-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95.0 | 5.0
26 | PS5-79-IG-0002-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95.0 | 5.0
27 | PS5-79-IG-0003-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95.0 | 5.0
28 | PS5-79-IG-0004-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95.0 | 5.0
29 | PS5-79-IG-0005-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95.0 | 5.0
30 | PS5-79-IG-0006-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95.0 | 5.0
31 | PS5-79-IG-0007-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95.0 | 5.0
32 | PS5-79-IG-0008-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95.0 | 5.0
33 | PS5-79-IG-0009-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95.0 | 5.0
34 | PS5-79-IG-0010-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95.0 | 5.0
35 | PS5-79-IG-0011-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95.0 | 5.0
36 | PS5-79-IG-0012-CG01 | 0.6/1KV | CU/XLPE/FR-LSZH/GSWA/FR-LSZH | 400V AC |  | 1C | 95.0 | 5.0
37 | PS5-79-IG-0001-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 6.0
38 | PS5-79-IG-0002-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 6.0
39 | PS5-79-IG-0003-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 6.0
40 | PS5-79-IG-0004-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 6.0
41 | PS5-79-IG-0005-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 6.0
42 | PS5-79-IG-0006-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 6.0
43 | PS5-79-IG-0007-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 6.0
44 | PS5-79-IG-0008-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 6.0
45 | PS5-79-IG-0009-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 6.0
46 | PS5-79-IG-0010-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 6.0
47 | PS5-79-IG-0011-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 6.0
48 | PS5-79-IG-0012-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 6.0
49 | PS5-79-BE-0316-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 88.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
50 | PS5-79-BE-0315-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 87.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
51 | PS5-79-BE-0168-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 84.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
52 | PS5-79-BE-0170-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 84.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
53 | PS5-79-BE-0163-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 76.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
54 | PS5-79-BE-0167-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 84.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
55 | PS5-79-SP-0167-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 4.0
56 | PS5-79-BE-0169-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 83.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
57 | PS5-79-SP-0169-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 4.0
58 | PS5-79-BE-0159-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 82.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
59 | PS5-79-BE-0164-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 82.0
60 | PS5-79-BE-0151-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 75.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
61 | PS5-79-BE-0356-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 87.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
62 | PS5-79-BE-0206-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 71.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
63 | PS5-79-BE-0148-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 80.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
64 | PS5-79-BE-0314-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 79.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
65 | PS5-79-BE-0149-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 79.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
66 | PS5-79-BE-0234-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 85.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
67 | PS5-79-BE-0114-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 83.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
68 | PS5-79-BE-0165-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 73.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
69 | PS5-79-BE-0166-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 83.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
70 | PS5-79-BE-0157-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 72.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
71 | PS5-79-BE-0153-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 81.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
72 | PS5-79-BE-0313-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 81.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
73 | PS5-79-BE-0188-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 71.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
74 | PS5-79-BE-0202-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 62.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
75 | PS5-79-BE-0103-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 52.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
76 | PS5-79-BE-0317-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 50.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
77 | PS5-79-BE-0306-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 51.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
78 | PS5-79-BE-0197-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 52.0
79 | PS5-71-BE-0361-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 85.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
80 | PS5-79-BE-0181-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 69.0
81 | PS5-79-BE-0184-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 69.0
82 | PS5-79-BE-0302-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 69.0
83 | PS5-79-BE-0185-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 65.0
84 | PS5-79-BE-0182-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 63.0
85 | PS5-79-BE-0303-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 65.0
86 | PS5-79-BE-0304-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 57.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
87 | PS5-79-BE-0325-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333449 | 2C+E | 6.0 | 74.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
88 | PS5-79-BE-0311-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333449 | 2C+E | 6.0 | 73.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
89 | PS5-79-BE-0312-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333449 | 2C+E | 6.0 | 71.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
90 | PS5-79-BE-0173-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 62.0
91 | PS5-79-BE-0183-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 59.0
92 | PS5-79-BE-0355-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333449 | 2C+E | 6.0 | 68.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
93 | PS5-79-BE-0354-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333449 | 2C+E | 6.0 | 69.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
94 | PS5-79-BE-0201-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 43.0
95 | PS5-79-BE-0172-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 59.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
96 | PS5-79-BE-0180-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 53.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
97 | PS5-79-BE-0191-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 53.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
98 | PS5-79-BE-0192-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 53.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
99 | PS5-79-BE-0193-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 37.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
100 | PS5-79-BE-0196-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 76.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
101 | PS5-79-BE-0179-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 56.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
102 | PS5-79-BE-0326-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333449 | 2C+E | 6.0 | 75.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
103 | PS5-79-BE-0238-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 93.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
104 | PS5-79-BE-0174-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 54.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
105 | PS5-79-BE-0244-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 77.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
106 | PS5-79-BE-0199-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 16.0
107 | PS5-79-BE-0187-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 13.0
108 | PS5-79-BE-0190-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 12.0
109 | PS5-79-BE-0023-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 104.0
110 | PS5-79-BE-0278-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 108.0
111 | PS5-79-BE-0307-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 104.0
112 | PS5-79-BE-0198-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 103.0
113 | PS5-79-BE-0046-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 103.0
114 | PS5-79-BE-0195-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 102.0
115 | PS5-79-BE-0252-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 95.0
116 | PS5-79-BE-0253-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 95.0
117 | PS5-79-BE-0200-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 90.0
118 | PS5-79-BE-0194-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 90.0
119 | PS5-79-BE-0246-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 89.0
120 | PS5-79-BE-0189-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 91.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
121 | PS5-79-BE-0210-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 65.0
122 | PS5-79-BE-0186-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 87.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
123 | PS5-79-BE-0279-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 99.0
124 | PS5-79-BE-0260-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 61.0
125 | PS5-79-BE-0211-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 64.0
126 | PS5-79-BE-0305-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 53.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
127 | PS5-79-BE-0322-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 38.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
128 | PS5-79-BE-0346-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 52.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
129 | PS5-79-BE-0348-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 131.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
130 | PS5-79-BE-0352-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 142.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
131 | PS5-79-BE-0242-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 157.0
132 | PS5-79-BE-0109-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 144.0
133 | PS5-79-BE-0113-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 145.0
134 | PS5-79-BE-0106-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 146.0
135 | PS5-79-BE-0351-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 160.0
136 | PS5-79-BE-0243-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 141.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
137 | PS5-60-BE-0365-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 85.0
138 | PS5-79-BE-0280-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 79.0
139 | PS5-79-BE-0331-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 75.0
140 | PS5-79-BE-0327-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 73.0
141 | PS5-79-BE-0266-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 73.0
142 | PS5-79-BE-0265-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 72.0
143 | PS5-79-BE-0212-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 16.0
144 | PS5-79-BE-0049-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 76.0
145 | PS5-79-BE-0329-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 67.0
146 | PS5-79-BE-0285-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 65.0
147 | PS5-79-BE-0220-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 58.0
148 | PS5-79-BE-0217-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 65.0
149 | PS5-79-BE-0219-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 54.0
150 | PS5-79-BE-0237-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 52.0
151 | PS5-79-SP-0237-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 4.0
152 | PS5-79-BE-0282-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 43.0
153 | PS5-79-BE-0213-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 34.0
154 | PS5-79-BE-0086-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 48.0
155 | PS5-79-BE-0214-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 48.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
156 | PS5-79-BE-0283-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 44.0
157 | PS5-79-BE-0092-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 68.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
158 | PS5-79-BE-0216-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 67.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
159 | PS5-79-BE-0215-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 68.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
160 | PS5-79-BE-0099-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 71.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
161 | PS5-79-BE-0171-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 74.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
162 | PS5-79-BE-0264-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 73.0
163 | PS5-79-BE-0281-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 22.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
164 | PS5-79-BE-0284-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 24.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
165 | PS5-60-BE-0366-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 90.0
166 | PS5-79-BE-0332-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 90.0
167 | PS5-79-BE-0330-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 87.0
168 | PS5-79-BE-0269-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 87.0
169 | PS5-79-BE-0267-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 88.0
170 | PS5-79-BE-0268-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 87.0
171 | PS5-79-BE-0334-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 81.0
172 | PS5-79-BE-0333-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 78.0
173 | PS5-79-BE-0272-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 78.0
174 | PS5-79-BE-0270-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 78.0
175 | PS5-79-BE-0271-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 77.0
176 | PS5-79-BE-0335-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 85.0
177 | PS5-79-BE-0339-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 88.0
178 | PS5-79-BE-0275-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 85.0
179 | PS5-79-BE-0273-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 83.0
180 | PS5-79-BE-0274-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 83.0
181 | PS5-79-BE-0328-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 76.0
182 | PS5-79-BE-0061-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 73.0
183 | PS5-79-BE-0218-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 65.0
184 | PS5-79-BE-0229-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 81.0
185 | PS5-79-BE-0223-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 61.0
186 | PS5-79-BE-0224-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 64.0
187 | PS5-79-BE-0221-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 72.0
188 | PS5-79-BE-0235-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 69.0
189 | PS5-79-BE-0222-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 68.0
190 | PS5-79-BE-0350-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 71.0
191 | PS5-79-BE-0228-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 77.0
192 | PS5-79-BE-0236-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 60.0
193 | PS5-60-BE-0367-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 86.0
194 | PS5-79-BE-0136-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 111.0
195 | PS5-79-BE-0027-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 109.0
196 | PS5-79-BE-0039-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 87.0
197 | PS5-79-BE-0037-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 82.0
198 | PS5-79-BE-0025-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 91.0
199 | PS5-79-BE-0343-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 109.0
200 | PS5-79-BE-0118-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 96.0
201 | PS5-79-BE-0137-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 89.0
202 | PS5-79-BE-0024-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 87.0
203 | PS5-79-BE-0150-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 99.0
204 | PS5-79-BE-0203-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 72.0
205 | PS5-79-BE-0204-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 70.0
206 | PS5-79-BE-0262-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 74.0
207 | PS5-79-BE-0102-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 75.0
208 | PS5-79-BE-0081-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 85.0
209 | PS5-79-BE-0036-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 85.0
210 | PS5-79-BE-0066-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 73.0
211 | PS5-79-BE-0067-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 82.0
212 | PS5-79-BE-0245-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 86.0
213 | PS5-79-BE-0134-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 92.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
214 | PS5-79-BE-0063-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 91.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
215 | PS5-79-BE-0154-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 98.0
216 | PS5-79-BE-0319-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 77.0
217 | PS5-79-BE-0290-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 101.0
218 | PS5-79-BE-0152-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 100.0
219 | PS5-79-BE-0002-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 83.0
220 | PS5-79-BE-0005-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 102.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
221 | PS5-79-BE-0146-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 84.0
222 | PS5-79-BE-0041-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 86.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
223 | PS5-79-BE-0135-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 102.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
224 | PS5-79-BE-0239-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 104
225 | PS5-79-IP-9901-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 107.0
226 | PS5-79-IP-9101-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 2.0
227 | PS5-79-IP-9102-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 2.0
228 | PS5-79-BE-0247-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 62.0
229 | PS5-79-BE-0084-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 63.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
230 | PS5-79-BE-0090-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 59.0
231 | PS5-79-BE-0085-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 102.0
232 | PS5-79-BE-0082-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 85.0
233 | PS5-79-BE-0101-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 67.0
234 | PS5-79-BE-0156-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 73.0
235 | PS5-79-BE-0107-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 61.0
236 | PS5-79-BE-0020-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 80
237 | PS5-79-BE-0147-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 62.0
238 | PS5-79-BE-0043-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 61.0
239 | PS5-79-BE-0344-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 60.0
240 | PS5-79-BE-0019-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 56.0
241 | PS5-79-BE-0100-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 52.0
242 | PS5-79-BE-0112-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 59.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
243 | PS5-79-BE-0068-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 74.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
244 | PS5-79-BE-0042-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 73.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
245 | PS5-79-BE-0121-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 65.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
246 | PS5-79-BE-0072-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 94
247 | PS5-79-BE-0116-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 65.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
248 | PS5-79-BE-0145-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 94
249 | PS5-79-BE-0155-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 93.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
250 | PS5-79-BE-0071-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 94
251 | PS5-79-BE-0083-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 66.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
252 | PS5-79-BE-0291-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 74.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
253 | PS5-79-BE-0003-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 73.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
254 | PS5-79-BE-0143-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 74.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
255 | PS5-79-BE-0059-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 76.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
256 | PS5-79-BE-0006-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 96.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
257 | PS5-79-BE-0144-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 99.0
258 | PS5-79-BE-0240-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 101.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
259 | PS5-79-IP-9902-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 100.0
260 | PS5-79-IP-9103-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 2.0
261 | PS5-79-IP-9104-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 2.0
262 | PS5-79-BE-0241-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 87.0 | [18 empty] | A=3 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
263 | PS5-79-BE-0208-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 60.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
264 | PS5-79-BE-0292-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 73.0 | [18 empty] | A=3 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
265 | PS5-79-BE-0058-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 77.0
266 | PS5-79-BE-0140-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 75.0 | [18 empty] | A=3 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
267 | PS5-79-BE-0004-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 73.0 | [18 empty] | A=3 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
268 | PS5-79-BE-0007-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 92.0 | [18 empty] | A=3 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
269 | PS5-79-BE-0161-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 72.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
270 | PS5-79-BE-0139-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 69.0 | [18 empty] | A=3 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
271 | PS5-79-BE-0162-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 73.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
272 | PS5-79-BE-0074-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 75.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
273 | PS5-79-BE-0142-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 76.0 | [18 empty] | A=3 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
274 | PS5-79-BE-0160-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 73.0
275 | PS5-79-BE-0077-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 68.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
276 | PS5-79-BE-0075-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 61.0
277 | PS5-79-BE-0053-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 55.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
278 | PS5-79-BE-0076-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 57.0
279 | PS5-79-BE-0070-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 69.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
280 | PS5-79-BE-0158-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 67.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
281 | PS5-79-BE-0060-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 63.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
282 | PS5-79-BE-0115-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 70.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
283 | PS5-79-BE-0108-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 69.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
284 | PS5-79-BE-0111-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 70.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
285 | PS5-79-BE-0062-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 60.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
286 | PS5-79-BE-0141-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 89.0 | [18 empty] | A=3 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
287 | PS5-79-BE-0207-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 61.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
288 | PS5-79-BE-0205-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 54.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
289 | PS5-79-BE-0044-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 59.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
290 | PS5-79-BE-0045-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 51.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
291 | PS5-79-BE-0261-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 45.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
292 | PS5-79-BE-0209-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 37.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
293 | PS5-79-IP-9903-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 90.0
294 | PS5-79-IP-9105-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 2.0
295 | PS5-79-IP-9106-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 2.0
296 | PS5-79-BE-0064-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 127.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
297 | PS5-79-BE-0057-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 129.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
298 | PS5-79-BE-0021-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 119.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
299 | PS5-79-BE-0128-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 128.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
300 | PS5-79-BE-0008-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 123.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
301 | PS5-79-SP-0008-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 4.0
302 | PS5-79-BE-0047-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 113.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
303 | PS5-79-BE-0052-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 127.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
304 | PS5-79-BE-0056-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 129.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
305 | PS5-79-BE-0055-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 130.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
306 | PS5-79-BE-0028-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 111.0
307 | PS5-79-BE-0294-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 124.0
308 | PS5-79-BE-0293-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 125.0
309 | PS5-79-BE-0129-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 124.0
310 | PS5-79-BE-0073-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 117.0
311 | PS5-79-BE-0010-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 117.0
312 | PS5-79-SP-0010-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 4.0
313 | PS5-79-BE-0124-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 126.0
314 | PS5-79-BE-0295-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 119.0
315 | PS5-79-BE-0030-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 111.0
316 | PS5-79-BE-0127-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 118.0
317 | PS5-79-BE-0051-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 113.0
318 | PS5-79-BE-0032-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 113.0
319 | PS5-79-BE-0033-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 112.0
320 | PS5-79-BE-0126-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 126.0
321 | PS5-79-BE-0125-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 128.0
322 | PS5-79-BE-0011-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 137.0
323 | PS5-79-BE-0301-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 118.0
324 | PS5-79-BE-0001-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 127.0
325 | PS5-79-BE-0009-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 121.0
326 | PS5-79-BE-0014-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 122.0
327 | PS5-79-BE-0034-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 110.0
328 | PS5-79-BE-0353-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 116.0
329 | PS5-71-BE-0362-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 96.0
330 | PS5-79-BE-0132-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 129.0
331 | PS5-79-BE-0131-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 123.0
332 | PS5-79-BE-0040-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 115.0
333 | PS5-79-BE-0233-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 117.0
334 | PS5-79-BE-0054-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 119.0
335 | PS5-79-BE-0022-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 120.0
336 | PS5-79-BE-0078-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 115.0
337 | PS5-79-BE-0105-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 112.0
338 | PS5-79-BE-0029-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 112.0
339 | PS5-79-BE-0035-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 103.0
340 | PS5-79-BE-0094-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 117.0
341 | PS5-79-BE-0120-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 102.0
342 | PS5-79-BE-0095-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 105.0
343 | PS5-79-BE-0087-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 99.0
344 | PS5-79-BE-0119-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 101.0
345 | PS5-79-BE-0117-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 118.0
346 | PS5-79-BE-0323-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 103.0
347 | PS5-79-BE-0096-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 73.0
348 | PS5-79-BE-0079-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 98.0
349 | PS5-79-BE-0345-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 96.0
350 | PS5-79-BE-0104-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 10.0 | 93.0
351 | PS5-79-BE-0230-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 83.0
352 | PS5-79-BE-0093-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 80.0
353 | PS5-79-BE-0088-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 81.0
354 | PS5-79-BE-0089-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 81.0
355 | PS5-79-BE-0091-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 71.0
356 | PS5-79-BE-0097-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 66.0
357 | PS5-79-BE-0321-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 101.0
358 | PS5-79-BE-0227-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 70.0
359 | PS5-60-BE-0364-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 156.0
360 | PS5-79-BE-0286-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 55.0
361 | PS5-79-BE-0347-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 55.0
362 | PS5-79-BE-0289-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 56.0
363 | PS5-79-BE-0342-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 64.0
364 | PS5-79-BE-0232-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 48.0
365 | PS5-79-BE-0231-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 43.0
366 | PS5-79-BE-0288-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 65.0
367 | PS5-79-BE-0225-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 40.0
368 | PS5-79-BE-0324-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 60.0
369 | PS5-79-BE-0080-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 51.0
370 | PS5-79-BE-0065-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 53.0
371 | PS5-79-BE-0287-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 62.0
372 | PS5-79-BE-0277-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 64.0
373 | PS5-79-BE-0276-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 65.0
374 | PS5-79-BE-0226-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 37.0
375 | PS5-79-BE-0340-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 65.0
376 | PS5-79-BE-0336-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 70.0
377 | PS5-79-BE-0031-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 55.0
378 | PS5-79-BE-0016-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 56.0
379 | PS5-79-BE-0038-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 56.0
380 | PS5-79-BE-0341-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 57.0
381 | PS5-79-BE-0337-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 60.0
382 | PS5-79-BE-0050-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 61.0
383 | PS5-79-BE-0048-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 62.0
384 | PS5-79-BE-0069-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 63.0
385 | PS5-79-BE-0349-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 56.0
386 | PS5-79-BE-0338-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 64.0
387 | PS5-60-BE-0368-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 69.0
388 | PS5-60-BE-0369-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 59.0
389 | PS5-60-BE-0370-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 64.0
390 | PS5-79-BE-0251-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333449 | 2C+E | 6.0 | 40.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
391 | PS5-79-BE-0297-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333449 | 2C+E | 6.0 | 41.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
392 | PS5-79-BE-0296-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333449 | 2C+E | 6.0 | 40.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
393 | PS5-79-BE-0012-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333486 | 2C+E | 6.0 | 32.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
394 | PS5-79-BE-0259-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 38.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
395 | PS5-79-BE-0257-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 42.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
396 | PS5-79-BE-0258-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333449 | 2C+E | 6.0 | 63.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
397 | PS5-79-BE-0098-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333449 | 2C+E | 6.0 | 65.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
398 | PS5-79-BE-0300-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333449 | 2C+E | 6.0 | 65.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
399 | PS5-79-BE-0248-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333449 | 2C+E | 6.0 | 85.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
400 | PS5-79-BE-0254-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333486 | 2C+E | 6.0 | 53.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
401 | PS5-79-BE-0310-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 57.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
402 | PS5-79-BE-0263-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 54.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
403 | PS5-79-BE-0122-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 53.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
404 | PS5-79-BE-0110-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 52.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
405 | PS5-79-BE-0256-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 51.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
406 | PS5-79-BE-0320-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 53.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
407 | PS5-79-BE-0255-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 55.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
408 | PS5-79-BE-0017-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 56.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
409 | PS5-79-BE-0250-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 57.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
410 | PS5-79-BE-0249-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 58.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
411 | PS5-79-BE-0318-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 59.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
412 | PS5-79-SP-0018-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 4.0
413 | PS5-79-BE-0299-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 53.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
414 | PS5-79-BE-0308-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 85.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
415 | PS5-79-BE-0013-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC | X-333449 | 2C+E | 6.0 | 42.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
416 | PS5-79-SP-0133-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 4.0
417 | PS5-79-BE-0138-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 24.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
418 | PS5-25-BE-0364-CL01 | 0.6/1KV | CU/XLPE/LSZH/GSWA | 230V AC |  | 2C+E | 6.0 | 148.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
419 | PS5-79-TE-0316-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 88.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
420 | PS5-79-TE-0315-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 87.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
421 | PS5-79-TE-0168-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 83.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
422 | PS5-79-TE-0170-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 83.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
423 | PS5-79-TE-0163-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 76.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
424 | PS5-79-TE-0167-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 83.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
425 | PS5-79-TE-0169-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 83.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
426 | PS5-79-TE-0159-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 82.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
427 | PS5-79-TE-0164-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 74.0
428 | PS5-79-TE-0151-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 75.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
429 | PS5-79-TE-0356-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 86.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
430 | PS5-79-TE-0206-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 70.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
431 | PS5-79-TE-0148-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 79.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
432 | PS5-79-TE-0314-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 79.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
433 | PS5-79-TE-0149-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 78.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
434 | PS5-79-TE-0234-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 84.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
435 | PS5-79-TE-0114-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 82.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
436 | PS5-79-TE-0165-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 73.0
437 | PS5-79-TE-0166-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 82.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
438 | PS5-79-TE-0157-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 72.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
439 | PS5-79-TE-0153-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 71.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
440 | PS5-79-TE-0313-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 80.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
441 | PS5-79-TE-0188-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 70.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
442 | PS5-79-TE-0202-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 61.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
443 | PS5-79-TE-0103-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 51.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
444 | PS5-79-TE-0317-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 49.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
445 | PS5-79-TE-0306-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 51.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
446 | PS5-79-TE-0197-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 51.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
447 | PS5-71-TE-0361-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 84.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-07 00:00:00 | CPP-RFI-68-331-05-0322
448 | PS5-79-TE-0181-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 68.0
449 | PS5-79-TE-0184-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 69.0
450 | PS5-79-TE-0302-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 68.0
451 | PS5-79-TE-0185-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 65.0
452 | PS5-79-TE-0182-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 63.0
453 | PS5-79-TE-0303-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 65.0
454 | PS5-79-TE-0304-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 56.0
455 | PS5-79-TE-0325-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 74.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
456 | PS5-79-TE-0311-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 72.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
457 | PS5-79-TE-0312-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 71.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
458 | PS5-79-TE-0173-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 62.0
459 | PS5-79-TE-0183-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 58.0
460 | PS5-79-TE-0355-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 68.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
461 | PS5-79-TE-0354-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 68.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
462 | PS5-79-TE-0201-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 70.0
463 | PS5-79-TE-0172-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 58.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
464 | PS5-79-TE-0180-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 53.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
465 | PS5-79-TE-0191-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 53.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
466 | PS5-79-TE-0192-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 52.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
467 | PS5-79-TE-0193-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 37.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
468 | PS5-79-TE-0196-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 77.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
469 | PS5-79-TE-0179-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 56.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
470 | PS5-79-TE-0326-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 74.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
471 | PS5-79-TE-0238-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 94.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
472 | PS5-79-TE-0174-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 53.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
473 | PS5-79-TE-0244-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 78.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
474 | PS5-79-TE-0199-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 15.0
475 | PS5-79-TE-0187-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 13.0
476 | PS5-79-TE-0190-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 12.0
477 | PS5-71-TE-0363-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 74.0
478 | PS5-79-TE-0023-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 104.0
479 | PS5-79-TE-0278-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 107.0
480 | PS5-79-TE-0307-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 104.0
481 | PS5-79-TE-0198-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 103.0
482 | PS5-79-TE-0046-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 103.0
483 | PS5-79-TE-0195-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 102.0
484 | PS5-79-TE-0252-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 95.0
485 | PS5-79-TE-0253-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 95.0
486 | PS5-79-TE-0200-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 90.0
487 | PS5-79-TE-0194-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 90.0
488 | PS5-79-TE-0246-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 90.0
489 | PS5-79-TE-0189-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 91.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
490 | PS5-79-TE-0210-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 66.0
491 | PS5-79-TE-0186-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 91.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
492 | PS5-79-TE-0279-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 99.0
493 | PS5-79-TE-0260-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 62.0
494 | PS5-79-TE-0211-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 64.0
495 | PS5-79-TE-0305-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 52.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
496 | PS5-79-TE-0322-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 38.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
497 | PS5-79-TE-0346-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 52.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-20 00:00:00 | CPP-RFI-68-33/1-05-0269
498 | PS5-79-TE-0348-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 132.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
499 | PS5-79-TE-0352-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 143.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
500 | PS5-79-TE-0242-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 158.0
501 | PS5-79-TE-0109-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 145.0
502 | PS5-79-TE-0113-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 146.0
503 | PS5-79-TE-0106-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 147.0
504 | PS5-79-TE-0351-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 161.0
505 | PS5-79-TE-0243-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 142.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
506 | PS5-60-TE-0365-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 85.0
507 | PS5-79-TE-0280-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 79.0
508 | PS5-79-TE-0331-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 76.0
509 | PS5-79-TE-0327-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 74.0
510 | PS5-79-TE-0266-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 73.0
511 | PS5-79-TE-0265-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 73.0
512 | PS5-79-TE-0212-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 16.0
513 | PS5-79-TE-0049-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 76.0
514 | PS5-79-TE-0329-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 67.0
515 | PS5-79-TE-0285-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 65.0
516 | PS5-79-TE-0220-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 59.0
517 | PS5-79-TE-0217-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 66.0
518 | PS5-79-TE-0219-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 55.0
519 | PS5-79-TE-0237-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 52.0
520 | PS5-79-TE-0282-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 43.0
521 | PS5-79-TE-0213-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 32.0
522 | PS5-79-TE-0086-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 47.0
523 | PS5-79-TE-0214-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 47.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
524 | PS5-79-TE-0283-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 45.0
525 | PS5-79-TE-0092-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 68.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
526 | PS5-79-TE-0216-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 66.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
527 | PS5-79-TE-0215-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 68.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
528 | PS5-79-TE-0099-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 70.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
529 | PS5-79-TE-0171-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 74.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
530 | PS5-79-TE-0264-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 73.0
531 | PS5-79-TE-0281-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 22.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
532 | PS5-79-TE-0284-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 24.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
533 | PS5-60-TE-0366-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 90.0
534 | PS5-79-TE-0332-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 89.0
535 | PS5-79-TE-0330-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 86.0
536 | PS5-79-TE-0269-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 87.0
537 | PS5-79-TE-0267-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 87.0
538 | PS5-79-TE-0268-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 87.0
539 | PS5-79-TE-0334-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 81.0
540 | PS5-79-TE-0333-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 77.0
541 | PS5-79-TE-0272-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 77.0
542 | PS5-79-TE-0270-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 78.0
543 | PS5-79-TE-0271-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 77.0
544 | PS5-79-TE-0335-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 85.0
545 | PS5-79-TE-0339-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 88.0
546 | PS5-79-TE-0275-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 85.0
547 | PS5-79-TE-0273-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 83.0
548 | PS5-79-TE-0274-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 82.0
549 | PS5-79-TE-0328-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 75.0
550 | PS5-79-TE-0061-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 72.0
551 | PS5-79-TE-0218-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 65.0
552 | PS5-79-TE-0229-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 81.0
553 | PS5-79-TE-0223-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 60.0
554 | PS5-79-TE-0224-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 64.0
555 | PS5-79-TE-0221-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 71.0
556 | PS5-79-TE-0235-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 96.0
557 | PS5-79-TE-0222-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 67.0
558 | PS5-79-TE-0350-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 70.0
559 | PS5-79-TE-0228-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 76.0
560 | PS5-79-TE-0236-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 90.0
561 | PS5-60-TE-0367-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 85.0
562 | PS5-79-TE-0136-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 110.0
563 | PS5-79-TE-0027-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 109.0
564 | PS5-79-TE-0039-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 87.0
565 | PS5-79-TE-0037-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 75.0
566 | PS5-79-TE-0025-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 97.0
567 | PS5-79-TE-0343-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 109.0
568 | PS5-79-TE-0118-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 88.0
569 | PS5-79-TE-0137-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 88.0
570 | PS5-79-TE-0024-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 87.0
571 | PS5-79-TE-0150-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 99.0
572 | PS5-79-TE-0203-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 69.0
573 | PS5-79-TE-0204-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 68.0
574 | PS5-79-TE-0262-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 73.0
575 | PS5-79-TE-0102-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 75.0
576 | PS5-79-TE-0081-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 84.0
577 | PS5-79-TE-0036-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 85.0
578 | PS5-79-TE-0066-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 73.0
579 | PS5-79-TE-0067-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 78.0
580 | PS5-79-TE-0245-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 82.0
581 | PS5-79-TE-0134-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 92.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
582 | PS5-79-TE-0063-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 91.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
583 | PS5-79-TE-0154-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 97.0
584 | PS5-79-TE-0319-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 74.0
585 | PS5-79-TE-0290-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 100.0
586 | PS5-79-TE-0152-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 99.0
587 | PS5-79-TE-0002-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 83.0
588 | PS5-79-TE-0005-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 96.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
589 | PS5-79-TE-0146-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 83.0
590 | PS5-79-TE-0041-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 85.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
591 | PS5-79-TE-0135-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 102.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
592 | PS5-79-TE-0239-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 114
593 | PS5-79-TE-0247-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 61.0
594 | PS5-79-TE-0084-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 63.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
595 | PS5-79-TE-0090-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 58.0
596 | PS5-79-TE-0085-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 75
597 | PS5-79-TE-0082-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 84.0
598 | PS5-79-TE-0101-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 67.0
599 | PS5-79-TE-0156-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 72.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
600 | PS5-79-TE-0107-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 61.0
601 | PS5-79-TE-0020-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 75 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-25 00:00:00 | CPP-RFI-68-33/1-05-0281
602 | PS5-79-TE-0147-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 55.0
603 | PS5-79-TE-0043-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 62.0
604 | PS5-79-TE-0344-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 61.0
605 | PS5-79-TE-0019-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 55.0
606 | PS5-79-TE-0100-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 51.0
607 | PS5-79-TE-0112-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 59.0
608 | PS5-79-TE-0068-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 74.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
609 | PS5-79-TE-0042-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 74.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
610 | PS5-79-TE-0121-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 65.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
611 | PS5-79-TE-0072-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 94
612 | PS5-79-TE-0116-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 65.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
613 | PS5-79-TE-0145-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 94
614 | PS5-79-TE-0155-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 93.0
615 | PS5-79-TE-0071-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 94
616 | PS5-79-TE-0083-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 66.0
617 | PS5-79-TE-0291-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 72.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
618 | PS5-79-TE-0003-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 73.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
619 | PS5-79-TE-0143-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 73.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
620 | PS5-79-TE-0059-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 75.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
621 | PS5-79-TE-0006-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 97.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
622 | PS5-79-TE-0144-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 99.0
623 | PS5-79-TE-0240-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 101.0 | [18 empty] | A=0 B=3 C=0 |  |  | 2026-06-05 00:00:00 | CPP-RFI-68-331-05-0315
624 | PS5-79-TE-0241-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 87.0 | [18 empty] | A=3 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
625 | PS5-79-TE-0208-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 58.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
626 | PS5-79-TE-0292-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 72.0 | [18 empty] | A=3 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
627 | PS5-79-TE-0058-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 76.0
628 | PS5-79-TE-0140-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 74.0 | [18 empty] | A=3 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
629 | PS5-79-TE-0004-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 73.0 | [18 empty] | A=3 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
630 | PS5-79-TE-0007-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 92.0 | [18 empty] | A=3 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
631 | PS5-79-TE-0161-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 71.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
632 | PS5-79-TE-0139-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 68.0 | [18 empty] | A=3 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
633 | PS5-79-TE-0162-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 72.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
634 | PS5-79-TE-0074-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 74.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
635 | PS5-79-TE-0142-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 74.0 | [18 empty] | A=3 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
636 | PS5-79-TE-0160-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 72.0
637 | PS5-79-TE-0077-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 67.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-23 00:00:00 | CPP-RFI-68-331-05-0277
638 | PS5-79-TE-0075-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 59.0
639 | PS5-79-TE-0053-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 54.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
640 | PS5-79-TE-0076-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 57.0
641 | PS5-79-TE-0070-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 69.0
642 | PS5-79-TE-0158-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 67.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
643 | PS5-79-TE-0060-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 64.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
644 | PS5-79-TE-0115-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 71.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
645 | PS5-79-TE-0108-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 69.0
646 | PS5-79-TE-0111-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 70.0
647 | PS5-79-TE-0062-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 59.0
648 | PS5-79-TE-0141-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 89.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
649 | PS5-79-TE-0207-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 59.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
650 | PS5-79-TE-0205-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 53.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
651 | PS5-79-TE-0044-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 59.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
652 | PS5-79-TE-0045-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 53.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
653 | PS5-79-TE-0261-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 52.0 | [18 empty] | A=2 B=2 C=0 |  |  | 2026-05-24 00:00:00 | CPP-RFI-68-33/1-05-0280
654 | PS5-79-TE-0209-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 35.0
655 | PS5-79-TE-0064-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 137.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
656 | PS5-79-TE-0057-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 134.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
657 | PS5-79-TE-0021-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 118.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
658 | PS5-79-TE-0128-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 128.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
659 | PS5-79-TE-0008-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 122.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
660 | PS5-79-TE-0047-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 112.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
661 | PS5-79-TE-0052-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 128.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
662 | PS5-79-TE-0056-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 130.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
663 | PS5-79-TE-0055-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 130.0 | [21 empty] | 2026-06-10 00:00:00 | CPP-RFI-68-33/1-07-0328
664 | PS5-79-TE-0028-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 111.0
665 | PS5-79-TE-0294-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 124.0
666 | PS5-79-TE-0293-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 125.0
667 | PS5-79-TE-0129-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 123.0
668 | PS5-79-TE-0073-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 118.0
669 | PS5-79-TE-0010-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 117.0
670 | PS5-79-TE-0124-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 126.0
671 | PS5-79-TE-0295-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 119.0
672 | PS5-79-TE-0030-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 111.0
673 | PS5-79-TE-0127-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 117.0
674 | PS5-79-TE-0051-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 114.0
675 | PS5-79-TE-0032-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 112.0
676 | PS5-79-TE-0033-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 111.0
677 | PS5-79-TE-0126-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 126.0
678 | PS5-79-TE-0125-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 128.0
679 | PS5-79-TE-0011-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 138.0
680 | PS5-79-TE-0301-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 118.0
681 | PS5-79-TE-0001-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 127.0
682 | PS5-79-TE-0009-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 120.0
683 | PS5-79-TE-0014-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 121.0
684 | PS5-79-TE-0034-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 110.0
685 | PS5-79-TE-0353-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 115.0
686 | PS5-71-TE-0362-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 97.0
687 | PS5-79-TE-0132-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 130.0
688 | PS5-79-TE-0131-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 133.0
689 | PS5-79-TE-0040-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 127.0
690 | PS5-79-TE-0233-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 118.0
691 | PS5-79-TE-0054-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 119.0
692 | PS5-79-TE-0022-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 120.0
693 | PS5-79-TE-0078-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 115.0
694 | PS5-79-TE-0105-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 112.0
695 | PS5-79-TE-0029-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 111.0
696 | PS5-79-TE-0035-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 103.0
697 | PS5-79-TE-0094-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 117.0
698 | PS5-79-TE-0120-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 102.0
699 | PS5-79-TE-0095-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 105.0
700 | PS5-79-TE-0087-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 99.0
701 | PS5-79-TE-0119-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 101.0
702 | PS5-79-TE-0117-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 118.0
703 | PS5-79-TE-0323-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 103.0
704 | PS5-79-TE-0096-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 73.0
705 | PS5-79-TE-0079-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 98.0
706 | PS5-79-TE-0345-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 96.0
707 | PS5-79-TE-0104-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 93.0
708 | PS5-79-TE-0230-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 83.0
709 | PS5-79-TE-0093-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 80.0
710 | PS5-79-TE-0088-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 81.0
711 | PS5-79-TE-0089-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 81.0
712 | PS5-79-TE-0091-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 71.0
713 | PS5-79-TE-0097-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 67.0
714 | PS5-79-TE-0321-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 100.0
715 | PS5-79-TE-0227-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 71.0
716 | PS5-60-TE-0364-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 157.0
717 | PS5-79-TE-0286-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 54.0
718 | PS5-79-TE-0347-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 55.0
719 | PS5-79-TE-0289-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 55.0
720 | PS5-79-TE-0342-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 63.0
721 | PS5-79-TE-0232-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 47.0
722 | PS5-79-TE-0231-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 42.0
723 | PS5-79-TE-0288-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 64.0
724 | PS5-79-TE-0225-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 40.0
725 | PS5-79-TE-0324-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 59.0
726 | PS5-79-TE-0080-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 49.0
727 | PS5-79-TE-0065-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 52.0
728 | PS5-79-TE-0287-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 61.0
729 | PS5-79-TE-0277-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 64.0
730 | PS5-79-TE-0276-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 64.0
731 | PS5-79-TE-0226-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 37.0
732 | PS5-79-TE-0340-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 64.0
733 | PS5-79-TE-0336-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 67.0
734 | PS5-79-TE-0031-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 54.0
735 | PS5-79-TE-0016-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 55.0
736 | PS5-79-TE-0038-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 55.0
737 | PS5-79-TE-0341-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 55.0
738 | PS5-79-TE-0337-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 59.0
739 | PS5-79-TE-0050-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 60.0
740 | PS5-79-TE-0048-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 61.0
741 | PS5-79-TE-0069-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 63.0
742 | PS5-79-TE-0349-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 55.0
743 | PS5-79-TE-0338-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 62.0
744 | PS5-60-TE-0368-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 67.0
745 | PS5-60-TE-0369-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 58.0
746 | PS5-60-TE-0370-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 63.0
747 | PS5-79-TE-0251-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 40.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
748 | PS5-79-TE-0297-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 41.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
749 | PS5-79-TE-0296-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 40.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
750 | PS5-79-TE-0012-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 52.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
751 | PS5-79-TE-0259-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 28.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
752 | PS5-79-TE-0257-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 55.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
753 | PS5-79-TE-0258-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 62.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
754 | PS5-79-TE-0098-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 63.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
755 | PS5-79-TE-0300-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 64.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
756 | PS5-79-TE-0123-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 62.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
757 | PS5-79-TE-0248-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 84.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
758 | PS5-79-TE-0254-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 51.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
759 | PS5-79-TE-0310-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 56.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
760 | PS5-79-TE-0263-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 53.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
761 | PS5-79-TE-0122-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 53.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
762 | PS5-79-TE-0110-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 51.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
763 | PS5-79-TE-0256-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 51.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
764 | PS5-79-TE-0320-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 53.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
765 | PS5-79-TE-0255-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 52.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
766 | PS5-79-TE-0017-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 54.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
767 | PS5-79-TE-0250-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 56.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
768 | PS5-79-TE-0249-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 58.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
769 | PS5-79-TE-0318-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 58.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
770 | PS5-79-TE-0299-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 52.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
771 | PS5-79-TE-0308-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 63.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
772 | PS5-79-TE-0013-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 26.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
773 | PS5-79-TE-0015-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 44.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
774 | PS5-79-TE-0133-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123188 | 3C | 1.5 | 40.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
775 | PS5-79-TE-0298-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123189 | 3C | 1.5 | 42.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
776 | PS5-79-TE-0026-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - | KD-123189 | 3C | 1.5 | 41.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-05-22 00:00:00 | CPP-RFI-68-331-05-0274
777 | PS5-79-TE-0138-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 24.0 | [18 empty] | A=1 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
778 | PS5-25-TE-0364-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 146.0 | [18 empty] | A=0 B=2 C=0 |  |  | 2026-06-20 00:00:00 | CPP-RFI-68-331-05-0370
779 | PS5-79-BE-0175-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 104.0
780 | PS5-79-IP-9101-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 2.0
781 | PS5-79-IP-9102-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 2.0
782 | PS5-79-BE-0176-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 97.0
783 | PS5-79-IP-9103-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 2.0
784 | PS5-79-IP-9104-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 2.0
785 | PS5-79-BE-0177-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 86.0
786 | PS5-79-IP-9105-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 2.0
787 | PS5-79-IP-9106-CW01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 2.0
788 | PS5-79-TE-0175-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 124.0
789 | PS5-79-TE-0176-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 125.0
790 | PS5-79-TE-0178-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 118.0
791 | PS5-79-TE-0177-CD01 | 0.6/1KV | CU/PVC/OSCR/FR-LSZH/GSWB/FR-LSZH | - |  | 3C | 1.5 | 119.0
792 | [7 empty] | 58287